## Revision History
Revision |  | Issue Date | Filename as sent
0 | AE allocated default risks to Failure Code and Systems, tag criticalities derived by 'highest wins' logic for each S,E,P,B factor and then 'highest wins' again to determine overall criticality result | 2017-10-12 | WND Criticality - Rev 0 - to BP.xlsx
1 | Comparison calculations using alternate 'voting table' approach to determining S,E,P,B factors from System and Failure code criticalities. Also showing results from preliminary AE criticality assessment that was part complete when WND Decision Paper procedure introduced. | 2017-10-23 | WND Criticality alternative calcs.xlsx
2 | Review coverage of Failure Class and systems (DefaultMethod and DefaultMethod2 worksheets) using pivot tables. Copy DefaultMethod supplied as a snapshot to illustrate coverage as "2017-10-25 Criticality Coverage illustration.xlsx" Added nearest identifiable MAH barrier 'typical criticality' to System and Failure Code tables for comparison / cross checking. These are not a perfect match so only included for guidance / reference and are in most cases debateable as to whether they should apply to everything in the System / Failure code. Not used in any criticality calculation. | 2017-10-25 | 2017-10-25 Criticality Coverage illustration.xlsx
3.0 | Added FCodeToUMCL+ to illustrate increased granularity from using this (not much) Added FCodeToUMCL+ToISO to illustrate increased granularity going to allocated ISO code) Added FCodeToUMCL+ToISOToFCode+ to illustrate increased granularity from using FAILRE CODE PLUS - mainly splits out Transmitters by type. Added BP Feedback comments column to Systems spreadsheet - Saved as Rev 3.0.xlsx as a non-issued release before making changes to any Systems rankings in response. Changed handling of systems to allow 'Not Assessed' input and output values to catch any tags added to previously unused system. This now applies to tags without a defined system. |  | Not issued, internal point release to capture state before responding to BP comments
3.1 | Updated risk inputs and comments where required to respond to BP feedback. Retains copy of original inputs and comments for reference. |  | not issued, internal point release to capture state before next changes
3.2 | Remove integrity only tags from results list (by labelling them excluded) |  | not issued, internal point release to capture state before next changes
3.3 | Add Tag Abbreviation to MELDefaultCodeApplied import query and identify shutdown tags using supplied list of shutdown abbreviations (see Tables sheet). Set all shutdown tags to A (or excluded if integrity only tags) |  | not issued, internal point release to capture state before next changes

## Method
Methodology
In this spreadsheet, the criticality results for functional locations has been set in line with EG001-OP-PRO-00-3051
Step 1: Assign criticalities to system codes
This is shown in the Systems worksheet, where risk rankings from BP Risk Management Policy 000030 have been
assigned for each of the four categories Safety (S), Environment (E), Production (P) and Business non-financial (B)
Risks have been assigned for the system codes in use in the WND MEL.
These risk rankings are converted into equivalent A,B,C criticalities using the matrix in Annex D of BP Guide
Functional Location Criticality for SAP PM (GOO-RL-GLN-00002)
Rev 0 - Risk rankings have been estimated by AE as a starting point for review and agreement by BP
Rev 1 - Baseline Rankings not changed, alternative combination rules demonstrated
Rev 2 - Baseline Rankings not changed, alternative combination rules demonstrated
Rev 3.0 - BP comments on systems codes added, 3.0 is before making any updates in response
Rev 3.1 - Some calculation changes to cope with Systems with only FA_SYLH codes in them. These tags will show up as None for system criticality, and not be included in A,B,C counts as the final criticality is a #N/A error due to the matrix lookup failing. 44 tags affected when first implemented, only 18 of which in a defined system, 12 of these are parent for non-validated tags in that system. Added "Not Assessed" as a valid input risk to propagate through to tag criticality to find any tags which might appear in previously unassessed systems. At first pass catches 664 tags with no system defined (XX) which were previously shown as C.
Rev 3.2 - No changes
Rev 3.3 - No changes
Step 2: Assign criticalities to failure codes
This is shown in the "FailureCodes" worksheet, where risk rankings have been allocated for each failure code.
Rev 0 - Risk rankings have been estimated by AE based on our experience, but in this case rankings have been
selected at the low end of the range of previously generated options due to concerns over 'criticality inflation'
inherent in the method outlined in EG001-OP-PRO-00-3051. To clarify, these are not the lowest possible rankings,
but the lowest of the range of rankings that AE had assigned within a failure class on initial review of the
functional location hierarchy for criticality.
Rev 1 - Baseline Rankings not changed, alternative combination rules demonstrated
Rev 2 - Baseline System and Failure codes rankings unchanged, looking at coverage of Failure Code and system combinations
Rev 3.0 - BP comments on systems codes added, 3.0 is before making any updates in response
Rev 3.1 - no changes
Rev 3.2 - Exclude integrity only Failure Classes by lookup in table defining split as per Paul Powney email.
Rev 3.3 - Change table to show counts of tags in failure code AFTER Excluding Integrity only tags
Step 3: Assign criticalities to Functional Locations based on System and Failure Code
This is shown in the "MELDefaultCodeApplied" worksheet for the VALID and DUP status codes (i.e. validated
functional locations and those where duplicate uses of a code have been identified requiring a new code to be
allocated in future issues of the Functional Location Hierarchy).
Tag listing is a filtered import from ASSET-C database only importing VALID and DUP status coded Functional Locations.
A simple summary count and %age of As, Bs and Cs allocated is included above the top right of the data table.
Rev 0 - For each Functional Location, Criticality components for S,E,P,B are shown for both System and Failure Code,
with the tag components being the highest of either. The overall criticality is the highest component code (i.e.
"highest wins").
Rev 0 - Special cases: The FA_SYLH (system level hierarchy) failure code has some special case handling where a
system code is not defined (Object Type desc = "XX", 244 Functional Locations affected). Functional Locations have either
been associated with a relevant or parent system, or treated as N/A where the Functional Location is acting as a parent
for unvalidated codes or where a sensible system association has not been defined.
Rev 1 - Baseline System and Failure codes rankings unchanged, additional voting rules trialled using a lookup matrix
Rev 2 - Baseline System and Failure codes rankings unchanged, looking at coverage of Failure Code and system combinations
Rev 3.0 - BP comments on systems codes added, 3.0 is before making any updates in response
Rev 3.1 - highest wins and AE prelim results removed to concentrate on matrix method.
Rev 3.2 - No change to calculation but mark integrity only F_Codes as Excluded and exclude them from summary numbers
Rev 3.3 - Add columns to identify shutdown tags from Tag Abbreviation (added field to ASSET-C query) - Make all shutdown tags A (a lot were C, e.g. ball valves) - Remove IFERROR() guard from system and F_Code lookups to avoid masking any lookup errors in future updates - Make Failurecodes table a Table to enable structured reference lookups - Refactor VLOOKUPs to INDEX/MATCH in main table to try and recover some performance and use structured referencing

## FailureCodes
Failure Code
|  |  | Inputs |  |  |  | Criticality Category Score |  |  |  |  | Final Criticality
FailureCode | Description | Number found in MEL | Safety | Environment | Production | Business Non Financial | Criticality S | Criticality E | Criticality P | Criticality B | → | Criticality Overall | - | MAH barrier(s) potentially applicable | MAH Barrier Criticality | Comment on MAH Barriers | -- | Planned corrections
FA_CFBC | CONTROL ROOM | 0 | E3 | H3 | H3 | H3 | B | C | C | C | → | B |  | M5 ¦ Muster areas, escape and evacuation routes ¦ Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | MAH barrier definition based on offshore context? Not a best fit selection
FA_CFSGW | WALL OR FENCE | 0 | G3 | H3 | H3 | H3 | C | C | C | C | → | C |  | P2 ¦ Structural Integrity ¦ Tertiary Structures - Failure may result in fall <1m | C | Nearest fit selection
FA_CFSSE | EQUIPMENT SUPPORT STRUCTURE | 0 | E3 | H3 | H3 | G3 | B | C | C | C | → | B |  | P4 ¦ Process Containment Integrity ¦ Supports for criticality A pressure systems | A | Suggest this would catch too many not critical supports.
FA_CFSSF | STRUCTURAL FOUNDATION | 0 | F3 | H3 | H3 | H3 | C | C | C | C | → | C |  | P4 ¦ Process Containment Integrity ¦ All other supports, paint and bolting | C | Best fit for non critical equipment
FA_CFSST | STRUCTURAL BASE | 0 | E3 | H3 | H3 | G3 | B | C | C | C | → | B |  | P4 ¦ Process Containment Integrity ¦ All other supports, paint and bolting | C | Need to rationalise difference with FA_CSSF or align them
FA_EECF | LIGHT FITTING | 398 | H7 | H7 | H7 | H7 | C | C | C | C | → | C |  | M3 ¦ Emergency Lighting ¦ Emergency Lighting - supplied from Emergency Generator Switchboard | B | Would catch non-emergency lighting as well
FA_EECH | ELECTRIC HEATER | 64 | G5 | H5 | G5 | H5 | C | C | C | C | → | C |  | M4 ¦ Ignition Prevention ¦ For Equipment in Zone 2 | B | Nearest fit for equipment level MAH, but would expect this secondary function to be covered by Ex register & inspection separately
FA_EECMD | DC ELECTRIC MOTOR | 7 | E6 | H6 | F6 | H6 | A | C | B | C | → | A |  | M4 ¦ Ignition Prevention ¦ Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | Assumed to be battery driven post shut down lube oil pumps for equipment cooldown cycles
FA_EECMI | AC INDUCTION ELECTRIC MOTOR | 379 | H6 | H6 | H6 | H6 | C | C | C | C | → | C |  | M4 ¦ Ignition Prevention ¦ For Equipment in Zone 2 | B | Nearest fit for equipment level MAH, but would expect this secondary function to be covered by Ex register & inspection separately
FA_EECMS | AC SYNCHRONOUS ELECTRIC MOTOR | 1 | E6 | H6 | F6 | H6 | A | C | B | C | → | A |  | M5 ¦ Lifting system ¦ Winch (general purpose - not for lifting personnel) | B | One tag, motor for flare tip maintenance winch. If treated as Cranes ¦ Prime mover would also a B
FA_EECO | ELECTRIC SOCKET OUTLET | 18 | H6 | H6 | H6 | H6 | C | C | C | C | → | C |  | M4 ¦ Ignition Prevention ¦ For Equipment in Zone 2 | B | Nearest fit for equipment level MAH, but would expect this secondary function to be covered by Ex register & inspection separately
FA_EEPBA | AIR CIRCUIT BREAKER | 868 | H6 | H6 | H6 | H6 | C | C | C | C | → | C |  |  | #N/A | none selected, should always be in non-hazardous zones
FA_EEPBV | VACUUM CIRCUIT BREAKER | 47 | F6 | H6 | F6 | H6 | B | C | B | C | → | B |  |  | #N/A | none selected, should always be in non-hazardous zones
FA_EEPCS | SACRIFICIAL ANODE | 5 | H5 | H5 | H5 | G5 | C | C | C | C | → | C |  |  | #N/A | None selected, long term equipment protection from corrosion, any issues should be caught by RBI
FA_EEPNE | EARTHING BAR | 118 | H6 | H6 | H6 | H6 | C | C | C | C | → | C |  |  | #N/A | None selected
FA_EEPNN | NEUTRAL GROUND RESISTOR | 8 | F6 | H6 | F6 | G6 | B | C | B | B | → | B |  |  | #N/A | None selected, assumed installed in non-hazardous zone
FA_EEPS | START / STOP SWITCH | 171 | F6 | H6 | F6 | H6 | B | C | B | C | → | B |  |  | #N/A | none selected
FA_EEPU | UNINTERRUPTIBLE POWER SUPPLY | 4 | E7 | H7 | F7 | F7 | A | C | A | A | → | A |  | M3 ¦ Emergency Power ¦ UPS Systems | A | Best fit for MAH barrier
FA_EETB | BATTERY | 15 | E7 | H7 | F7 | F7 | A | C | A | A | → | A |  | M3 ¦ Emergency Power ¦ UPS Systems | A | for batteries in UPS systems, post trip DC motor supplies
FA_EETC | BATTERY CHARGER | 4 | E7 | H7 | F7 | F7 | A | C | A | A | → | A |  | M3 ¦ Emergency Power ¦ UPS Systems | A | for batteries in UPS systems, post trip DC motor supplies
FA_EETD | BUS DUCT / BUS BAR | 70 | F3 | H3 | F3 | G3 | C | C | C | C | → | C |  |  | #N/A | None selected. Should be in non-hazardous areas
FA_EETFW | WET TRANSFORMER | 20 | H4 | H4 | F4 | F4 | C | C | B | B | → | B |  |  | #N/A | None selected
FA_EETGA | AC ELECTRIC GENERATOR | 11 | G5 | H5 | F5 | G5 | C | C | B | C | → | B |  | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Alternators | B | Best fit for MAH barrier
FA_EETI | ELECTRIC ISOLATOR | 9 | G6 | H6 | H6 | H6 | B | C | C | C | → | B |  |  | #N/A | None selected
FA_EETM | MOTOR CONTROL CENTER | 910 | H6 | H6 | H6 | H6 | C | C | C | C | → | C |  |  | #N/A | none selected, should always be in non-hazardous zones
FA_EETO | POWER / CONTROL MODULE | 4 | H6 | H6 | F6 | H6 | C | C | B | C | → | B |  |  | #N/A | none selected, should always be in non-hazardous zones
FA_EETP | ELECTRICAL PANEL | 3 | G4 | H4 | F4 | F4 | C | C | B | B | → | B |  |  | #N/A | none selected, should always be in non-hazardous zones
FA_EETR | POWER RECTIFIER | 2 | H4 | H4 | F4 | F4 | C | C | B | B | → | B |  |  | #N/A | none selected, should always be in non-hazardous zones
FA_EETW | SWITCHGEAR | 140 | H6 | H6 | H6 | H6 | C | C | C | C | → | C |  |  | #N/A | none selected, should always be in non-hazardous zones
FA_EETY | POWER SUPPLY | 28 | G4 | H4 | G4 | H4 | C | C | C | C | → | C |  |  | #N/A | none selected, should always be in non-hazardous zones
FA_INAM | FLOW METER | 15 | H6 | H6 | G6 | H6 | C | C | B | C | → | B |  | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable | B | Best fit for MAH barrier
FA_INAP | SAMPLER | 10 | H7 | H7 | H7 | G7 | C | C | C | B | → | B |  |  | #N/A | None selected
FA_INDC | LOCAL CONTROLLER | 8 | H6 | H6 | F6 | H6 | C | C | B | C | → | B |  | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable | B | Best fit for MAH barrier
FA_INDFD | DAMPER | 20 | E7 | H7 | H7 | G7 | A | C | C | B | → | A |  | M5 ¦ Muster areas, escape and evacuation routes ¦ Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | For non-TR Rotating equipment enclosures (mainly GTs), P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Pressurized Enclosures or P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Fire & Gas System could be considered
FA_INDFS | SOLENOID VALVE | 204 | H6 | H6 | F6 | H6 | C | C | B | C | → | B |  | P7 ¦ SIS - Non LoP Components ¦ LoP Components: Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke | B | Solenoid valves, in F&G or LOPs would be A from P7 ¦ SIS - LoP Components ¦ LoP Components: Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial or P6 ¦ Control systems - LoPs ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, p or M6 ¦ Fire & Gas systems ¦ Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution.
FA_INDI | INDICATOR | 1249 | H7 | H7 | H7 | H7 | C | C | C | C | → | C |  |  | #N/A | None selected
FA_INDMS | SENSING ELEMENT | 1386 | H6 | H6 | F6 | H6 | C | C | B | C | → | B |  | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable | B | Best fit for MAH barrier
FA_INDMT | TRANSMITTER | 2410 | H5 | H5 | F5 | H5 | C | C | B | C | → | B |  | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable | B | Best fit for MAH barrier
FA_INDS | INSTRUMENT SWITCH | 1048 | H6 | H6 | H6 | H6 | C | C | C | C | → | C |  | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable | B | Best fit for MAH barrier
FA_INDT | TRANSDUCER | 33 | H5 | H5 | F5 | H5 | C | C | B | C | → | B |  | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable | B | Best fit for MAH barrier
FA_INSC | PLC PANEL | 8 | G7 | H7 | G7 | H7 | B | C | B | C | → | B |  | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable | B | Best fit for MAH barrier
FA_INSJ | JUNCTION BOX | 734 | F7 | H7 | H7 | H7 | A | C | C | C | → | A |  | M4 ¦ Ignition Prevention ¦ Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | Arguable whether should consider ignition prevention as a primary function in this case, as elsewhere consider Ex inspection to be taken care of separately.
FA_INSL | LOCAL CONTROL PANEL | 206 | H5 | H5 | H5 | H5 | C | C | C | C | → | C |  | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable | B | Best fit for MAH barrier
FA_INSS | OPERATOR STATION | 3 | G7 | H7 | G7 | H7 | B | C | B | C | → | B |  | P8 ¦ Alarms & operator response ¦ Instruments associated with non-Safety Related Alarms - transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distributio | B | Best fit for MAH barrier, unless consider station also associated with safety related alarms (LOPA) to be on operator panel in which case would be an A
FA_INSY | SAFETY INSTRUMENT SYSTEM PANEL | 19 | E7 | H7 | G7 | G7 | A | C | B | B | → | A |  | P8 ¦ Alarms & operator response ¦ Instruments associated with Safety Related Alarms (credited in LOPA) - transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and po | A | Best fit for MAH barrier
FA_PEA | SELF-ACTUATING VALVE | 125 | H5 | H5 | G5 | G5 | C | C | C | C | → | C |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | C | Best fit for MAH barrier
FA_PEG | PIPING | 0 | G4 | H4 | G4 | G4 | C | C | C | C | → | C |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | C | Best fit for MAH barrier
FA_PEL | PIG LAUNCHER / RECEIVER | 0 | H5 | H5 | E5 | F5 | C | C | A | B | → | A |  | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | Best fit for MAH barrier
FA_PEM | MANIFOLD | 0 | H4 | H4 | F4 | G4 | C | C | B | C | → | B |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | C | Best fit for MAH barrier
FA_PEO | RESTRICTIVE ORIFICE | 0 | H4 | H4 | H4 | H4 | C | C | C | C | → | C |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | C | Higher ratings for specific applications - ROs to restrict flow Flare or to a PSV - A ROs to in pump recirc lines - B
FA_PESC | CONVENTIONAL PRESSURE SAFETY VALVE | 502 | E5 | F5 | F5 | H5 | A | B | B | C | → | A |  | P5 ¦ Overpressure Protection ¦ All other PSVs | B | Lowest rated MAH barrier for PSVs, expect most to be covered by the A rating for: Hazardous or toxic duty, pressure > 50barg, Temp > 120°C, inlet size >= 8"
FA_PESR | RUPTURE DISC | 49 | E5 | F5 | F5 | H5 | A | B | B | C | → | A |  | P5 ¦ Overpressure Protection ¦ Other bursting disks | B | Context expected to raise most rupture discs to A: Hazardous duty, HP/LP interface protection, Relieving directly to flare, upstream of PSV as fouling protection if PSV is A.
FA_PESV | VACUUM RELIEF PRESSURE SAFETY VALVE | 15 | E5 | F5 | F5 | H5 | A | B | B | C | → | A |  | P5 ¦ Overpressure Protection ¦ Vacuum breakers in hazardous or toxic duty | A | Nearest fit MAH barrier, treating safety valve as critical vacuum breaker
FA_PET | THERMOWELL | 0 | E5 | H5 | F5 | H5 | A | C | B | C | → | A |  | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | Nearest fit MAH barrier, unless categorise with "All Other Pressure containment Equipment" and make it default C.
FA_PEVB | BALL VALVE | 5535 | G5 | G5 | G5 | H5 | C | C | C | C | → | C |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | C | Nearest fit barrier. Majority isolation hand valves
FA_PEVC | CHECK VALVE | 1013 | G5 | G5 | G5 | H5 | C | C | C | C | → | C |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | C | Nearest fit for MAH barrier
FA_PEVD | DIAPHRAGM VALVE | 3 | G5 | G5 | G5 | H5 | C | C | C | C | → | C |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | C | Nearest fit for MAH barrier
FA_PEVG | GATE VALVE | 2331 | G5 | G5 | G5 | H5 | C | C | C | C | → | C |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | C | Nearest fit for MAH barrier
FA_PEVL | GLOBE VALVE | 814 | G5 | G5 | G5 | H5 | C | C | C | C | → | C |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | C | Nearest fit for MAH barrier
FA_PEVM | MULTIPLE ORIFICE VALVE | 9 | G6 | G6 | G6 | H6 | B | B | B | C | → | B |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | C | Code allocated to 3 way valves, 5 As in water mist systems, 4 Bs in chemical sampling
FA_PEVN | NEEDLE VALVE | 73 | H5 | H5 | H5 | H5 | C | C | C | C | → | C |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | C
FA_PEVX | DIVERTER VALVE | 4 | E5 | F5 | F5 | F5 | A | B | B | B | → | A |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | C | 4 tags are all NOTAGs which may get reallocated failure code. Applied rating copied from AGT definition which may have been allocated to different , more critical valves
FA_PEVY | BUTTERFLY VALVE | 65 | G6 | G6 | G6 | H6 | B | B | B | C | → | B |  | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable | B | Butterfly valves assumed to be used where some element of control is used, including hand valves.
FA_REBC | BLOWER, CENTRIFUGAL | 4 | E7 | H7 | G7 | G7 | A | C | B | B | → | A |  | P4 ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | Systems will elevate all 4 tags to A
FA_REC | CENTRIFUGE | 4 | G7 | H7 | G7 | G7 | B | C | B | B | → | B |  | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ All Casing joints, fittings and seals | B | Approximate match for MAH barrier. (All MEG centrifuges, criticality A from system)
FA_REDH | HYDRAULIC MOTOR | 9 | G7 | G7 | G7 | H7 | B | B | B | C | → | B |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | C | Rough match for MAH barrier as a pressure system
FA_REDP | PNEUMATIC MOTOR | 11 | G7 | G7 | G7 | H7 | B | B | B | C | → | B |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | C | Rough match for MAH barrier as a pressure system
FA_REEL | LIQUID FUEL COMBUSTION ENGINE | 5 | E7 | H7 | E7 | G7 | A | C | A | B | → | A |  | P4 ¦ Diesel Driven Packages ¦ Diesel Engine | B | 3 firepump drivers + emergency generator driver
FA_REFA | AXIAL FAN | 21 | E7 | G7 | F7 | F7 | A | B | A | A | → | A |  | P4 ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | Initial allocation biased toward EM Gen cooling fans escalation to loss of emergency power, so should probably have been B here and closer match to centrifugal fans |  | Reset to match centrifugal fan
FA_REFC | CENTRIFUGAL FAN | 121 | G7 | H7 | G7 | G7 | B | C | B | B | → | B |  | P4 ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | Best fit for MAH barrier
FA_REMC | CENTRIFUGAL COMPRESSOR | 3 | G6 | G6 | F6 | F6 | B | B | B | B | → | B |  | P4 ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 3 centrifugal compressors, 1 for air start system on Em Gen, 2 export compressors which escalate to A from system.
FA_REMR | RECIPROCATING COMPRESSOR | 6 | G6 | G6 | E6 | F6 | B | B | A | B | → | A |  | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | Flash gas compressors
FA_REMT | ROTARY COMPRESSOR | 11 | G6 | G6 | F6 | F6 | B | B | B | B | → | B |  | P4 ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | All air compressors
FA_RENG | GAS TURBINE | 8 | F7 | G7 | E7 | F7 | A | B | A | A | → | A |  | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Gas Generator | A | Best fit MAH barrier
FA_REPC | CENTRIFUGAL PUMP | 250 | H7 | H7 | G7 | G7 | C | C | B | B | → | B |  | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ All Shaft Seals | A | Arguable fit for MAH barrier amongst RE and Process containment
FA_REPD | POSITIVE DISPLACEMENT PUMP | 12 | G6 | G6 | F6 | F6 | B | B | B | B | → | B |  | P4 ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | Mostly hydraulic system re-charge or hand pumps, arguable case for saying they are firepump controls
FA_RER | RAKE / SCRAPER | 2 | H6 | G6 | G6 | G6 | C | B | B | B | → | B |  |  | #N/A | None selected
FA_RETP | COUPLING | 5 | F6 | H6 | F6 | H6 | B | C | B | C | → | B |  | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ All coupling members | B | Best fit MAH barrier All rated A from parent system
FA_SEC | CYCLONE | 0 | H5 | G5 | G5 | G5 | C | C | C | C | → | C |  | P4 ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | All Vortex cooler sin air compressor packages
FA_SEFB | BASKET STRAINER FILTER | 275 | H7 | H7 | H7 | H7 | C | C | C | C | → | C |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | C | Best fit MAH barrier
FA_SEFE | ELEMENT FILTER | 186 | H7 | H7 | H7 | H7 | C | C | C | C | → | C |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | C | Best fit MAH barrier
FA_SEFS | SCREEN FILTER | 18 | H7 | H7 | H7 | H7 | C | C | C | C | → | C |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | C | Best fit MAH barrier
FA_SEHF | FINNED COIL HEAT EXCHANGER | 0 | H5 | H5 | F5 | H5 | C | C | B | C | → | B |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | C | Best fit MAH barrier
FA_SEHS | SPIRAL HEAT EXCHANGER | 0 | H5 | H5 | F5 | H5 | C | C | B | C | → | B |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | C | Best fit MAH barrier
FA_SEHT | SHELL & TUBE HEAT EXCHANGER | 0 | G5 | H5 | F5 | G5 | C | C | B | C | → | B |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | C | Best fit MAH barrier
FA_SEL | FLAME ARRESTOR | 42 | E5 | H5 | H5 | H5 | A | C | C | C | → | A |  | M4 ¦ Ignition Prevention ¦ Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | Best fit MAH barrier, others could be considered
FA_SEM | FLARE | 0 | E5 | G5 | E5 | F5 | A | C | A | B | → | A |  | P5 ¦ Blowdown vent and flare ¦ Flare tips | A | Best fit MAH barrier, others could be considered
FA_SENF | FIRED HEATER FURNACE | 0 | H5 | G5 | F5 | G5 | C | C | B | C | → | B |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | C | Considered nearest fit MAH barrier.
FA_SEPA | ACCUMULATOR | 0 | E5 | H5 | H5 | G5 | A | C | C | C | → | A |  | P4 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | Assumed all are high pressure accumulators. Contrast with pulsation dampeners below
FA_SEPC | CYLINDER | 0 | H5 | H5 | H5 | G5 | C | C | C | C | → | C |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | C | Considered nearest fit MAH barrier.
FA_SEPHC | CONDENSER VESSEL | 0 | H5 | H5 | F5 | G5 | C | C | B | C | → | B |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | C | Considered nearest fit MAH barrier. 2 tags in system 21 inherit A
FA_SEPHS | SEPARATOR VESSEL | 0 | H5 | H5 | G5 | G5 | C | C | C | C | → | C |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | C | Considered nearest fit MAH barrier.
FA_SES | PULSATION DAMPENER | 72 | G5 | H5 | G5 | H5 | C | C | C | C | → | C |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | C | Considered nearest fit MAH barrier, contrast with Accumulators as physically similar devices, but generally expect lower working pressures.
FA_SETAC | CLOSED ROOF ATMOSPHERIC TANK | 0 | H5 | F5 | G5 | G5 | C | B | C | C | → | B |  | P4 ¦ Oil Storage & Offloading ¦ Hydrocarbon Tanks | A | MAH shown only applies to subset of tags with this failure code
FA_SETAP | PIT / SUMP | 0 | H5 | F5 | G5 | G5 | C | B | C | C | → | B |  | M1 ¦ Bunding, Open and Closed Hazardous Drains ¦ Secondary containments | B
FA_SETPC | CYLINDRICAL PRESSURISED TANK | 0 | E5 | H5 | G5 | F5 | A | C | C | B | → | A |  | P4 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | Arguably excessive - air start system for EMGen has air start tank 30barg design pressure, other tags are previously untagged gas /water cylinders on water mist system, 5 of which only 6lt capacity on pneumatic panels
FA_SEZ | SILENCER / MUFFLER | 63 | H5 | G5 | H5 | H5 | C | C | C | C | → | C |  |  | #N/A | None selected
FA_SQFC | EQUIPMENT CABINET | 21 | E4 | H4 | H4 | H4 | B | C | C | C | → | B |  | M7 ¦ Fire protection ¦ Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | All fire hydrant cabinets
FA_SQFDF | FLAME DETECTOR | 375 | F7 | H7 | H7 | H7 | A | C | C | C | → | A |  | M6 ¦ Fire & Gas systems ¦ Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | Best fit MAH barrier
FA_SQFDG | FIXED GAS DETECTOR | 628 | F7 | H7 | H7 | H7 | A | C | C | C | → | A |  | M6 ¦ Fire & Gas systems ¦ Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | Best fit MAH barrier
FA_SQFDS | SMOKE DETECTOR | 36 | F7 | H7 | H7 | H7 | A | C | C | C | → | A |  | M6 ¦ Fire & Gas systems ¦ Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | Best fit MAH barrier
FA_SQFFD | FIREWATER DELUGE SYSTEM | 17 | E7 | H7 | F7 | F7 | A | C | A | A | → | A |  | M7 ¦ Fire protection ¦ Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | Best fit MAH barrier
FA_SQFFH | FIRE HOSE | 3 | E7 | H7 | H7 | F7 | A | C | C | A | → | A |  | M7 ¦ Fire protection ¦ Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | Best fit MAH barrier
FA_SQFFM | FIRE WATER/FOAM MONITOR | 19 | E6 | H6 | H6 | H6 | A | C | C | C | → | A |  | M7 ¦ Fire protection ¦ Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | Best fit MAH barrier
FA_SQFFY | FIRE HYDRANT | 109 | E5 | H5 | H5 | F5 | A | C | C | B | → | A |  | M7 ¦ Fire protection ¦ Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | Best fit MAH barrier
FA_SQFRA | EMERGENCY ALARM DEVICE | 175 | F7 | H7 | H7 | H7 | A | C | C | C | → | A |  | M6 ¦ Fire & Gas systems ¦ Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | Best fit MAH barrier
FA_SQFRE | SAFETY SHOWER OR EYE BATH | 18 | E5 | H5 | H5 | H5 | A | C | C | C | → | A |  |  | #N/A | None selected
FA_SQMT | MAINTENANCE TOOL | 2 | H7 | H7 | H7 | H7 | C | C | C | C | → | C |  |  | #N/A | None selected (flash gas compressor barring device)
FA_SQTA | PUBLIC ADDRESS AND ALARM SYSTEM | 34 | F7 | H7 | H7 | H7 | A | C | C | C | → | A |  | M3 ¦ Personnel Address (PA) System ¦ Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | Best fit MAH barrier
FA_SQTB | NON DIRECTIONAL BEACON | 97 | F7 | H7 | H7 | H7 | A | C | C | C | → | A |  | P9 ¦ Collision Prevention ¦ Navigation Aids, lights, sounders & UPS systems | A | Best fit MAH barrier
FA_SQTE | TELECOMMUNICATION CABINET | 16 | E7 | H7 | H7 | G7 | A | C | C | B | → | A |  | M3 ¦ Facility Emergency Telephone & Hot line systems ¦ Call control - PABX/IPT Ex telephones Designated emergency phones (Control rooms muster points etc.) Interconnecting cable plant and networks | A | Best fit MAH barrier, may only apply to subset, but not clear how to identify
FA_SQTL | LOUDSPEAKER | 294 | E7 | H7 | H7 | G7 | A | C | C | B | → | A |  | M3 ¦ Personnel Address (PA) System ¦ Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | Best fit MAH barrier
FA_SQTOF | FIXED RADIO | 2 | G6 | H6 | G6 | G6 | B | C | B | B | → | B |  | M3 ¦ Facility radio system ¦ Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | Best fit MAH barrier, arguable whether the same ranking required onshore vs. offshore
FA_SQTP | COMPUTER PERIPHERAL | 104 | H7 | H7 | H7 | H7 | C | C | C | C | → | C |  |  | #N/A | None selected, assumed to have no MAH role
FA_SQTS | TELEPHONE OR MULTIMEDIA EQUIPMENT | 78 | G6 | H6 | H6 | G6 | B | C | C | B | → | B |  |  | #N/A | None selected, assumed to have no MAH role, but note is a mix of IP phones and Ex phones internal and external
FA_SQTV | CCTV CAMERA UNIT | 101 | H7 | H7 | H7 | H7 | C | C | C | C | → | C |  |  | #N/A | None selected, assumed to have no MAH role
FA_SQTW | WIRELESS COMMUNICATION OR CONTROL EQUIPMENT | 17 | F6 | H6 | G6 | H6 | B | C | B | C | → | B |  | M3 ¦ Electronic Muster System ¦ Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | All tags in this code are currently part of the access control system, so could be argued to constitute and electronic muster system, but this would need confirming. (Plus if they stop working, likely to be noticed immediately?)
FA_SQTY | RECEIVER / TRANSMITTER | 4 | E7 | H7 | G7 | G7 | A | C | B | B | → | A |  | M6 ¦ Fire & Gas systems ¦ Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | Code assigned to gas detectors.
FA_SYLH | SYSTEM LEVEL HIERARCHY | 308 | H3 | H3 | H3 | H3 | C | C | C | C | → | C |  |  | #N/A | None selected, non-physical code
FA_WEHY | CONVEYOR | 2 | H6 | H6 | H6 | H6 | C | C | C | C | → | C |  |  | #N/A | None selected
Note on C4: Douglas Crooke: after excluding Integrity Only codes
Note on F4: Financial
Note on G4: Non-Financial

## Systems
[17 empty] | System Criticalities for Tags |  | Final Criticalities for Tags
[17 empty] | Counts: A=11352 B=24327 C=1317 |  | Counts are: A=3273 B=12561 C=21162
Reference Data from ASSET-C | [6 empty] | INPUT FIELDS |  |  |  | Calculated / Output Fields | [5 empty] | A=30% B=65% C=3% |  | Percentages are: A=9% B=33% C=56%
[18 empty] | BP Comments on Rev0 Criticality Selection for Systems |  | Original Values prior to comments
Functional location | Function Location Description | System No | Tag Abbreviation | Utilities System YorN | Comment | Tags in System | S | E | P | B | Criticality S | Criticality E | Criticality P | Criticality B | Leading to | Criticality Overall | Notes on Criticality Selection | BP COMMENTS | Changes made in response to comments | S_Rev0 | E_Rev0 | P_Rev0 | B_Rev0 | Notes_Rev0_to_3.0 | Column1 | MAH barrier(s) applicable | MAH Barrier Criticality | Comment on MAH Barriers
SYSTEM-00 | GENERAL / NON SPECIFIC SYSTEM SYS 00 | 00 | SYS | N |  | 1 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | General Notes on approach to assessment. Based on initial discussion, GF & R are treated as a single unit, i.e. there is no attempt to split out events into GF and R having different impact levels on either asset. Therefore a common production rate figure is used based on combined production levels of $1million per day shutdown of Raven, $200,000 per day shutdown of GF, i.e. all assessment is based on $1.2M/day of loss. Put another way, a system event is treated as affecting both sites and common production. Loss of a system is considered largely in terms of its primary function / objective, so production focussed systems are not treated as having a safety function, and are assumed to generate a safe shutdown when losing their primary function. e.g. Loss of reception facilities function causes loss of production but has no direct safety impact. Loss of a safety system (e.g. firewater) is considered as having a safety impact and may also have a knock-on production impact if unavailable. At system level this generally leaves a low environmental impact, as systems are assumed to shutdown without loss of containment (no System has and environmental criticality of A) | 1.) GF&R are separate non-identical production trains processing gases from separate fields. Impacts on these trains from other utility and process systems failures are not always common and need to be assessed. 2.) The primary function assumption is absoluely fine, however an open mind needs to be kept as to the 4 corresponding impacts. The example here about firewater having primarily a safety impact is interesting because for onshore gas plants most of the fire hazards are not managed with deluge or fire water. 3.) Environmentally speaking any failure (and there are some on WND) leading to flaring \ venting events needs to have it's impacts assessed. 4.) Large amount of copy\paste errors in Notes and they don't match the scoring. 5.) Common usage of the "Very Likely" - 7 score which looks excessive. 6.) Environmental impacts are typically lower inside the plant if they are captured in a drain or bund system. There could be safety impacts however. | Added new valid Risk input of "Not Assessed" and updated calcs so that this will propagate into codes so can be caught and reviewed rather than defaulting to a "C" which they were doing to ensure all codes were valid. Not Assessed now applied to all those systems where no assessment made. These codes will now be excluded form A,B,C counts without creating an #N/A error in the counts. | H3 | H3 | H3 | H3 | General Notes on approach to assessment. Based on initial discussion, GF & R are treated as a single unit, i.e. there is no attempt to split out events into GF and R having different impact levels on either asset. Therefore a common production rate figure is used based on combined production levels of $1million per day shutdown of Raven, $200,000 per day shutdown of GF, i.e. all assessment is based on $1.2M/day of loss. Put another way, a system event is treated as affecting both sites and common production. Loss of a system is considered largely in terms of its primary function / objective, so production focussed systems are not treated as having a safety function, and are assumed to generate a safe shutdown when losing their primary function. e.g. Loss of reception facilities function causes loss of production but has no direct safety impact. Loss of a safety system (e.g. firewater) is considered as having a safety impact and may also have a knock-on production impact if unavailable. At system level this generally leaves a low environmental impact, as systems are assumed to shutdown without loss of containment (no System has and environmental criticality of A) |  | None | #N/A
SYSTEM-01 | RESERVED FOR SUBSEA USE | 01 | SYS | N | System Not in Use | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed | No Comment. |  | H3 | H3 | H3 | H3 | Not assessed |  |  |  |  | #REF!
SYSTEM-02 | RESERVED FOR SUBSEA USE | 02 | SYS | N | System Not in Use | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed | No Comment. |  | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-03 | RESERVED FOR SUBSEA USE | 03 | SYS | N | System Not in Use | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed | No Comment. |  | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-04 | RESERVED FOR SUBSEA USE | 04 | SYS | N | System Not in Use | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed | No Comment. |  | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-05 | CONTROL UMBILICALS AND HPU SYS 05 | 05 | SYS | N |  | 222 | H7 | H7 | F7 | G7 | C | C | A | B | → | A | Loss of system primary function = assumes shutdown of subsea valves etc, no forward flow and loss of production output. Safety - minimal impact on assumption of safe shutdown Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen multiple times in life of facility (7) Note: this review applies to failures of the onshore side of the system boundary only, not the offshore. IE HPU. | Comment: Note this review applies to failures of the onshore side of the system boundary only, not the offshore. IE HPU. S = OK E = OK P = OK B = OK | Added comment to end of Notes | H7 | H7 | F7 | G7 | Loss of system primary function = assumes shutdown of subsea valves etc, no forward flow and loss of production output. Safety - minimal impact on assumption of safe shutdown Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen multiple times in life of facility (7) |  | P4 ¦ Subsea Integrity ¦ Subsea Hydraulic Power Unit | A | Subsea Umbilicals rated B as an alternative, chose HPU as this is rated A an presumably the main accessible component from onshore.
SYSTEM-06 | RESERVED FOR SUBSEA USE | 06 | SYS | N | System Not in Use | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added to this system. | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-07 | RESERVED FOR SUBSEA USE | 07 | SYS | N | System Not in Use | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added to this system. | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-08 | RESERVED FOR SUBSEA USE | 08 | SYS | N | System Not in Use | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added to this system. | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-09 | RESERVED FOR SUBSEA USE | 09 | SYS | N | System Not in Use | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added to this system. | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-10 | RESERVED FOR SUBSEA USE | 10 | SYS | N | System Not in Use | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added to this system. | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-11 | RESERVED FOR SUBSEA USE | 11 | SYS | N | System Not in Use | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added to this system. | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-12 | RESERVED FOR SUBSEA USE | 12 | SYS | N | System Not in Use | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added to this system. | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-13 | SUBSEA - WELLHEAD AND TEST SEPARATOR | 13 | SYS | N |  | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed - No Tags in System 13 | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added to this system. | H3 | H3 | H3 | H3 | Not assessed - No Tags in System 13 |  | P4 ¦ Subsea Integrity ¦ Production Tree | A | Nearest equivalent MAH
SYSTEM-14 | RESERVED FOR SUBSEA USE | 14 | SYS | N | System Not in Use | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added to this system. | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-15 | RESERVED FOR SUBSEA USE | 15 | SYS | N | System Not in Use | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added to this system. | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-16 | RESERVED FOR SUBSEA USE | 16 | SYS | N | System Not in Use | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added to this system. | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-17 | RESERVED FOR SUBSEA USE | 17 | SYS | N | System Not in Use | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added to this system. | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-18 | RESERVED FOR SUBSEA USE | 18 | SYS | N | System Not in Use | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added to this system. | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-19 | RESERVED FOR SUBSEA USE | 19 | SYS | N | System Not in Use | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed | Comment: S = E = P = B = | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added to this system. | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-20 | PROCESS SEPARATION SYS 20 | 20 | SYS | N |  | 1750 | H5 | G5 | F5 | G5 | C | C | B | C | → | B | Loss of system primary function = no production feed into rest of system, loss of production output. Safety - minimal impact on assumption of safe shutdown Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen in life of 10 similar facilities (5) BP Feedback: There are 2 independent separation systems (Raven=660mmscfd & GF=438mmscfd). The liklihood of both failing simultaneously leading to total production loss is therefore probably not "Very Likely". Please revise this to "Possible" which is score of 5. Failure would also lead to venting \ flaring. | Comment: There are 2 independent separation systems (Raven=660mmscfd & GF=438mmscfd). The liklihood of both failing simultaneously leading to total production loss is therefore probably not "Very Likely". Please revise this to "Possible" which is score of 5. Failure would also lead to venting \ flaring. S = H5 = C E = G5 = C P = F5 = B B = G5 = C | Updated risks in line with guidance, updated Notes with some of the comments | H7 | H7 | F7 | G7 | Loss of system primary function = no production feed into rest of system, loss of production output. Safety - minimal impact on assumption of safe shutdown Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen multiple times in life of facility (7) |  | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | This MAH used for all main gas containing systems
SYSTEM-21 | PROCESS CONDENSATE HANDLING SYS 21 | 21 | SYS | N |  | 1688 | H6 | H6 | F6 | G6 | C | C | B | B | → | B | Loss of system primary function = no production feed into rest of system, loss of production output. Safety - minimal impact on assumption of safe shutdown Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen once or twice in life of facility (6) BP Feedback: This affects abilty to remove condensate from vessels and within a few hours would cause a total production loss because as the system is common to Raven and GF. Given the few hours of "ullage" there is a possiblity to try to avoid total plant shutdown and because of this the liklihood is therefore probably not "Very Likely". Please revise this to "Likely" which is score of 6. | Comment: This affects abilty to remove condensate from vessels and within a few hours would cause a total production loss because as the system is common to Raven and GF. Given the few hours of "ullage" there is a possiblity to try to avoid total plant shutdown and because of this the liklihood is therefore probably not "Very Likely". Please revise this to "Likely" which is score of 6. S = H6 = C E = H6 = C P = F6 = B B = G6 = B | Updated risks in line with guidance, updated Notes with some of the comments | H7 | H7 | F7 | G7 | Loss of system primary function = no production feed into rest of system, loss of production output. Safety - minimal impact on assumption of safe shutdown Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen multiple times in life of facility (7) |  | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | This MAH used for all main gas containing systems
SYSTEM-22 | PROCESS RECEPTION SYS 22 | 22 | SYS | N |  | 315 | H5 | G5 | F5 | G5 | C | C | B | C | → | B | Loss of system primary function = no production feed into rest of system, loss of production output. Safety - minimal impact on assumption of safe shutdown Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to occur in life of 10 facilities (5) BP Feedback: This is a Raven related system only. Primary function is simple and robust and also parts of the system (pig receivers) are not required for production. Because of this the liklihood is therefore probably not "Very Likely". Please revise this to "Possible" which is score of 5. Flaring of inventory inside plant boundary is a possibility but not flaring of whole pipeline). | Comment: This is a Raven related system only. Primary function is simple and robust and also parts of the system (pig receivers) are not required for production. Because of this the liklihood is therefore probably not "Very Likely". Please revise this to "Possible" which is score of 5. Flaring of inventory inside plant boundary is a possibility but not flaring of whole pipeline). S = H5 = C E = G5 = C P = F5 = B B = G5 = C | Updated risks in line with guidance, updated Notes with some of the comments | H7 | H7 | F7 | G7 | Loss of system primary function = no production feed into rest of system, loss of production output. Safety - minimal impact on assumption of safe shutdown Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen multiple times in life of facility (7) |  | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | This MAH used for all main gas containing systems
SYSTEM-23 | PROCESS COMPRESSION MAIN | 23 | SYS | N |  | 7 | H3 | H3 | F3 | G3 | C | C | C | C | → | C | Possibly misleading-named system, only non SYLH tags are junction boxes (main/export compression in System 27) As these are digital junction boxes, assuming that loss of one might generate a trip through signal loss, but at low likelihood (e.g. truck runs into junction box) Loss of system primary function = loss of signal data, potentially leading to production trip and time to identify and reinstate. Safety - minimal impact on assumption of safe shutdown Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered unlikely, a similar event has occurred somewhere in industry (3) | GF | At time of review, looks like System 23 mis-named - main export compression in System 27, and only 10 tags in this system, junction boxes and a few SYLH tags, no System Operating Guide. Likelihood of loss reduced to on arguments added to comments. | H7 | H7 | F7 | G7 | Loss of system primary function = no production feed into rest of system, loss of production output. Safety - minimal impact on assumption of safe shutdown Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen multiple times in life of facility (7) |  | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | This MAH used for all main gas containing systems
SYSTEM-24 | FLASH GAS COMPRESSION SYS 24 | 24 | SYS | N |  | 1895 | H7 | G7 | H7 | G7 | C | B | C | B | → | B | Loss of system primary function =Flash gas not compressed and lost to flare, with increased flare emissions, but production can continue. Safety - minimal impact on assumption of safe shutdown Environment - minimal impact on assumption of safe shutdown, but flare emissions increased for duration of outage. Production - not directly impacted by loss of flash gas compression = impact level H Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen multiple times in life of facility (7) BP Feedback incorporated: This is a Raven related system only and is not required for production, however there will be a need to flare limited volumes of flash gases during repair of system. Liklihood is ok at 7, however production impacts are lower than assessed. | Comment: This is a Raven related system only and is not required for production, however there will be a need to flare limited volumes of flash gases during repair of system. Liklihood is ok at 7, however production impacts are lower than assessed. S = H7 = C E = G7 = B P = H7 = C B = G7 = B | Risk inputs updated, comments added to notes | H7 | H7 | F7 | G7 | Loss of system primary function = no production feed into rest of system, loss of production output. Safety - minimal impact on assumption of safe shutdown Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen multiple times in life of facility (7) |  | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | This MAH used for all main gas containing systems
SYSTEM-25 | GAS TREATMENT SYS 25 | 25 | SYS | N |  | 2526 | H5 | H5 | F5 | H5 | C | C | B | C | → | B | Loss of system primary function = no production feed into rest of system, loss of production output. Safety - minimal impact on assumption of safe shutdown Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to occur in life of 10 facilitie (5) BP Feedback incorporated: There are 2 independent gas treatment systems and a 250mmscfd crossover line. Therefore the liklihood of both failing simultaneously leading to total production loss (due to not meeting spec) is probably not "Very Likely". Please revise this to "Possible" which is score of 5 | Comment: There are 2 independent gas treatment systems and a 250mmscfd crossover line. Therefore the liklihood of both failing simultaneously leading to total production loss (due to not meeting spec) is probably not "Very Likely". Please revise this to "Possible" which is score of 5. S = H5 = C E = G5 = C P = F5 = B B = G5 = C | risk updated in line with guidance and comments added to notes. | H7 | H7 | F7 | G7 | Loss of system primary function = no production feed into rest of system, loss of production output. Safety - minimal impact on assumption of safe shutdown Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen multiple times in life of facility (7) |  | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | This MAH used for all main gas containing systems
SYSTEM-26 | RESERVED FOR ONSHORE USE | 26 | SYS | N | System Not in Use | 0 | H3 | H3 | H3 | H3 | None | None | None | None | → | None | Not assessed | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added to this system. | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-27 | GAS EXPORT SYS 27 | 27 | SYS | N |  | 1155 | H6 | H6 | F6 | G6 | C | C | B | B | → | B | Loss of system primary function = no production feed into rest of system, loss of production output. Safety - minimal impact on assumption of safe shutdown Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen multiple times in life of facility (6) BP Feedback incorporated: There are 2 gas exports and a small crossover line. Therefore the liklihood of both failing simultaneously leading to total production loss is probably not "Very Likely". GF compressors are in this system though. Please revise this to "Likely" which is score of 6. | Comment: There are 2 gas exports and a small crossover line. Therefore the liklihood of both failing simultaneously leading to total production loss is probably not "Very Likely". GF compressors are in this system though. Please revise this to "Likely" which is score of 6. S = H6 = C E = H6 = C P = F6 = B B = G6 = B | Risks update in line with guidance, comments added to Notes | H7 | H7 | F7 | G7 | Loss of system primary function = no production feed into rest of system, loss of production output. Safety - minimal impact on assumption of safe shutdown Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen multiple times in life of facility (7) |  | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | This MAH used for all main gas containing systems
SYSTEM-28 | RICH MEG SYS 28 | 28 | SYS | N |  | 2146 | H6 | H6 | F6 | G6 | C | C | B | B | → | B | Loss of system primary function = unable to meet export gas spec leading to shutdown of production Safety - minimal impact on assumption of safe shutdown Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen once or twice in life of facility (6) B Feedback incorporated: System contains the Rich MEG tanks which are common to GF&R, however GF wells have a lower dependency on MEG and may be able to operate longer without Rich MEG collection. Please revise this to "Likely" which is score of 6. | Comment: System contains the Rich MEG tanks which are common to GF&R, however GF wells have a lower dependency on MEG and may be able to operate longer without Rich MEG collection. Please revise this to "Likely" which is score of 6. S = H6 = C E = H6 = C P = F6 = B B = G6 = B | Risks update in line with guidance, comments added to Notes | H7 | H7 | F7 | G7 | Loss of system primary function = unable to meet export gas spec leading to shutdown of production Safety - minimal impact on assumption of safe shutdown Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen multiple times in life of facility (7) |  | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | This MAH used for all main gas containing systems. Assuming sufficient gas in liquid for this system to match this MAH barrier
SYSTEM-29 | LEAN MEG SYS 29 | 29 | SYS | N |  | 772 | H6 | H6 | F6 | G6 | C | C | B | B | → | B | Loss of system primary function = unable to meet export gas spec leading to shutdown of production Safety - minimal impact on assumption of safe shutdown Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen multiple times in life of facility (6) BP Feedback incorporated: System is common to GF&R, however GF wells have a lower dependency on MEG and may be able to operate longer without Lean MEG supply. MEG is mitigation for Hydrates. Please revise this to "Likely" which is score of 6. | Comment: System is common to GF&R, however GF wells have a lower dependency on MEG and may be able to operate longer without Lean MEG supply. MEG is mitigation for Hydrates. Please revise this to "Likely" which is score of 6. S = H6 = C E = H6 = C P = F6 = B B = G6 = B | Risks update in line with guidance, comments added to Notes | H7 | H7 | F7 | G7 | Loss of system primary function = unable to meet export gas spec leading to shutdown of production Safety - minimal impact on assumption of safe shutdown Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen multiple times in life of facility (7) |  | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | This MAH used for all main gas containing systems. Assuming sufficient gas in liquid for this system to match this MAH barrier
SYSTEM-30 | MEG REGENERATION SYS 30 | 30 | SYS | N |  | 3451 | H5 | H5 | F5 | G5 | C | C | B | C | → | B | Loss of system primary function = unable to meet export gas spec leading to shutdown of production Safety - minimal impact on assumption of safe shutdown Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to occur in life of 10 similar facilities (5) BP Feedback incorporated: System is common to GF&R, however there is about a 7 day tank inventory which allows production to continue whilst contigencies are brought into place. Please revise this to "Possible" which is score of 5. | Comment: System is common to GF&R, however there is about a 7 day tank inventory which allows production to continue whilst contigencies are brought into place. Please revise this to "Possible" which is score of 5. S = H5 = C E = H5 = C P = F5 = B B = G5 = C | Risks update in line with guidance, comments added to Notes | H7 | H7 | F7 | G7 | Loss of system primary function = unable to meet export gas spec leading to shutdown of production Safety - minimal impact on assumption of safe shutdown Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen multiple times in life of facility (7) |  | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | This MAH used for all main gas containing systems. Assuming sufficient gas in liquid for this system to match this MAH barrier Parts of system operate at >120°C, which is a second A typical criticality for pressurised equipment.
SYSTEM-31 | RESERVED FOR ONSHORE USE | 31 | SYS | N | System Not in Use | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added to this system. | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-32 | RESERVED FOR ONSHORE USE | 32 | SYS | N | System Not in Use | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added to this system. | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-33 | RESERVED FOR ONSHORE USE | 33 | SYS | N | System Not in Use | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added to this system. | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-34 | RESERVED FOR ONSHORE USE | 34 | SYS | N | System Not in Use | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added to this system. | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-35 | RESERVED FOR ONSHORE USE | 35 | SYS | N | System Not in Use | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added to this system. | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-36 | RESERVED FOR ONSHORE USE | 36 | SYS | N | System Not in Use | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added to this system. | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-37 | RESERVED FOR ONSHORE USE | 37 | SYS | N | System Not in Use | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added to this system. | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-38 | RESERVED FOR ONSHORE USE | 38 | SYS | N | System Not in Use | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added to this system. | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-39 | RESERVED FOR ONSHORE USE | 39 | SYS | N | System Not in Use | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added to this system. | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-40 | LP FUEL GAS SYS 40 | 40 | SYS | N |  | 214 | E6 | G6 | F6 | G6 | A | B | B | B | → | A | Loss of system primary function = loss of main power generation cascading to production shutdown of Raven Safety - Loss of fuel gas blanketing in MEG tanks, leading to explosion/fire 1-2 death potential at lower probability Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen once or twice in life of facility (6) BP Feedback: System is Raven only. Impact is Loss of Raven production. Fired heaters cannot run. Blanket on tanks is affected, which increases safety risk because of vacuum. Flare is N2 so not affected. Thermal oxidixer cannot run causing extra gases to flare \ vent. Raven Flare pilots will not light and need to switch to propane option. Please revise this to "Likely" which is score of 6. | Comment: System is Raven only. Impact is Loss of Raven production. Fired heaters cannot run. Blanket on tanks is affected, which increases safety risk because of vacuum. Flare is N2 so not affected. Thermal oxidixer cannot run causing extra gases to flare \ vent. Raven Flare pilots will not light and need to switch to propane option. Please revise this to "Likely" which is score of 6. S = E6 = A E = G6 = B P = F6 = B B = G6 = B | Input fields updated in line with BP feedback and comment added to notes | E4 | H7 | F7 | G7 | Loss of system primary function = loss of main power generation cascading to production shutdown. Safety - Loss of fuel gas blanketing in MEG tanks, leading to explosion/fire 1-2 death potential at lower probability Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen multiple times in life of facility (7) |  | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | This MAH used for all main gas containing systems
SYSTEM-41 | PROCESS - HP WET FLARE | 41 | SYS | N |  | 158 | E6 | G6 | F6 | G6 | A | B | B | B | → | A | Loss of system primary function = loss of safe route for hydrocarbon disposal Safety - various potential impacts due to interconnections, bad things happen - E as maximum safety impact Environment - future impact with localized damage to non-sensitive environment restorable in weeks Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - short term diversion of senior management to manage issue/event Likelihood - considered likely to happen once or twice in life of facility (6) System is GF only. Impact is Loss of GF production. Various safety impacts because of flare interconnections. Please revise this to "Likely" which is score of 6. | Comment: System is GF only. Impact is Loss of GF production. Why power gen? Various safety impacts because of flare interconnections. Please revise this to "Likely" which is score of 6. S = E6 = A E = G6 = B P = F6 = B B = G6 = B | Notes description change as was referring to power gen incorrectly, risk updated in line with guidance. Part comments added to notes | E6 | H6 | F6 | F6 | Loss of system primary function = loss of main power generation cascading to production shutdown. Safety - Loss of fuel gas blanking in drains treatment, leading to explosion/fire 1-2 death potential at lower probability Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - short term diversion of senior management to manage issue/event Likelihood - considered likely to happen once or twice in life of facility (7) |  | P5 ¦ Blowdown vent and flare ¦ Flare pipework and headers (align with barrier P4) | A | Assuming here could also be considered as gas containing under P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C and hence is aligned to A criticality
SYSTEM-42 | PROCESS - HP FLARE | 42 | SYS | N |  | 678 | E6 | G6 | F6 | G6 | A | B | B | B | → | A | Loss of system primary function = safe disposal route for hydrocarbon vapours, with potential for local explosion or fire Safety - Uncontrolled gas build up leading to explosion/fire 1-2 death potential Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - short term diversion of senior management to manage issue/event Likelihood - considered likely to happen once or twice in life of facility (6) BP feedback incorporated: System is mostly common. Impact is Loss of all production. Various safety impacts because of flare interconnections. Please revise this to "Likely" which is score of 6. | Comment: System is mostly common. Impact is Loss of all production. Why power gen? Various safety impacts because of flare interconnections. Please revise this to "Likely" which is score of 6. S = E6 = A E = G6 = B P = F6 = B B = G6 = B | Notes description change as was referring to power gen incorrectly, risk updated in line with guidance. Part comments added to notes | E6 | H6 | F6 | F6 | Loss of system primary function = loss of main power generation cascading to production shutdown. Safety - Loss of fuel gas blanking in drains treatment, leading to explosion/fire 1-2 death potential at lower probability Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - short term diversion of senior management to manage issue/event Likelihood - considered likely to happen once or twice in life of facility (7) |  | P5 ¦ Blowdown vent and flare ¦ Flare pipework and headers (align with barrier P4) | A | Assuming here could also be considered as gas containing under P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C and hence is aligned to A criticality
SYSTEM-43 | PROCESS - VENT AND BLOW DOWN | 43 | SYS | N |  | 171 | E6 | G6 | F6 | F6 | A | B | B | B | → | A | Loss of system primary function = Loss of safe disposal route for hydrocarbons, leading to Safety - to potential for explosion/fire 1-2 death potential Environment - Future impact with localized damage to a non sensitive environment restorable within weeks - G Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - short term diversion of senior management to manage issue/event - F Likelihood - considered likely to happen once or twice in life of facility (6) BP Feedback incorporated: System is GF only. Impact is Loss of GF production. Various safety impacts because of flare interconnections. | Comment: System is GF only. Why power gen? Impact is Loss of GF production. Various safety impacts because of flare interconnections. S = E6 = A E = G6 = B P = F6 = B B = F6 = B | Changes to notes, risk input updated iin line with guidance, comments added to Notes. | E6 | H6 | F6 | F6 | Loss of system primary function = loss of main power generation cascading to production shutdown. Safety - Loss of fuel gas blanking in drains treatment, leading to explosion/fire 1-2 death potential at lower probability Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - short term diversion of senior management to manage issue/event Likelihood - considered likely to happen once or twice in life of facility (7) |  | P5 ¦ Blowdown vent and flare ¦ Flare pipework and headers (align with barrier P4) | A | Assuming here could also be considered as gas containing under P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C and hence is aligned to A criticality
SYSTEM-44 | PROCESS - LP FLARE | 44 | SYS | N |  | 431 | E6 | G6 | F6 | F6 | A | B | B | B | → | A | Loss of system primary function = Loss of safe disposal route for hydrocarbons, leading to Safety - to potential for explosion/fire 1-2 death potential Environment - Future impact with localized damage to a non sensitive environment restorable within weeks - G Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - short term diversion of senior management to manage issue/event - F Likelihood - considered likely to happen once or twice in life of facility (6) BP Feedback incorporated: System is GF only. Impact is Loss of GF production. Various safety impacts because of flare interconnections. | Comment: System is GF only. Why power gen? Impact is Loss of GF production. Various safety impacts because of flare interconnections. S = E6 = A E = G6 = B P = F6 = B B = F6 = B | Changes to notes, risk input updated iin line with guidance, comments added to Notes. | E6 | H6 | F6 | F6 | Loss of system primary function = loss of main power generation cascading to production shutdown. Safety - Loss of fuel gas blanking in drains treatment, leading to explosion/fire 1-2 death potential at lower probability Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - short term diversion of senior management to manage issue/event Likelihood - considered likely to happen once or twice in life of facility (7) |  | P5 ¦ Blowdown vent and flare ¦ Flare pipework and headers (align with barrier P4) | A | Assuming here could also be considered as gas containing under P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C and hence is aligned to A criticality
SYSTEM-45 | UTILITIES - FUEL GAS | 45 | SYS | N |  | 381 | E6 | G6 | F6 | G6 | A | B | B | B | → | A | Loss of system primary function = loss of fuel gas supplies to users on GF (although Raven can supply GF as a non-normal operating mode, auto-switching on pressure control) Safety - Loss of fuel gas blanketing in MEG tanks, leading to explosion/fire 1-2 death potential at lower probability - E. Likelihood of this event is reduced because only happens if Raven unavailable coincident with failure on GF, on basis Raven offline 3-30days per year gives 10x reduction in likelihood. Environment - minimal impact on assumption of safe shutdown - H Production - No immediate impact, automatic re-sourcing from Raven if it is online and supply pressure drops = impact level H on asusmption Raven available Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen once or twice in life of facility (6) BP Feedback incorporated: System is GF only. Review the scores vs. the notes. Liklihood looks more like 6. | Comment: System is GF only. Review the scores vs. the notes. Liklihood looks more like 6. One impact has unlikely and others very likely? | Intent was E4 to represent lower likelihood of explosion following loss of fuel gas, but reset likelihood for consistency. SOG indicates GF normally supplies GF & R, but R can supply GF as alternate configuration, so redundancy should minimise production impact of this single system failure. Production impact minimal as automatic pressure control should switch supply when required. Inputs copied from System 40 fuel gas for consistency as GF is normal supply whilst Raven is backup. | E4 | H7 | F7 | G7 | Loss of system primary function = loss of main power generation cascading to production shutdown. Safety - Loss of fuel gas blanketing in MEG tanks, leading to explosion/fire 1-2 death potential at lower probability Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen multiple times in life of facility (7) |  | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | This MAH used for all main gas containing systems
SYSTEM-46 | UTILITIES - FUEL GAS HP | 46 | SYS | N |  | 777 | E6 | G6 | F6 | G6 | A | B | B | B | → | A | Loss of system primary function = loss of fuel gas supplies to users on GF & Raven Safety - Loss of fuel gas blanketing in MEG tanks, leading to explosion/fire 1-2 death potential at lower probability - E. Environment - low impact on assumption of safe shutdown - future impact with localized damage to non-sensitive environment restorable in days or weeks- G Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen once or twice in life of facility (6) BP Feedback incorporated: System is mostly common. Impact is Loss of all production. Various safety impacts because of flare interconnections. Liklihood looks more like 6. | Comment: System is mostly common. Impact is Loss of all production. Various safety impacts because of flare interconnections. Liklihood looks more like 6. One impact has unlikely and others very likely? | Inputs copied from System 40. | E4 | H7 | F7 | G7 | Loss of system primary function = loss of main power generation cascading to production shutdown. Safety - Loss of fuel gas blanketing in MEG tanks, leading to explosion/fire 1-2 death potential at lower probability Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen multiple times in life of facility (7) |  | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | This MAH used for all main gas containing systems
SYSTEM-47 | CHEMICALS - METHANOL INJECTION | 47 | SYS | N |  | 544 | E5 | H5 | E5 | F5 | A | C | A | B | → | A | Loss of system primary function = unable to maintain hydrate free flow leading to blockage, reduce production flow and or shutdown and loss of flowline(s) Safety - Hydrates risk affects plant safety, assumed to have E level potential if unmitigated Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of weeks/months equivalent to fully recover from an event @ $400k/day, => impact level E range Business - Mid term diversion of local management to manage issue/event Likelihood - considered unlikely but could occur in lifetime of 10 similar facilities (5) BP Feedback: System is common. Required for well start-up and intermittent inejection onshore for hydrate remediation. There are impacts for production and safety. Total loss of production is unlikley because it is not continuously injected. Upon failure risk of hydrates affects the safety of the plant. MEG is the one that prevents flowline \ pipeline hydrate. | Comment: System is common. Required for well start-up and intermittent inejection onshore for hydrate remediation. There are impacts for production and safety. Total loss of production is unlikley because it is not continuously injected. Upon failure risk of hydrates affects the safety of the plant. MEG is the one that prevents flowline \ pipeline hydrate. | Safety impact increased to E in response to feedback | H5 | H5 | E5 | F5 | Loss of system primary function = unable to maintain hydrate free flow leading to blockage, reduce production flow and or shutdown and loss of flowline(s) Safety - Assumed minimal impact Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of weeks/months equivalent to fully recover from an event @ $400k/day, => impact level E range Business - Mid term diversion of local management to manage issue/event Likelihood - considered unlikely but could occur in lifetime of 10 similar facilities (5) |  | P4 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for highly toxic substances | A | Methanol is a hazardous chemical but arguably not 'highly toxic' in the terms used in the MAH barrier family typical criticalities, in which case this system is A criticality from its financial consequences
SYSTEM-48 | CHEMICALS - CORROSION INHIBITOR INJECTION | 48 | SYS | N |  | 1 | H5 | H5 | E5 | F5 | C | C | A | B | → | A | Loss of system primary function = Premature internal corrosion of process pipeline eventually requiring pipework replacement or removal from service impacting production Safety - Assumed minimal impact, RBI inspection prevents any LOPC. Environment - minimal impact on assumption of safe shutdown before LOPC Production - $1.2M per day shutdown, assumption of weeks/months equivalent to fully recover from an event @ $400k/day, => impact level E range Business - Mid term diversion of local management to manage issue/event Likelihood - considered unlikely but could occur in lifetime of 10 similar facilities (5) | Are there any tags here. Process Engineer though all chemicals were in 51. | One piping tag (+ 3 SYLH) in this system R-CL-48-001 (which will be removed from Equipment Criticality scope anyway, so change to not assessed in case any future ones added back in. | H5 | H5 | E5 | F5 | Loss of system primary function = Premature internal corrosion of process pipeline eventually requiring pipework replacement or removal from service impacting production Safety - Assumed minimal impact, RBI inspection prevents any LOPC. Environment - minimal impact on assumption of safe shutdown before LOPC Production - $1.2M per day shutdown, assumption of weeks/months equivalent to fully recover from an event @ $400k/day, => impact level E range Business - Mid term diversion of local management to manage issue/event Likelihood - considered unlikely but could occur in lifetime of 10 similar facilities (5) |  |  | #N/A | No system operating guide available to consult, no appropriate MAH barrier identified.
SYSTEM-49 | CHEMICALS - KINETIC INHIBITOR INJECTION | 49 | SYS | N |  | 0 | H5 | H5 | E5 | F5 | None | None | None | None | → | None | Loss of system primary function = assumed similar to methanol as a hydrate inhibitor Safety - Assumed minimal impact, RBI inspection prevents any LOPC. Environment - minimal impact on assumption of safe shutdown before LOPC Production - $1.2M per day shutdown, assumption of weeks/months equivalent to fully recover from an event @ $400k/day, => impact level E range Business - Mid term diversion of local management to manage issue/event Likelihood - considered unlikely but could occur in lifetime of 10 similar facilities (5) | Are there any tags here. Process Engineer though all chemicals were in 51. | Only 3 FA_SYLH codes currently in, will now show as None | H5 | H5 | E5 | F5 | Loss of system primary function = assumed similar to methanol as a hydrate inhibitor Safety - Assumed minimal impact, RBI inspection prevents any LOPC. Environment - minimal impact on assumption of safe shutdown before LOPC Production - $1.2M per day shutdown, assumption of weeks/months equivalent to fully recover from an event @ $400k/day, => impact level E range Business - Mid term diversion of local management to manage issue/event Likelihood - considered unlikely but could occur in lifetime of 10 similar facilities (5) |  | P4 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for highly toxic substances | A | No system operating guide available to consult, so choosing to treat this as similar to Methanol Injection, This may be overrating the MAH hazard in this case, depending on chemicals in use, and their hazard relative to Methanol.
SYSTEM-50 | CHEMICALS - REVERSE EMULSION BREAKER | 50 | SYS | N |  | 0 | H5 | H5 | F5 | G5 | None | None | None | None | → | None | Loss of system primary function = reduced throughput through slower separation (no reference documentation found to understand this one) Safety - Assumed minimal impact. Environment - minimal impact on assumption of safe shutdown before discharge of out of spec fluids. Production - $1.2M per day shutdown, assumption of 8 hours to recover from an incident ($400k), => impact level F range Business - Mid term diversion of local management to manage issue/event Likelihood - considered unlikely but could occur in lifetime of 10 similar facilities (5) | Are there any tags here. Process Engineer though all chemicals were in 51. | Only 3 FA_SYLH codes currently in, will now show as None | H5 | H5 | F5 | G5 | Loss of system primary function = reduced throughput through slower separation (no reference documentation found to understand this one) Safety - Assumed minimal impact. Environment - minimal impact on assumption of safe shutdown before discharge of out of spec fluids. Production - $1.2M per day shutdown, assumption of 8 hours to recover from an incident ($400k), => impact level F range Business - Mid term diversion of local management to manage issue/event Likelihood - considered unlikely but could occur in lifetime of 10 similar facilities (5) |  |  | #N/A | No system operating guide available to consult, no appropriate MAH barrier identified.
SYSTEM-51 | CHEMICAL INJECTION SYS 51 | 51 | SYS | N |  | 261 | H6 | H6 | F6 | G6 | C | C | B | B | → | B | Loss of system primary function = reduced throughput through slower separation Safety - Assumed minimal impact. Environment - minimal impact on assumption of safe shutdown before discharge of out of spec fluids. Production - $1.2M per day shutdown, assumption of 8 hours to recover from an incident ($400k), => impact level F range Business - Mid term diversion of local management to manage issue/event Likelihood - considered unlikely but could occur in lifetime of facility (6) | Need to see the breakdown in here. Production chemicals are all here? | Only piping tags (which are about to be ignored) show chemicals in them, so difficult to tell. | H6 | H6 | F6 | G6 | Loss of system primary function = reduced throughput through slower separation Safety - Assumed minimal impact. Environment - minimal impact on assumption of safe shutdown before discharge of out of spec fluids. Production - $1.2M per day shutdown, assumption of 8 hours to recover from an incident ($400k), => impact level F range Business - Mid term diversion of local management to manage issue/event Likelihood - considered unlikely but could occur in lifetime of facility (6) |  |  | #N/A | No MAH barrier identified. Chemicals considered Hazardous but not highly toxic
SYSTEM-52 | MEG CHEMICAL INJECTION SYS 52 | 52 | SYS | N |  | 1109 | H5 | H5 | F5 | G5 | C | C | B | C | → | B | Loss of system primary function = reduced throughput through slower separation ofwater from gas due to MEG contamination / deterioration. Safety - Assumed minimal impact. Environment - minimal impact on assumption of safe shutdown before discharge of out of spec fluids. Production - $1.2M per day shutdown, assumption of 8 hours to recover from an incident ($400k), => impact level F range Business - Mid term diversion of local management to manage issue/event Likelihood - considered unlikely but could occur in lifetime of 10 similar facilities (5) | Don't understand this one. MEG is for pipeline \ flowline assurance? | Changed initial description a bit. No changes to risk inputs. SOG intro is: System 52 contains chemicals (Hydrochloric Acid, Sodium Carbonate, Sodium Hydroxide Antifoam and Oxygen Scavenger), which are required to dose in MEG regeneration unit and Citric Acid which is required to clean heaters in MEG regeneration unit. The objective of system 52 can be divided into three section, i.e. offloading, storage and injection. | H5 | H5 | F5 | G5 | Loss of system primary function = reduced throughput through slower separation Safety - Assumed minimal impact. Environment - minimal impact on assumption of safe shutdown before discharge of out of spec fluids. Production - $1.2M per day shutdown, assumption of 8 hours to recover from an incident ($400k), => impact level F range Business - Mid term diversion of local management to manage issue/event Likelihood - considered unlikely but could occur in lifetime of 10 similar facilities (5) |  |  | #N/A | No MAH barrier identified. Chemicals considered Hazardous but not highly toxic
SYSTEM-53 | POTABLE WATER SYS 53 | 53 | SYS | Y |  | 306 | F6 | H6 | G6 | H6 | B | C | B | C | → | B | Loss of system primary function = lack of potable water to systems demand. Loss of supply to chemicals / slurry dilution, and water seal on LP flare stack. Safety - Assumed minimal impact from potable in isolation (drinking supplies will be bottled water) BUT supplies safety showers which would become unavailable. Environment - minimal impact on assumption of safe shutdown before discharge of out of spec fluids. Production - $1.2M per day shutdown, assumption of 8 hours to recover from an incident ($400k), => impact level G range Business - Mid term diversion of local management to manage issue/event Likelihood - considered could occur once or twice in lifetime of facility (6) | Mainly insignificant because mitigations are easy to put in place with tanker. Need to confirm if this actually affects the safety showers function. Do they have separate storage. | Removed reference to tankered supply, as SOG 53 indicates existing tank TK-5321 supplies GF users and Raven safety showers, supplied from existing town water supply. | F6 | H6 | G6 | H6 | Loss of system primary function = lack of potable water to systems demand (tankered supply). Loss of supply to chemicals / slurry dilution, and water seal on LP flare stack. Safety - Assumed minimal impact from potable in isolation (drinking supplies will be bottled water) BUT supplies safety showers which would become unavailable. Environment - minimal impact on assumption of safe shutdown before discharge of out of spec fluids. Production - $1.2M per day shutdown, assumption of 8 hours to recover from an incident ($400k), => impact level G range Business - Mid term diversion of local management to manage issue/event Likelihood - considered could occur once or twice in lifetime of facility (6) |  |  | #N/A | No MAH Barrier identified. Safety showers not mentioned in MAH barrier typical criticalities. Principal risk in SOG is legionella, managed by sampling and biocide treatment. Potable water supplies water to the seal on the LP flare stack
SYSTEM-54 | UTILITY WATER SYS 54 | 54 | SYS | Y |  | 314 | E6 | H6 | G6 | H6 | A | C | B | C | → | A | Loss of system primary function = Utility water tank also supplies firewater. Safety - Loss of firewater cover, potential for multiple fatalities. Environment - minimal impact on assumption of safe shutdown before discharge of out of spec fluids. Production - $1.2M per day shutdown, assumption of 8 hours to recover from an incident ($400k), => impact level G range Business - Mid term diversion of local management to manage issue/event Likelihood - considered could occur once or twice in lifetime of facility (5) | There are separate firewater tanks that make them independent of this system and have the capacity to match the hazard? | Looks like Raven has firewater storage tanks TK-8101/8102, filled from tanker, but single tank for GF taking town water, with tanker offloading option. | E6 | H6 | G6 | H6 | Loss of system primary function = Utility water tank also supplies firewater. Safety - Loss of firewater cover, potential for multiple fatalities. Environment - minimal impact on assumption of safe shutdown before discharge of out of spec fluids. Production - $1.2M per day shutdown, assumption of 8 hours to recover from an incident ($400k), => impact level G range Business - Mid term diversion of local management to manage issue/event Likelihood - considered could occur once or twice in lifetime of facility (5) |  |  | #N/A | No MAH Barrier identified. Safety showers not mentioned in MAH barrier typical criticalities. Principal risk in SOG is legionella, managed by sampling and biocide treatment. NB GF Utility water tank is a combined Utility and Firewater tank, which contributed to selecting A for safety.
SYSTEM-55 | CHEMICALS - MISCELLANEOUS | 55 | SYS | N |  | 0 | H6 | H6 | G6 | G6 | None | None | None | None | → | None | Loss of system primary function = Safety - Assume safe shutdown and no loss of containment. Environment - Release of chemicals within local environment, unlikely to spread offsite. Production - $1.2M per day shutdown, assumption of 6 hours to recover from an incident ($300k), => impact level G range Business - Mid term diversion of local management to manage issue/event Likelihood - considered could occur once or twice in lifetime of facility (6) | Are there any tags here. Process Engineer though all chemicals were in 51. | No non SYLH tags in system, will now show as None unless some added. | H6 | H6 | G6 | G6 | Loss of system primary function = Safety - Assume safe shutdown and no loss of containment. Environment - Release of chemicals within local environment, unlikely to spread offsite. Production - $1.2M per day shutdown, assumption of 6 hours to recover from an incident ($300k), => impact level G range Business - Mid term diversion of local management to manage issue/event Likelihood - considered could occur once or twice in lifetime of facility (6) |  |  | #N/A | No System Operating Guide available to review. No MAH barrier identified.
SYSTEM-56 | DRAINS - HAZARDOUS OPEN SYS 56 | 56 | SYS | N |  | 593 | G5 | G5 | G5 | G5 | C | C | C | C | → | C | Loss of system primary function = no safe route for contaminated water/ fluids Safety - Assume medium impact incident with personnel exposed to health effects. G Environment - Release of contaminated water, localized damage to non-sensitive environment restorable within days or weeks, unlikely to spread offsite. - G Production - $1.2M per day shutdown, assumption of 6 hours to recover from an incident ($300k), => impact level G range Business - Mid term diversion of local management to manage issue/event Likelihood - considered could occur once or twice in lifetime of facility (6) BP Feedback incorporated: common system. Mostly Maintenance water and rain. There is also a large pod for storage. Unlikle to impact production. Consider "possible" since it is a simple and robust system. | common system. Mostly Maintenance water and rain. There is also a large pod for storage. Unlikle to impact production. Consider "possible" since it is a simple and robust system. | Reduced likelihood to 5 in response to feedback. | G6 | G6 | G6 | G6 | Loss of system primary function = no safe route for contaminated water/ fluids Safety - Assume medium impact incident with personnel exposed to health effects. G Environment - Release of contaminated water, localized damage to non-sensitive environment restorable within days or weeks, unlikely to spread offsite. - G Production - $1.2M per day shutdown, assumption of 6 hours to recover from an incident ($300k), => impact level G range Business - Mid term diversion of local management to manage issue/event Likelihood - considered could occur once or twice in lifetime of facility (6) |  | M1 ¦ Bunding, Open and Closed Hazardous Drains ¦ Open Hazardous Drains Water seals | A | Not clear that any water seals are identified on or components of item on MEL.
SYSTEM-57 | CLOSED DRAINS SYS 57 | 57 | SYS | N |  | 778 | E5 | F5 | F5 | G5 | A | B | B | C | → | A | Loss of system primary function = no safe disposal route for hazardous fluids Safety - Potential for gas release and explosion / fire with 1-2 fatalities E Environment - LOPC within local environment, remediation days to weeks, unlikely to spread offsite. - G Production - $1.2M per day shutdown, assumption of 24 hours to recover from an incident ($1.2M), => impact level F range Business - Mid term diversion of local management to manage issue/event Likelihood - considered could occur in lifetime of 10 similar facilities (5) | closed system. Production not affected. | No changes identified | E5 | F5 | F5 | G5 | Loss of system primary function = no safe disposal route for hazardous fluids Safety - Potential for gas release and explosion / fire with 1-2 fatalities E Environment - LOPC within local environment, remediation days to weeks, unlikely to spread offsite. - G Production - $1.2M per day shutdown, assumption of 24 hours to recover from an incident ($1.2M), => impact level F range Business - Mid term diversion of local management to manage issue/event Likelihood - considered could occur in lifetime of 10 similar facilities (5) |  | M1 ¦ Bunding, Open and Closed Hazardous Drains ¦ Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | Also closed drain drum alarms, arguable whether also gas containment due to LP fuel gas purge. H2S potential could also be considered as 'highly toxic' containment.
SYSTEM-58 | NON-HAZARDOUS OPEN DRAINS SYS 58 | 58 | SYS | Y |  | 525 | G5 | H5 | G5 | H5 | C | C | C | C | → | C | Loss of system primary function = no safe disposal route for surface water Safety - medium level health/safety incident (slip/trip) - G Environment - minimal impact, unlikely to spread offsite. - H Production - $1.2M per day shutdown, assumption of 4 hours to recover from an incident ($0.3M), => impact level G range Business - Mid term diversion of local management to manage issue/event Likelihood - considered could occur once or twice in lifetime of 10 facilities (5) BP Feedback incorporated: common system. Mostly Maintenance water and rain. There is also a large pod for storage. Unlikle to impact production. Consider "possible" since it is a simple and robust system. | common system. Mostly Maintenance water and rain. There is also a large pod for storage. Unlikle to impact production. Consider "possible" since it is a simple and robust system. |  | G5 | H5 | G5 | H5 | Loss of system primary function = no safe disposal route for surface water Safety - medium level health/safety incident (slip/trip) - G Environment - minimal impact, unlikely to spread offsite. - H Production - $1.2M per day shutdown, assumption of 4 hours to recover from an incident ($0.3M), => impact level G range Business - Mid term diversion of local management to manage issue/event Likelihood - considered could occur once or twice in lifetime of 10 facilities (5) |  |  | #N/A | None allocated
SYSTEM-59 | SANITARY WATER SYS 59 | 59 | SYS | Y |  | 0 | F6 | H6 | H6 | H6 | None | None | None | None | → | None | Copied from potable water Loss of system primary function = lack of potable water to systems demand (tankered supply). Loss of supply to chemicals / slurry dilution, and water seal on LP flare stack. Safety - Assumed minimal impact from potable in isolation (drinking supplies will be bottled water) BUT supplies safety showers which would become unavailable. Environment - minimal impact on assumption of safe shutdown before discharge of out of spec fluids. Production -Assumed no impact Business - Mid term diversion of local management to manage issue/event Likelihood - considered could occur once or twice in lifetime of facility (6) | OK | No changes made, but no active tags in system anyway. | F6 | H6 | H6 | H6 | Copied from potable water Loss of system primary function = lack of potable water to systems demand (tankered supply). Loss of supply to chemicals / slurry dilution, and water seal on LP flare stack. Safety - Assumed minimal impact from potable in isolation (drinking supplies will be bottled water) BUT supplies safety showers which would become unavailable. Environment - minimal impact on assumption of safe shutdown before discharge of out of spec fluids. Production -Assumed no impact Business - Mid term diversion of local management to manage issue/event Likelihood - considered could occur once or twice in lifetime of facility (6) |  |  | #N/A | No system operating guide for System 59 to review. None allocated
SYSTEM-60 | HOT OIL SYS 60 | 60 | SYS | N |  | 1269 | H6 | H6 | F6 | G6 | C | C | B | B | → | B | Loss of system primary function = loss of process heating where required leading to reduced throughput and/or shutdown of production from Raven only. Safety - assume safe shutdown, no safety impact, no loss of hot oil containment - H Environment - minimal impact on assumption of safe shutdown / no loss of oil to environment - H Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to once or twice in life of facility (6) (thermal cycling contributing to long term unreliability) BP Feedback incorporated: Raven only. Causes loss of Raven Production. 200 degrees. Some safety impacts. Not cheap to replace oil. Consider Possible or Likely liklihoods | Raven only. Causes loss of Raven Production. 200 degrees. Some safety impacts. Not cheap to replace oil. Consider Possible or Likely liklihoods | Likelihood reduced to 6 (which reduces system criticality from A to B) | H7 | H7 | F7 | G7 | Loss of system primary function = loss of process heating where required leading to reduced throughput and/or shutdown of production Safety - assume safe shutdown, no safety impact, no loss of hot oil containment - H Environment - minimal impact on assumption of safe shutdown / no loss of oil to environment - H Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen multiple times in life of facility (7) (thermal cycling contributing to long term unreliability) |  | P4 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | Hot oil system operates above120°C threshold in parts
SYSTEM-61 | OXYGEN SCAVENGER SYS 61 | 61 | SYS | N |  | 14 | H6 | H6 | F6 | G6 | C | C | B | B | → | B | Loss of system primary function = unable to scavenge oxygen in Lean MEG system, leading to off spec export gas and fines / reduced value of exports, long term accelerated corrosion Safety - assume safe shutdown, no safety impact, no loss of scavenger containment - H Environment - minimal impact on assumption of safe shutdown - H Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen once or twice in life of facility (6) | is not 61. comes under system 52? Check | Only piping and SYLH tags in this system, will only leave SYLH after removing pipework as integrity defined tags. | H6 | H6 | F6 | G6 | Loss of system primary function = unable to scavenge oxygen in Lean MEG system, leading to off spec export gas and fines / reduced value of exports, long term accelerated corrosion Safety - assume safe shutdown, no safety impact, no loss of scavenger containment - H Environment - minimal impact on assumption of safe shutdown - H Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen once or twice in life of facility (6) |  |  | #N/A | No system 61 system operating guide to consult, no MAH barriers identified.
SYSTEM-62 | DIESEL SYS 62 | 62 | SYS | N |  | 144 | H6 | G6 | H6 | G6 | C | B | C | B | → | B | Loss of system primary function = loss of diesel top-up supply to day tanks to firepumps and emergency and essential generators. Top up is manually initiated, not constant. Safety - No immediate impact on loss. Option to tanker diesel to day tanks as back-up. Level H Environment - minimal impact on assumption of safe shutdown, but if shutdown for a diesel release - G Production - No immediate impact on production, cost of additional tankering <$50k - H Business - Mid term diversion of local management to manage issue/event, Non-compliance with industry standards but no regulatory action taken - G Likelihood - considered likely to happen once or twice in life of facility (6) BP feedback incorporated: not fully online it's just topping day tanks. Back up to truck it round. Will not affect fire pumps or generators. | not fully online it's just topping day tanks. Back up to truck it round. Will not affect fire pumps or generators. | Reduced S impact in response to comments, updated notes inline with comments, reduced production impact to 0 hours, arguably could say no immediate production impact apart from cost of tankering. Environment impact increased in case shutdown it due to spill/leak/release. Changes system from A to B overall (& 1 notch above C) | E6 | H6 | F6 | G6 | Loss of system primary function = loss of diesel supply to day tanks including diesel driven firepumps, leading to eventual loss of firepump cover and essential / emergency generation Safety - Eventual loss of firepump cover, E ( cascading to production shutdown.) Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen once or twice in life of facility (6) (full escalation unlikely with use of temporary tanker supplies hoses if required?) |  | P4 ¦ Oil Storage & Offloading ¦ Hydrocarbon Tanks | A | Arguable to also / alternatively consider firepumps as firewater pumps diesel tanks are in this system.
SYSTEM-63 | INSTRUMENT AIR SYS 63 | 63 | SYS | Y |  | 792 | G6 | H6 | F6 | G6 | B | C | B | B | → | B | Loss of system primary function = safe shutdown of multiple systems on loss of instrument air, loss of all production form GF & R, large blowdown/flaring event Safety - Heavy flaring with potential to affect personnel in vicinitiy coincident with event, potential single or multiple recordable injuries - G Environment - minimal impact on assumption of safe shutdown, large flaring but disperses with no lasting damage to local environment - H Production - $1.2M per day shutdown, assumption of 24 hours to fully recover from an event, $1.2M = impact level F Business - Mid term diversion of local management to manage issue/event, Non-compliance with industry standards bu no regulatory action taken - G Likelihood - considered likely to happen once or twice in life of facility (6) BP Feedback incorporated: Common. Loose both plants. Envirnmentally causes a very large Blow down! | Safety is E5? But notes call it "minimal impact"? Common. Loose both plants. Envirnmentally causes a very large Blow down! | Treating blowdown as emissions/regulatory compliance under B category rather than environmental as there is no lasting damage. Removed consideration of missiling as its not the primary function and more an inspection/integrity issue on pipework and fittings. Re-evaluated S impact on bassis of heavy flaring incident. | E5 | H6 | F6 | G6 | Loss of system primary function = safe shutdown of multiple systems on loss of instrument air Safety - Minimal impact unless considering failure of pressure containment in system (e.g. missiling failed fitting), as a low probability event Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 24 hours to fully recover from an event, $1.2M = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen once or twice in life of facility (6) |  | P4 ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | Only one step risk change on safety risk required to match this MAH barrier.
SYSTEM-64 | INERT GAS SYS 64 | 64 | SYS | Y |  | 633 | E5 | H6 | F6 | G6 | A | C | B | B | → | A | Loss of system primary function = loss of inerting blanket in tanks Safety - potential to create explosive atmosphere in tank voids, with explosion/fire risk on ignition. E Environment - minimal impact on assumption of safe shutdown, asphyxiation risk on loss of containment in confined spaces Production - $1.2M per day shutdown, assumption of 24 hours to fully recover from an event, $1.2M = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen once or twice in life of facility (6), potential to mitigate with temporary tankered / bottled supplies BP Feedback incorporated: common. Goes into raven flare and goes into blanketting tanks. Also supplies gas seals on GF Comp. It is a fairly robust system, mostly static equipment. Check which tank voids and what is the liklihood of explosion? Is Fuel Gas not also connected? | common. Goes into raven flare and goes into blanketting tanks. Also supplies gas seals on GF Comp. It is a fairly robust system, mostly static equipment. Check which tank voids and what is the liklihood of explosion? Is Fuel Gas not also connected? | Critical Low Purity Nitrogen consumers: • Supply of Low Purity Nitrogen to Flash gas compressor • Supply of Low Purity Nitrogen to HP Flare Header Purging • Supply of Low Purity Nitrogen to LP Flare Header Purging • Supply of Low Purity Nitrogen to Thermal oxidiser LP Header Purging • Supply of Low Purity Nitrogen to Thermal oxidiser LLP Header Purging • Supply of Low Purity Nitrogen to Hot oil fired heater and expansion drum inbreathing • Supply of Low Purity Nitrogen to Slop MEG tank inbreathing • Supply of Low Purity Nitrogen to chemical cleaning tank in-breathing • Supply of Low Purity Nitrogen to Giza Fayoum consumers Non - Critical Low Purity Nitrogen consumers: • Supply of Low Purity Nitrogen to Utility stations in Raven facility • Supply of Low Purity Nitrogen to TSA regeneration gas fired heaters • Supply of Low Purity Nitrogen to Hot oil fired heaters High Purity Nitrogen consumers: • Supply of High Purity Nitrogen to MEG regeneration unit • Supply of High Purity Nitrogen to Lean MEG offloading tank • Supply of High Purity Nitrogen to Methanol storage drum | E5 | H6 | F6 | G6 | Loss of system primary function = loss of inerting blanket in tanks Safety - potential to create explosive atmosphere in tank voids, with explosion/fire risk on ignition. E Environment - minimal impact on assumption of safe shutdown, asphyxiation risk on loss of containment in confined spaces Production - $1.2M per day shutdown, assumption of 24 hours to fully recover from an event, $1.2M = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen once or twice in life of facility (6), potential to mitigate with temporary tankered / bottled supplies |  | M4 ¦ Inert Gas Blanketing ¦ IGG Generator | A | best fit MAH barrier chosen.
SYSTEM-65 | PLANT/UTILITY AIR SYS 65 | 65 | SYS | Y |  | 950 | G6 | H6 | F6 | G6 | B | C | B | B | → | B | Copied from instrument air Loss of system primary function = safe shutdown of multiple systems on loss of instrument air Safety - Minimal impact unless considering failure of pressure containment in system (e.g. missiling failed fitting), as a low probability event Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 24 hours to fully recover from an event, $1.2M = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen once or twice in life of facility (6) | Process Engineer says not commonly in use. Check what tags are in this system and what is their function. | Copied in line with instrument air. Changes overall from A to B. From SOG: Plant Air consumers: • Supply of Plant Air to Air Dryer Package. • Supply of Plant Air to Thermal oxidizer. • Supply of Plant Air to Utility stations. • Supply of Plant Air to Giza Fayoum consumers. • Supply of Plant Air to Neutralisation pit logistics area | E5 | H6 | F6 | G6 | Copied from instrument air Loss of system primary function = safe shutdown of multiple systems on loss of instrument air Safety - Minimal impact unless considering failure of pressure containment in system (e.g. missiling failed fitting), as a low probability event Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 24 hours to fully recover from an event, $1.2M = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen once or twice in life of facility (6) |  | P4 ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | Only one step risk change on safety risk required to match this MAH barrier.
SYSTEM-66 | THERMAL OXIDIZER SYS 66 | 66 | SYS | N |  | 466 | H6 | H6 | H6 | F6 | C | C | C | B | → | B | Loss of system primary function = loss of disposal route for combustible hazardous gases Safety - Assume safe shutdown / safe venting / dilution route if thermal oxidiser unavailable. H Environment - toxic emissions disperse in atmosphere, no future impact - H Production - Loss of system does not stop production - impact level H Business - Mid term diversion of local management to manage issue/event. Assume likely to exceed permitted plant emissions of e.g. VOCs. Regulatory compliance issue which does not lead to regulatory or higher severity level consequence - F Likelihood - considered likely to happen once or twice in life of facility (6) BP Feedback incorporated: No production impact. Can produce without it but there will be an environment impact. Flare \ vent. Raven only. There is no H2S but other products are toxic. VOCs etc? | No production impact. Can produce without it but there will be an environment impact. Flare \ vent. Raven only. There is no H2S but other products are toxic. VOCs etc? | shifted impact form E to B category on basis atmospheric dispersal is not a lasting impact in terms of Risk Management Policy, it is a regulatory compliance issue under B. Production impact set low in line with feedback | H6 | F6 | F6 | G6 | Loss of system primary function = loss of disposal route for combustible hazardous gases Safety - Assume safe shutdown / safe venting / dilution route if thermal oxidiser unavailable. H Environment - Assume likely to exceed permitted plant emissions of e.g. H2S. - F Production - $1.2M per day shutdown, assumption of 24 hours to fully recover from an event, $1.2M = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen once or twice in life of facility (6) |  |  | #N/A | No MAH barrier identified for this system. Considered P4 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for highly toxic substances as an option for any H2S going to the incinerator.
SYSTEM-67 | PRODUCED WATER SYS 67 | 67 | SYS | N |  | 1122 | H5 | H5 | F5 | G5 | C | C | B | C | → | B | Loss of system primary function = unable to process produced water and route for disposal by tanker Safety - Assume safe shutdown on high levels in produced water tanks/drums. H Environment - Minimal, assuming shutdown and no tank overflow / loss of containments - H Production - $1.2M per day shutdown, assumption of 24 hours to fully recover from an event, $1.2M = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - loss of system lasting > 7 days considered likely to occur in life of 10 facilities (5) BP Feedback incorporated: Common system but no shutdown expected for about 7 days. along same guidelines as meg. 7 days depending on rate. Unlikley to cause a production shutdown if can be fixed in 7 days. | Common system but no shutdown expected for about 7 days. along same guidelines as meg. 7 days depending on rate. Unlikley to cause a production shutdown if can be fixed in 7 days. | Reduced production likelihood on basis of feedback and assumption most problems could be addressed within 7 days, so likelihood of event escalation to production shutdown reduced to possible(5) | H6 | H6 | F6 | G6 | Loss of system primary function = unable to process produced water and route for disposal by tanker Safety - Assume safe shutdown on high levels in produced water tanks/drums. H Environment - Minimal, assuming shutdown and no tank overflow / loss of containments - H Production - $1.2M per day shutdown, assumption of 24 hours to fully recover from an event, $1.2M = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen once or twice in life of facility (6) |  | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | Vessels in system blanketed with fuel gas (e.g. skimmed oil vessel), so treat as gas containing process containment.
SYSTEM-68 | RESERVED FOR ONSHORE USE | 68 | SYS | N | System Not in Use | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added to this system. | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-69 | RESERVED FOR ONSHORE USE | 69 | SYS | N | System Not in Use | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added to this system. | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-70 | RESERVED FOR ONSHORE USE | 70 | SYS | N | System Not in Use | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added to this system. | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-71 | RESERVED FOR ONSHORE USE | 71 | SYS | N | System Not in Use | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added to this system. | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-72 | RESERVED FOR ONSHORE USE | 72 | SYS | N | System Not in Use | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added to this system. | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-73 | RESERVED FOR ONSHORE USE | 73 | SYS | N | System Not in Use | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added to this system. | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-74 | RESERVED FOR ONSHORE USE | 74 | SYS | N | System Not in Use | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added to this system. | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-75 | RESERVED FOR ONSHORE USE | 75 | SYS | N | System Not in Use | 1 | H6 | H6 | G6 | H6 | C | C | B | C | → | B | Loss of system primary function = loss of online / realtime condition monitoring data (this is assumed separate from any machinery protection functions as part of equipment control system, e.g. its a System type 1 panel not a Bently 3500 machinery protection panel delivering condition onitoring input)). Safety - no impact on loss of condition monitoring data - H Environment - No impact on loss of condition monitoring data - H Production - Potential for unplanned monnitored equipment outage rather than planned intervention, estimated cost range $50k-$500k - G Business - Short term diversion Local management time ro manage issue/event - H Likelihood - Probably more likely to be generated by software intervention / network configuration issues that hardware failure, treat as Likely to occur once or twice in facility lifetime - 6 | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | Assessed on basis of condition monitoring panels (only one tag in system at time of assessment) | H3 | H3 | H3 | H3 | Not assessed
SYSTEM-76 | ICSS - PROCESS AUTOMATION SYSTEM | 76 | SYS | N |  | 87 | H7 | H7 | G7 | H7 | C | C | B | C | → | B | Loss of system primary function = process trip and plant shutdown, reset, fault-finding and restart. Safety - Assume safe shutdown from safety instrumented system / failsafe behaviour. H Environment - Minimal, assuming shutdown and no tank overflow / loss of containments - H Production - $1.2M per day shutdown, assumption of 8 hours to fully recover from an event, $0.4M = impact level G Business - short term diversion of local management to manage issue/event Likelihood - considered likely to happen several times in life of facility (7) | ok | None | H7 | H7 | G7 | H7 | Loss of system primary function = process trip and plant shutdown, reset, fault-finding and restart. Safety - Assume safe shutdown from safety instrumented system / failsafe behaviour. H Environment - Minimal, assuming shutdown and no tank overflow / loss of containments - H Production - $1.2M per day shutdown, assumption of 8 hours to fully recover from an event, $0.4M = impact level G Business - short term diversion of local management to manage issue/event Likelihood - considered likely to happen several times in life of facility (7) |  | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable | B | Alternate selection which also gives B result is: P6 ¦ Control systems - non LoPs, LOPA initiating causes ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI sc
SYSTEM-77 | ICSS - SAFETY INSTRUMENTED SYSTEM ESD | 77 | SYS | N |  | 27 | E5 | G5 | F5 | G5 | A | C | B | C | → | A | Loss of system primary function = undetected loss of protection layer / shutdown, with potential for escalating event Safety - potential for explosion, fire, multiple fatalities - E+ Environment - G Production - $1.2M per day shutdown, assumption of 48 hours to fully recover from an event, $2.4M = impact level F Business - short term diversion of local management to manage issue/event Likelihood - considered likely to happen in lifetime of 10 facilities (5) | ok | None | E5 | G5 | F5 | G5 | Loss of system primary function = undetected loss of protection layer / shutdown, with potential for escalating event Safety - potential for explosion, fire, multiple fatalities - E+ Environment - G Production - $1.2M per day shutdown, assumption of 48 hours to fully recover from an event, $2.4M = impact level F Business - short term diversion of local management to manage issue/event Likelihood - considered likely to happen in lifetime of 10 facilities (5) |  | P7 ¦ SIS - LoP Components ¦ LoP Components: Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial | A | Could also select under P6 - Control systems - LoPs with same result.
SYSTEM-78 | FIRE AND GAS DETECTION | 78 | SYS | N |  | 1371 | E5 | G5 | E5 | E5 | A | C | A | A | → | A | Loss of system primary function = undetected gas release and / or fire, leading to escalating incident Safety - potential for explosion, fire, multiple fatalities - E+ Environment - G Production - $1.2M per day shutdown, assumption of 168 hours to fully recover from an event, $8.4M = impact level E Business - mid term diversion of senior management to manage issue/event - E Likelihood - considered a similar event may have occurred within life of 10 facilities (5) | Procduction loss looks high. What is the scenario that may take 168 hours to repair? Normally use software controls or replacement of components. | Rationale for week to recover was large scale explosion damaging significant areas of plant / equipment, since if detection system not functioning (and not apparent) there would be no detection prior to an ignition event - hence a big bang. This is really just arguing the case that everything in Fire and Gas detection should be an A. | E5 | G5 | E5 | E5 | Loss of system primary function = undetected gas release and / or fire, leading to escalating incident Safety - potential for explosion, fire, multiple fatalities - E+ Environment - G Production - $1.2M per day shutdown, assumption of 168 hours to fully recover from an event, $8.4M = impact level E Business - mid term diversion of senior management to manage issue/event - E Likelihood - considered a similar event may have occurred within life of 10 facilities (5) |  | M6 ¦ Fire & Gas systems ¦ Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | Could also select (with same result) M6 ¦ Fire & Gas systems ¦ Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution.
SYSTEM-79 | SAFETY - FIRE FIGHTING | 79 | SYS | N |  | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Loss of system primary function = unable to fight any fire incident Safety - potential for explosion, fire, multiple fatalities - E+ Environment - G Production - $1.2M per day shutdown, assumption of 48 hours to fully recover from an event, $2.4M = impact level F Business - mid term diversion of local management to manage issue/event - G Likelihood - considered a similar event may have occurred within life of 10 facilities (5) | Is this fixed or portable fire fighting? What is the fire incident event causing the impacts? Is there really a production impact? | No non-SYLH tags in system, so set to Not Assessed in case any tags added in future to force re-assessment | E5 | G5 | F5 | G5 | Loss of system primary function = unable to fight any fire incident Safety - potential for explosion, fire, multiple fatalities - E+ Environment - G Production - $1.2M per day shutdown, assumption of 48 hours to fully recover from an event, $2.4M = impact level F Business - mid term diversion of local management to manage issue/event - G Likelihood - considered a similar event may have occurred within life of 10 facilities (5) |  | M7 ¦ Miscellaneous fire protection systems ¦ Mobile (wheeled) fire extinguishers | B | System 79 only contains two SYLH tags for foam and dry chemicals and 'extinguishing systems', so this is considered nearest of MAH barriers to match.
SYSTEM-80 | NORMAL POWER | 80 | SYS | N |  | 969 | H7 | H7 | F7 | G7 | C | C | A | B | → | A | Loss of system primary function = Shutdown/Trip of normal operations. Assume UPS covers protected systems, Essential / Emergency generators started after short delay. Safety -minimal impact on 'fail safe' power trip assumptions - H Environment - minimal impact assumed - H Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $0.6M = impact level F Business - short term diversion of local management to manage issue/event - H Likelihood - considered may happen several times in facility lifetime (7) BP feedback incorporated: No System Operating Guides available to determine if auto-start of backup generators. | To what extent what other power system be able to maintain safety systems? | Added comments to notes, with a response based on currently available information, no changes to inputs. | H7 | H7 | F7 | G7 | Loss of system primary function = Shutdown of normal operations Safety -minimal impact on 'fail safe' power trip assumptions - H Environment - minimal impact assumed - H Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $0.6M = impact level F Business - short term diversion of local management to manage issue/event - H Likelihood - considered may happen several times in facility lifetime (7) |  |  | #N/A | No MAH selected, trip is not a MAH.
SYSTEM-81 | FIRE WATER SYS 81 | 81 | SYS | N |  | 1539 | E5 | G5 | H5 | G5 | A | C | C | C | → | A | Loss of system primary function = unable to use firewater in any fire incident Safety - potential for explosion, fire, multiple fatalities - E+ Environment - G Production - $1.2M per day shutdown, assumption loss of fire water system does not require shutdown = impact level H Business - mid term diversion of local management to manage issue/event - G Likelihood - considered a similar event may have occurred within life of 10 facilities (5) | need to read the background. Unlikely to cause production impact because of onshore gas plant. Fire water has limited benefit to the production. | Original inputs assumed loss of firewater required a shutdown, hence production impact. Changed production impact to minimal if this is not the case for onshore gas plant. | E5 | G5 | F5 | G5 | Loss of system primary function = unable to use firewater in any fire incident Safety - potential for explosion, fire, multiple fatalities - E+ Environment - G Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $0.6M = impact level F Business - mid term diversion of local management to manage issue/event - G Likelihood - considered a similar event may have occurred within life of 10 facilities (5) |  | M7 ¦ Fire protection ¦ Firewater pumps (main and jockey), drivers, their controls and control panels | A | Selected as main supplier to system. Alternative component could be M7 ¦ Fire protection ¦ Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system)
SYSTEM-82 | UTILITIES - SEWAGE SYSTEM | 82 | SYS | Y |  | 46 | H5 | G5 | H5 | G5 | C | C | C | C | → | C | Loss of system primary function = unable to treat and dispose of foul water Safety - Low impact incidents - H Environment - G Production - Minimal impact on loss of system - H Business - short term diversion of local management to manage issue/event - G Likelihood - considered a similar event may have occurred within life of 10 facilities (5) | ok | None | H5 | G5 | H5 | G5 | Loss of system primary function = unable to treat and dispose of foul water Safety - Low impact incidents - H Environment - G Production - Minimal impact on loss of system - H Business - short term diversion of local management to manage issue/event - G Likelihood - considered a similar event may have occurred within life of 10 facilities (5) |  |  | #N/A | None allocated
SYSTEM-83 | TELECOMS (GENERAL) | 83 | SYS | N |  | 21 | G6 | H6 | H6 | G6 | B | C | C | B | → | B | Loss of system primary function = unable to communicate within / off site, loss of control, Safety - No immediate effect in isolation - G Environment - No impact Production - Loss of production management information, potentially unmetered production leading to financial loss equivalent to 24hrs production - $1.2M, - F Business - mid term diversion of local management to manage issue/event - G Likelihood - considered a similar event may once or twice in facility life(6) | clarify is this impacts incident management. | 21 non SYLH tags. Includes PAGA cabinets, PABX cabinet, guard house and outdoor phones, so assuming if these are down would affect incident management through loss of some/all telephone communications, but mobile / sat phones may be available as mitigation. No changes made to inputs. | G6 | H6 | H6 | G6 | Loss of system primary function = unable to communicate within / off site, loss of control, Safety - No immediate effect in isolation - G Environment - No impact Production - Loss of production management information, potentially unmetered production leading to financial loss equivalent to 24hrs production - $1.2M, - F Business - mid term diversion of local management to manage issue/event - G Likelihood - considered a similar event may once or twice in facility life(6) |  | M3 ¦ Telecommunications ¦ Class A Telecommunication UPS & Shut down | A | Alternatives could be M3 ¦ Facility Emergency Telephone & Hot line systems ¦ Call control - PABX/IPT Ex telephones Designated emergency phones (Control rooms muster points etc.) Interconnecting cable plant and networks
SYSTEM-84 | ESSENTIAL POWER | 84 | SYS | N |  | 2 | H5 | H5 | F5 | G5 | C | C | B | C | → | B | Loss of system primary function = unable to start/re-start process systems after main power outage or Level 1/2 ESD leading to loss of production. Each site has 2 EDGs with 'duty' unit set to auto-start on loss of main power. Safety - No immediate effect in isolation - H Environment - No impact Production -Unable to start-up until resolved, assume 12hr loss planned production = $600k, F Business - mid term diversion of local management to manage issue/event - G Likelihood - considered a similar event may occur in life of 10 facilities (5), as both duty and standby generators would have to fail to start to give production impact quoted. | blackout? Blow down, flare, loss of power? | Only 2 active tags in this system, the two diesel generators for GF. Notes update based on following information: EG001-OP-MAN-00-3042-B01 on Sharecat is only found reference to essential power. According to this, Essential Power is used to start after loss of power or Level 1/2 ESD. Duty EDG will auto-start on total power loss from main power system. (Manual start on first start or complete shutdown) Assumption is that critical systems protected by UPS Power are kept alive allowing for Essential power to start. Likelihood revised to 5 on basis of duty / standby machines giving redundancy on both sites. | H6 | H6 | F6 | G6 | Loss of system primary function = unable to start process systems leading to loss of production Safety - No immediate effect in isolation - H Environment - No impact Production -Unable to start-up until resolved, assume 12hr loss planned production = $600k, F Business - mid term diversion of local management to manage issue/event - G Likelihood - considered a similar event may once or twice in facility life(6) |  |  | #N/A | None selected, considered as more a start-up system with no MAH role.
SYSTEM-85 | ESSENTIAL LIGTING AND SMALL POWER | 85 | SYS | N |  | 245 | F6 | H6 | H6 | G6 | B | C | C | B | → | B | Loss of system primary function = unable to access dark areas to start process systems leading to loss of production, unable to work in affected areas if normal lighting not available. For impact to occur, requires loss of normal lighting as well as essential lighting. Safety - Potential DAFWC injury on sudden loss of lighting on safe access/egress - F Environment - No impact - H Production - No immediate production effect, H Business - mid term diversion of local management to manage issue/event - G Likelihood - considered a similar event may once or twice in facility life(6) | clarify is this impacts incident management. Safe access and egress etc. Is there a production impact? | Revise safety impact to F to account for DAFWC for injury potential following loss of lighting. Reduce production impact, limited night shift working and dayshift internal areas only affected. | H6 | H6 | G6 | G6 | Loss of system primary function = unable to start process systems leading to loss of production Safety - No immediate effect in isolation - H Environment - No impact Production - Constrained personnel working, assume equivalent to 8hr loss production to resolve = $400k, G Business - mid term diversion of local management to manage issue/event - G Likelihood - considered a similar event may once or twice in facility life(6) |  | M3 ¦ Emergency Lighting ¦ Emergency Lighting - supplied from Emergency Generator Switchboard | B | Potential to debate Essential vs. Emergency lighting here
SYSTEM-86 | TRACE HEATING | 86 | SYS | N |  | 8 | E5 | H5 | H5 | G5 | A | C | C | C | → | A | Loss of system primary function = trace heating inactive, potential to freeze valves JT expansion, or in exceptional cold weather. Safety - Leaking valve/PSV may freeze up and not achieve credited relief rate if demanded. Likely to be observed on operator rounds. Potential for overpressure leading to 1-2 fatalities. E Environment - No impact - H Production - No immediate production effect, H Business - mid term diversion of local management to manage issue/event - G Likelihood - considered a similar event may occur in life of 10 facilities(5) | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | 3 non-piping tags in MEL, associated with electrical supplies to heat tracing rather than the tracing itself | H3 | H3 | H3 | H3 | Not assessed |  |  | #N/A | None allocated
SYSTEM-87 | EMERGENCY POWER | 87 | SYS | N |  | 664 | H5 | H5 | F5 | G5 | C | C | B | C | → | B | Loss of system primary function = unable to start/re-start process systems after main power outage or Level 1/2 ESD leading to loss of production. Each site has 2 EDGs with 'duty' unit set to auto-start on loss of main power. Safety - No immediate effect in isolation - H Environment - No impact Production -Unable to start-up until resolved, assume 12hr loss planned production = $600k, F Business - mid term diversion of local management to manage issue/event - G Likelihood - considered a similar event may occur in life of 10 facilities (5), as both duty and standby generators would have to fail to start to give production impact quoted. | blackout? Blow down, flare, loss of power? | Updated to match system 84 as has the generators for Raven. Notes update based on following information: EG001-OP-MAN-00-3042-B01 on Sharecat is only found reference to essential power (refers to essential power generators in System 84 (GF) and 87 (Raven). According to this, Essential Power is used to start after loss of power or Level 1/2 ESD. Duty EDG will auto-start on total power loss from main power system. (Manual start on first start or complete shutdown) Assumption is that critical systems protected by UPS Power are kept alive allowing for Essential power to start. Likelihood revised to 5 on basis of duty / standby machines giving redundancy on both sites. | F6 | H6 | G6 | G6 | Loss of system primary function = no electrical power supply in emergency, loss of all non-battery backed emergency systems Safety - Reduced ability to manage incident - F Environment - No impact Production - Unable to operate without emergency power backup, 8hr loss production to resolve = $400k, G Business - mid term diversion of local management to manage issue/event - G Likelihood - considered a similar event may once or twice in facility life(6) |  | M3 ¦ Emergency Power ¦ Emergency Generator | A | best fit MAH barrier chosen.
SYSTEM-88 | UPS POWER | 88 | SYS | N |  | 564 | F6 | H6 | G6 | G6 | B | C | B | B | → | B | Loss of system primary function = no electrical power supply in emergency, loss of all non-independent battery backed emergency systems. Safety - Reduced ability to manage incident - F Environment - No impact Production - Unable to operate without emergency power backup, 8hr loss production to resolve = $400k, G Business - mid term diversion of local management to manage issue/event - G Likelihood - considered a similar event may once or twice in facility life(6) | ok | None | F6 | H6 | G6 | G6 | Loss of system primary function = no electrical power supply in emergency, loss of all non-independent battery backed emergency systems. Safety - Reduced ability to manage incident - F Environment - No impact Production - Unable to operate without emergency power backup, 8hr loss production to resolve = $400k, G Business - mid term diversion of local management to manage issue/event - G Likelihood - considered a similar event may once or twice in facility life(6) |  | M3 ¦ Emergency Power ¦ UPS Systems | A | best fit MAH barrier chosen.
SYSTEM-89 | NORMAL LIGHTING AND SMALL POWER | 89 | SYS | N |  | 304 | F6 | H6 | H6 | G6 | B | C | C | B | → | B | Loss of system primary function = unable to access dark areas to start process systems leading to loss of production, unable to work in affected areas if normal lighting not available. For full impact to occur, requires loss of essential lighting as well as normal. Safety - Potential DAFWC injury on sudden loss of lighting on safe access/egress - F Environment - No impact - H Production - No immediate production effect, H Business - mid term diversion of local management to manage issue/event - G Likelihood - considered a similar event may once or twice in facility life(6) BP Feedback incorporated: should have lower impacts than essential power and lighting? Response: set to same impact, as requires double system failure to generate full impact. | should have lower impacts than essential power and lighting? | Aligned to match essential power and lighting. Arguably there would be higher likelihood of losing normal lighting e.g. from main power trip, but not though sufficient to change likelihood ranking as its tied to absence of both systems. | H7 | H7 | F6 | G6 | Loss of system primary function = loss of normal lighting, constraining personnel operations Safety - may lead to medium impact incident, - G Environment - No impact Production - Constrained personnel working, assume equivalent to 8hr loss production to resolve = $400k, G Business - mid term diversion of local management to manage issue/event - G Likelihood - considered a similar event may occur several times in facility life(6) |  |  | #N/A | None allocated
SYSTEM-90 | EARTHING AND LIGHTING PROTECTION | 90 | SYS | N |  | 161 | E4 | H5 | G5 | H5 | B | C | C | C | → | B | Loss of system primary function = loss of normal earthing, lightning protection to earth. Safety - electric shock hazard, 1-2 fatality potential, with low likelihood - E Environment - No impact - H Production - no immediate impact, potential for equipment damage through unmitigated lightning strike, guestimate repair / replacement costs $100k - G Business - short term diversion of local management to manage issue/event - H Likelihood - considered a similar event may occur in lifetime of several facilities (5) | ok | None | E4 | H5 | G5 | H5 | Loss of system primary function = loss of normal earthing, lightning protection to earth. Safety - electric shock hazard, 1-2 fatality potential, with low likelihood - E Environment - No impact - H Production - no immediate impact, potential for equipment damage through unmitigated lightning strike, guestimate repair / replacement costs $100k - G Business - short term diversion of local management to manage issue/event - H Likelihood - considered a similar event may occur in lifetime of several facilities (5) |  |  | #N/A | None allocated
SYSTEM-91 | POWER - MAIN GENERATION SYS 91 | 91 | SYS | N |  | 1725 | H7 | H7 | F7 | H7 | C | C | A | C | → | A | Loss of system primary function = loss of normal power supplies, escalating to production shutdown and restart Safety - minimal impact, momentary loss of lighting in some areas - H Environment - No impact - H Production - Production trip and restart / ramp-up costs estimated at equivalent to 12 hrs production $600k - F Business - short term diversion of local management to manage issue/event - H Likelihood - considered a similar event may several times in facility lifetime (7) | ok | None | H7 | H7 | F7 | H7 | Loss of system primary function = loss of normal power supplies, escalating to production shutdown and restart Safety - minimal impact, momentary loss of lighting in some areas - H Environment - No impact - H Production - Production trip and restart / ramp-up costs estimated at equivalent to 12 hrs production $600k - F Business - short term diversion of local management to manage issue/event - H Likelihood - considered a similar event may several times in facility lifetime (7) |  | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Gas Generator | A | Selected as highest criticality component of power generation system. Other components with different criticalities, e.g. Alternator - B
SYSTEM-92 | CATHODIC PROTECTION | 92 | SYS | N |  | 2 | H5 | H5 | G5 | G5 | C | C | C | C | → | C | Loss of system primary function = loss of cathodic protection to structures and containment leading to accelerated corrosion. Assume corrosion is found by RBI before structural collapse / loss of containment imminent. Safety - minimal impact short term - H Environment - No impact - H Production - Costs of premature replacement of equipment / structures, assumed in range G ($50-$500k) Business - mid term diversion of local management to manage issue/event - G Likelihood - considered a similar event may occur once in lifetime of several facilities(5) BP Feedback incorporated: Take some credit for TAR and using these opportunities to make repairs in a way that limits production impact. | Take some credit for TAR and using these opportunities to make repairs in a way that limits production impact. | Revised cost of replacement to G in production / financial costs | H5 | H5 | F5 | G5 | Loss of system primary function = loss of cathodic protection to structures and containment leading to accelerated corrosion. Assume corrosion is found by RBI before structural collapse / loss of containment imminent. Safety - minimal impact short term - H Environment - No impact - H Production - Costs of premature replacement of equipment / structures, assumed in range F Business - mid term diversion of local management to manage issue/event - G Likelihood - considered a similar event may occur once in lifetime of several facilities(5) |  |  | #N/A | None allocated
SYSTEM-93 | POWER MANAGEMENT SYSTEM | 93 | SYS | N |  | 5 | H6 | H6 | F6 | H6 | C | C | B | C | → | B | Loss of system primary function = poor electrical load management, uncontrolled load shedding could escalate to loss of main power with plant shutdown and loss of production Safety - minimal impact short term - H Environment - No impact - H Production - Treat as power trip - F Business - short term diversion of local management to manage issue/event - H Likelihood - considered a similar event may occur once or twice in lifetime of facility(6) | ok | None | H6 | H6 | F6 | H6 | Loss of system primary function = poor electrical load management, uncontrolled load shedding could escalate to loss of main power with plant shutdown and loss of production Safety - minimal impact short term - H Environment - No impact - H Production - Treat as power trip - F Business - short term diversion of local management to manage issue/event - H Likelihood - considered a similar event may occur once or twice in lifetime of facility(6) |  |  | #N/A | None allocated
SYSTEM-94 | UTILITIES - HVAC | 94 | SYS | Y |  | 4 | H6 | H6 | F6 | H6 | C | C | B | C | → | B | Loss of system primary function = loss of HVAC Safety - confirmed gas in intake shuts down fans and closes dampers, so no direct impact from loss of HVAC, as this is the emrgency response for gas. - No impact - H Environment - No impact - H Production - Potential for control equipment to operate outside temperature range leading to shutdown escalating to production trip and shutdown. - F Business - short term diversion of local management to manage issue/event - H Likelihood - considered a similar event may occur once or twice in lifetime of facility(6) BP Feedback: F&G system would detect gas if it entered an at risk environment. Need to check some F&G C&Es to see if a shutdown would occur and hence take away the safety impacts. Prouction and environment would both be affected however | F&G system would detect gas if it entered an at risk environment. Need to check some F&G C&Es to see if a shutdown would occur and hence take away the safety impacts. Prouction and environment would both be affected however | Confirmed gas in inlet shuts fire dampers and stops fans, so assume here that loss of HVAC is not safety related as likelihhod of system failing concident with presence gas cloud is remote. Evacuation is manually initiated, so assume this would also lead to manually initiated plant shutdown. Then becomes a comfort issue if temperatures too high for operators to work. Only 4 non-SYLH tags in system at time of review - shutdown switches and MCC supplies. | E6 | H6 | F6 | H6 | Loss of system primary function = loss of HVAC Safety - loss of atmosphere control in control rooms / safe areas leaving them vulnerable to gas ingress in emergency situation. - E+ Environment - No impact - H Production - Potential for control equipment to operate outside temperature range leading to shutdown escalating to production trip and shutdown. - F Business - short term diversion of local management to manage issue/event - H Likelihood - considered a similar event may occur once or twice in lifetime of facility(6) |  |  | #N/A | None allocated
SYSTEM-95 | ACCESS CONTROL | 95 | SYS | N |  | 21 | H5 | H5 | H5 | G5 | C | C | C | C | → | C | Loss of system primary function = Loss of control of personnel access to site. Note - assuming this is not a barrier to unauthorised/hostile site access via any boundary. In event of loss assume post a security guard and revert to manual checks Safety - No impact, revert to manual system if required. H Environment - H Production - H Business - medium term diversion of local management to manage issue/event - G Likelihood - considered a similar event may occur once in lifetime of several facilities(5) BP Feedback: On failure of the systems let's assume that we post a security guard and revert to manual checks. Not related to emergency response. | On failure of the systems let's assume that we post a security guard and revert to manual checks. Not related to emergency response. | Safety impact reduced to H as no emergency response role. Notes updated. | E5 | H5 | H5 | H3 | Loss of system primary function = Loss of control of personnel access to site. Note - assuming this is not a barrier to unauthorised/hostile site access via any boundary. Safety - Loss of control of personnel on site leading to incomplete evacuation or inaccurate mustering, leading to 1-2 fatalities - E Environment - H Production - H Business - medium term diversion of local management to manage issue/event - G Likelihood - considered a similar event may occur once in lifetime of several facilities(5) |  | M3 ¦ Electronic Muster System ¦ Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | Treating access control as muster system in an emergency
SYSTEM-96 | CCTV - SECURITY | 96 | SYS | N |  | 82 | H7 | H7 | H7 | H7 | C | C | C | C | → | C | Loss of system primary function = loss of remote visual surveillance of site. Fall back send personnel to look and report back if required. Safety - minimal impact on immediate loss - H Environment - minimal impact, not substituting for operator walk rounds - H Production - no immediate impact on loss - H Business - short term diversion of local management to manage issue/event - H Likelihood - considered a similar event may occur once or twice in life of facility(6) BP Feedback incorporated: Security related and also possiblly used for emergency response | Security related and also possiblly used for emergency response. Liklihood of failure looks too high. | Likelihood reduced to 6. Notes updated. | H7 | H7 | H7 | H7 | Loss of system primary function = loss of remote visual surveillance of site Safety - minimal impact on immediate loss - H Environment - minimal impact, not substituting for operator walk rounds - H Production - no immediate impact on loss - H Business - short term diversion of local management to manage issue/event - H Likelihood - considered a similar event may occur several time in life of facility(7) |  |  | #N/A | None allocated
SYSTEM-97 | LAN - VOIP | 97 | SYS | N |  | 12 | H6 | H6 | H6 | H6 | C | C | C | C | → | C | Loss of system primary function = loss of routine voice communications (assuming no impact on Process Automation System components) Safety - loss of some emergency co-ordination facilities, not an immediate problem unless coincident with incident, so H Environment - no direct impact leading to future impact to area - H Production - no immediate impact on loss - H Business - short term diversion of local management to manage issue/event - G Likelihood - considered a similar event may occur once or twice in life of facility (7) | Is this telephones only? Impacts look high | Covers indoor and outdoor industrial Ex and NonEX phones (only). Reduced likelihood one step. | G7 | G7 | H7 | G7 | Loss of system primary function = loss of routine voice and data communications (assuming no impact on Process Automation System components) Safety - loss of some emergency co-ordination facilities, not an immediate problem unless coincident with incident. G Environment - may lose ability to track/record emissions for duration leading industry standards non-compliance G Production - no immediate impact on loss - H Business - medium term diversion of local management to manage issue/event - G Likelihood - considered a similar event may occur several time in life of facility (7) |  | M3 ¦ Facility Emergency Telephone & Hot line systems ¦ Call control - PABX/IPT Ex telephones Designated emergency phones (Control rooms muster points etc.) Interconnecting cable plant and networks | A | Nearest applicable shown, but depends whether LAN - VOIP system classes as hot-line / emergency phones.
SYSTEM-98 | PAGA | 98 | SYS | N |  | 315 | E5 | H5 | H5 | F5 | A | C | C | B | → | A | Loss of system primary function = loss of routine voice and data communications Safety - In the event of incident, unable to alert personnel and direct to place of safety - E+ Environment - minimal impact, H Production - No direct impact unless decision to shutdown for loss of PAGA. H Business - Short term diversion of Senior Management time to manage issue/event Likelihood - considered a similar event may occur life of 10 facilities (5) BP Feedback incorporated: check redundancy and if a liklihood 6 of system failure is correct. If it's dual redundant we can make it a 5. Response - Block diagram indicates SystemA / System B dual redundant. | Need to check redundancy and if a liklihood 6 of system failure is correct. If it's dual redundant we can make it a 5. | PAGA system block diagram shows System A and system B, so likelihood of failure changed to 5 | E6 | H6 | H6 | F6 | Loss of system primary function = loss of routine voice and data communications Safety - In the event of incident, unable to alert personnel and direct to place of safety - E+ Environment - minimal impact, H Production - No direct impact unless decision to shutdown for loss of PAGA. H Business - Short term diversion of Senior Management time to manage issue/event Likelihood - considered a similar event may occur once or twice in life of facility (6) |  | M3 ¦ Personnel Address (PA) System ¦ Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | best fit MAH barrier chosen.
SYSTEM-99 | RADIO SYSTEMS (INCLUDING SAT COM) | 99 | SYS | N |  | 1 | G6 | H6 | H6 | H6 | B | C | C | C | → | B | Loss of system primary function = backup communication system (SATCOM) and site communications. Mobile phone in non-hazardous area as potential mitigation. Safety - In the event of incident, unable to alert personnel and direct to place of safety -G Environment - minimal impact, H Production - No direct impact unless decision to shutdown for loss of radio systems. H Business - Short term diversion of Senior Management time to manage issue/event Likelihood - considered a similar event may occur once or twice in life of facility (6) | Need to check system details and emergency response impacts | No change to inputs, Notes updated. | G6 | H6 | H6 | H6 | Loss of system primary function = backup communication system (SATCOM) and site communications Safety - In the event of incident, unable to alert personnel and direct to place of safety -G Environment - minimal impact, H Production - No direct impact unless decision to shutdown for loss of PAGA. H Business - Short term diversion of Senior Management time to manage issue/event Likelihood - considered a similar event may occur once or twice in life of facility (6) |  | M3 ¦ Facility radio system ¦ Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | Nearest fit selected
| NO-SYSTEM | XX |  |  |  | 620 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed, tag will inherit failure class criticality components | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added not allocated to a system. | H3 | H3 | H3 | H3 | Not assessed, tag will inherit failure class criticality components |  |  |  | None allocated
| NO-SYSTEM | N/A |  |  |  | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed, tag will inherit failure class criticality components | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added not allocated to a system. | H3 | H3 | H3 | H3 | Not assessed, tag will inherit failure class criticality components |  |  |  | None allocated
| BLANK-SYSTEM |  |  |  |  | 0 | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | Not Assessed | → | Not Assessed | Not assessed. Will be C by default unless overridden by Failure Code. This line is not actually accessed by the lookup formulae in the MEL list, the formula used will default to C if SYSTEM code is not found or blank. | If it is not assessed why are all impacts scored as C? Better to remove this because it might be counted in % A, B or C by accident. | changed to output None whilst there are no non-FA_SYLH coded MEL tags in this system, and Not Assessed if new tags are added not allocated to a system. | H3 | H3 | H3 | H3 | Not assessed. Will be C by default unless overridden by Failure Code. This line is not actually accessed by the lookup formulae in the MEL list, the formula used will default to C if SYSTEM code is not found or blank. |  |  |  | None allocated
Note on G5: Douglas Crooke: EXCLUDES an FA_SYLH in this sytem

## Voted
Final_tag_AplusA | (All)
Count of Final_tag_AplusA |  | SystemSelector | System Criticality
|  | 05 | 13 | 20 | 21 | 22 | 23 | 24 | 25 | 27 | 28 | 29 | 30 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | N/A | XX
Object type2 | Failure code Criticality | A | C | A | A | A | A | A | A | A | A | A | A | A | A | A | A | A | A | A | A | A | C | C | B | B | B | A | C | B | A | C | C | A | B | A | A | A | A | B | B | C | B | A | A | C | A | A | C | B | B | B | C | B | B | B | B | A | B | B | A | A | C | B | A | B | C | C
FA_CFBC | B | [66 empty] | 2
FA_CFSGW | C | System Criticality 81: 3 |  | 2
FA_CFSSE | B | System Criticality 98: 4 |  | 104
FA_CFSSF | C | [66 empty] | 18 | bar: System Criticality 67
FA_CFSST | B | System Criticality 57: 13 |  | 97
FA_EECF | C | System Criticality 42: 12; System Criticality 85: 188; System Criticality 89: 198
FA_EECH | C | System Criticality 20: 4; System Criticality 24: 6; System Criticality 29: 3; System Criticality 30: 2; System Criticality 42: 1; System Criticality 44: 1; System Criticality 45: 2; System Criticality 46: 3; System Criticality 52: 4; System Criticality 64: 1; System Criticality 81: 3; System Criticality 87: 5; System Criticality 91: 29
FA_EECMD | A | System Criticality 81: 3; System Criticality 87: 4
FA_EECMI | C | SystemSelector 05: 5; System Criticality 21: 20; System Criticality 24: 39; System Criticality 25: 14; System Criticality 28: 15; System Criticality 29: 11; System Criticality 30: 59; System Criticality 45: 3; System Criticality 47: 10; System Criticality 51: 8; System Criticality 52: 32; System Criticality 53: 4; System Criticality 56: 16; System Criticality 57: 9; System Criticality 58: 2; System Criticality 60: 14; System Criticality 65: 20; System Criticality 66: 2; System Criticality 67: 17; System Criticality 81: 6; System Criticality 87: 30; System Criticality 91: 41 |  | 2
FA_EECMS | A | bar: System Criticality 44
FA_EECO | C | System Criticality 66: 2; System Criticality 80: 16
FA_EEPBA | C | System Criticality 80: 121; System Criticality 85: 36; System Criticality 87: 47; System Criticality 88: 526; System Criticality 89: 60; System Criticality 91: 78
FA_EEPBV | B | System Criticality 80: 44; System Criticality 87: 3
FA_EEPCS | C | bar: System Criticality 20 to System Criticality 21; System Criticality 27; System Criticality 29; System Criticality 56
FA_EEPNE | C | System Criticality 90: 94 |  | 24
FA_EEPNN | B | System Criticality 80: 4; System Criticality 91: 4
FA_EEPS | B | SystemSelector 05: 17; System Criticality 20: 4; System Criticality 21: 12; System Criticality 27: 2; System Criticality 28: 6; System Criticality 29: 6; System Criticality 30: 18; System Criticality 45: 3; System Criticality 47: 9; System Criticality 51: 8; System Criticality 52: 20; System Criticality 56: 10; System Criticality 57: 4; System Criticality 60: 13; System Criticality 65: 25; System Criticality 66: 5; System Criticality 67: 9
FA_EEPU | A | System Criticality 88: 4
FA_EETB | A | System Criticality 81: 6; System Criticality 87: 1; System Criticality 88: 6; System Criticality 91: 2
FA_EETC | A | System Criticality 87: 4
FA_EETD | C | System Criticality 80: 8; System Criticality 87: 2; System Criticality 90: 60
FA_EETFW | B | System Criticality 80: 16; System Criticality 87: 4
FA_EETGA | B | System Criticality 84: 2; System Criticality 87: 4; System Criticality 91: 4
FA_EETI | B | System Criticality 81: 3; System Criticality 87: 4; System Criticality 88: 2
FA_EETM | C | System Criticality 80: 739; System Criticality 87: 171
FA_EETO | B | SystemSelector 05: 4
FA_EETP | B | SystemSelector 05: 3
FA_EETR | B | System Criticality 92: 2
FA_EETW | C | System Criticality 80: 12; System Criticality 85: 21; System Criticality 86: 2; System Criticality 87: 9; System Criticality 88: 18; System Criticality 89: 46; System Criticality 90: 1; System Criticality 91: 8; System Criticality 94: 2; System Criticality 95: 21
FA_EETY | C | System Criticality 76: 16; System Criticality 77: 6; System Criticality 78: 6
FA_INAM | B | System Criticality 21: 10; System Criticality 27: 4; System Criticality 46: 1
FA_INAP | B | System Criticality 21: 2; System Criticality 27: 2; System Criticality 46: 1; System Criticality 52: 4; System Criticality 60: 1
FA_INDC | B | System Criticality 20: 3; System Criticality 22: 2; System Criticality 66: 3
FA_INDFD | A | System Criticality 87: 12; System Criticality 91: 8
FA_INDFS | B | System Criticality 20: 2; System Criticality 21: 9; System Criticality 24: 24; System Criticality 25: 47; System Criticality 27: 29; System Criticality 45: 3; System Criticality 46: 3; System Criticality 62: 2; System Criticality 65: 50; System Criticality 66: 4; System Criticality 87: 7; System Criticality 91: 24
FA_INDI | C | SystemSelector 05: 27; System Criticality 20: 61; System Criticality 21: 74; System Criticality 22: 5; System Criticality 24: 118; System Criticality 25: 114; System Criticality 27: 91; System Criticality 28: 94; System Criticality 29: 33; System Criticality 30: 98; System Criticality 40: 1; System Criticality 41: 1; System Criticality 42: 13; System Criticality 43: 16; System Criticality 44: 8; System Criticality 45: 15; System Criticality 46: 38; System Criticality 47: 23; System Criticality 51: 4; System Criticality 52: 17; System Criticality 53: 10; System Criticality 54: 1; System Criticality 56: 21; System Criticality 57: 31; System Criticality 58: 3; System Criticality 60: 42; System Criticality 62: 40; System Criticality 63: 8; System Criticality 64: 26; System Criticality 65: 17; System Criticality 66: 13; System Criticality 67: 25; System Criticality 78: 2; System Criticality 81: 84; System Criticality 82: 4; System Criticality 87: 12; System Criticality 91: 59
FA_INDMS | B | System Criticality 20: 53; System Criticality 21: 54; System Criticality 22: 8; System Criticality 24: 152; System Criticality 25: 134; System Criticality 27: 51; System Criticality 28: 20; System Criticality 29: 9; System Criticality 30: 74; System Criticality 42: 20; System Criticality 43: 10; System Criticality 44: 25; System Criticality 45: 16; System Criticality 46: 38; System Criticality 51: 4; System Criticality 52: 18; System Criticality 53: 1; System Criticality 56: 1; System Criticality 57: 7; System Criticality 60: 88; System Criticality 63: 3; System Criticality 64: 2; System Criticality 65: 116; System Criticality 66: 31; System Criticality 67: 15; System Criticality 81: 1; System Criticality 87: 63; System Criticality 91: 372
FA_INDMT | B | SystemSelector 05: 19; System Criticality 20: 131; System Criticality 21: 122; System Criticality 22: 28; System Criticality 24: 256; System Criticality 25: 247; System Criticality 27: 134; System Criticality 28: 106; System Criticality 29: 59; System Criticality 30: 275; System Criticality 40: 8; System Criticality 42: 36; System Criticality 43: 15; System Criticality 44: 28; System Criticality 45: 36; System Criticality 46: 86; System Criticality 47: 50; System Criticality 51: 29; System Criticality 52: 83; System Criticality 53: 6; System Criticality 54: 2; System Criticality 56: 18; System Criticality 57: 28; System Criticality 58: 4; System Criticality 60: 103; System Criticality 62: 2; System Criticality 63: 16; System Criticality 64: 18; System Criticality 65: 85; System Criticality 66: 43; System Criticality 67: 45; System Criticality 81: 37; System Criticality 82: 1; System Criticality 87: 30; System Criticality 91: 224
FA_INDS | C | SystemSelector 05: 6; System Criticality 20: 15; System Criticality 21: 57; System Criticality 22: 1; System Criticality 24: 71; System Criticality 25: 152; System Criticality 27: 72; System Criticality 28: 11; System Criticality 29: 3; System Criticality 30: 38; System Criticality 42: 10; System Criticality 43: 19; System Criticality 44: 10; System Criticality 45: 14; System Criticality 46: 17; System Criticality 52: 7; System Criticality 53: 2; System Criticality 56: 3; System Criticality 57: 4; System Criticality 60: 52; System Criticality 62: 26; System Criticality 63: 40; System Criticality 64: 6; System Criticality 65: 16; System Criticality 66: 28; System Criticality 67: 23; System Criticality 77: 6; System Criticality 78: 1; System Criticality 80: 4; System Criticality 81: 97; System Criticality 86: 1; System Criticality 87: 23; System Criticality 90: 5; System Criticality 91: 204; System Criticality 94: 2 |  | 2
FA_INDT | B | System Criticality 65: 33
FA_INSC | B | SystemSelector 05: 1; System Criticality 87: 2; System Criticality 93: 5
FA_INSJ | A | System Criticality 20: 29; System Criticality 21: 44; System Criticality 22: 34; System Criticality 23: 7; System Criticality 24: 9; System Criticality 25: 43; System Criticality 28: 34; System Criticality 29: 38; System Criticality 30: 63; System Criticality 40: 1; System Criticality 42: 14; System Criticality 44: 2; System Criticality 45: 10; System Criticality 46: 6; System Criticality 47: 15; System Criticality 53: 3; System Criticality 56: 2; System Criticality 57: 3; System Criticality 58: 1; System Criticality 60: 29; System Criticality 63: 1; System Criticality 64: 1; System Criticality 65: 17; System Criticality 66: 12; System Criticality 67: 26; System Criticality 78: 171; System Criticality 81: 6; System Criticality 82: 1; System Criticality 91: 3 |  | 109
FA_INSL | C | SystemSelector 05: 7; System Criticality 20: 4; System Criticality 25: 7; System Criticality 27: 2; System Criticality 42: 4; System Criticality 46: 5; System Criticality 52: 2; System Criticality 60: 23; System Criticality 63: 2; System Criticality 64: 2; System Criticality 65: 15; System Criticality 66: 2; System Criticality 75: 1; System Criticality 76: 48; System Criticality 77: 2; System Criticality 78: 44; System Criticality 80: 3; System Criticality 81: 6; System Criticality 87: 4; System Criticality 88: 8; System Criticality 90: 1; System Criticality 91: 9 |  | 5
FA_INSS | B | [66 empty] | 2 | bar: System Criticality 98
FA_INSY | A | System Criticality 22: 1; System Criticality 76: 5; System Criticality 77: 13
FA_PEA | C | SystemSelector 05: 2; System Criticality 20: 5; System Criticality 21: 5; System Criticality 24: 10; System Criticality 27: 28; System Criticality 28: 2; System Criticality 29: 2; System Criticality 45: 4; System Criticality 46: 12; System Criticality 47: 7; System Criticality 63: 2; System Criticality 64: 2; System Criticality 65: 12; System Criticality 81: 15; System Criticality 87: 3; System Criticality 91: 14
FA_PEG | C | 40 |  | 603 | 460 | 91 |  | 466 | 586 | 154 | 886 | 296 | 1184 | 96 | 78 | 365 | 24 | 228 | 90 | 206 | 174 | 1 |  |  | 102 | 553 | 176 | 267 |  | 382 | 444 | 432 |  | 425 | 14 | 19 | 423 | 354 | 250 | 132 | 538 | [6 empty] | 467 | 27 |  |  |  | 5 | 50 |  |  |  | 118 | [9 empty] | 17
FA_PEL | A | bar: System Criticality 22; System Criticality 27
FA_PEM | B | System Criticality 63: 130; System Criticality 91: 4
FA_PEO | C | System Criticality 20: 15; System Criticality 21: 16; System Criticality 22: 3; System Criticality 24: 54; System Criticality 25: 36; System Criticality 27: 28; System Criticality 28: 19; System Criticality 29: 13; System Criticality 30: 26; System Criticality 41: 1; System Criticality 42: 1; System Criticality 43: 2; System Criticality 44: 3; System Criticality 45: 7; System Criticality 46: 8; System Criticality 47: 2; System Criticality 53: 1; System Criticality 56: 7; System Criticality 57: 7; System Criticality 58: 1; System Criticality 60: 31; System Criticality 64: 6; System Criticality 66: 20; System Criticality 67: 15; System Criticality 81: 15; System Criticality 82: 2; System Criticality 91: 12
FA_PESC | A | SystemSelector 05: 13; System Criticality 20: 41; System Criticality 21: 30; System Criticality 22: 9; System Criticality 24: 52; System Criticality 25: 54; System Criticality 27: 45; System Criticality 28: 15; System Criticality 29: 10; System Criticality 30: 41; System Criticality 40: 4; System Criticality 45: 9; System Criticality 46: 26; System Criticality 47: 13; System Criticality 51: 8; System Criticality 52: 22; System Criticality 54: 1; System Criticality 56: 2; System Criticality 57: 3; System Criticality 60: 9; System Criticality 62: 1; System Criticality 63: 10; System Criticality 64: 6; System Criticality 65: 12; System Criticality 66: 4; System Criticality 67: 8; System Criticality 81: 35; System Criticality 87: 6; System Criticality 91: 13
FA_PESR | A | SystemSelector 05: 6; System Criticality 20: 4; System Criticality 21: 6; System Criticality 81: 21; System Criticality 91: 12
FA_PESV | A | System Criticality 21: 2; System Criticality 28: 5; System Criticality 29: 3; System Criticality 52: 2; System Criticality 64: 1; System Criticality 67: 2
FA_PET | A | System Criticality 20: 22; System Criticality 21: 27; System Criticality 24: 34; System Criticality 25: 84; System Criticality 27: 24; System Criticality 28: 21; System Criticality 29: 2; System Criticality 30: 64; System Criticality 42: 2; System Criticality 44: 2; System Criticality 45: 9; System Criticality 46: 17; System Criticality 52: 7; System Criticality 54: 1; System Criticality 57: 7; System Criticality 60: 23; System Criticality 64: 2; System Criticality 65: 7; System Criticality 66: 5; System Criticality 67: 3
FA_PEVB | C | SystemSelector 05: 24; System Criticality 20: 340; System Criticality 21: 350; System Criticality 22: 66; System Criticality 24: 37; System Criticality 25: 588; System Criticality 27: 346; System Criticality 28: 519; System Criticality 29: 187; System Criticality 30: 993; System Criticality 40: 75; System Criticality 41: 18; System Criticality 42: 40; System Criticality 43: 56; System Criticality 44: 15; System Criticality 45: 93; System Criticality 46: 204; System Criticality 47: 138; System Criticality 51: 57; System Criticality 52: 155; System Criticality 53: 49; System Criticality 54: 25; System Criticality 56: 35; System Criticality 57: 102; System Criticality 58: 15; System Criticality 60: 53; System Criticality 62: 36; System Criticality 63: 90; System Criticality 64: 110; System Criticality 65: 66; System Criticality 66: 30; System Criticality 67: 279; System Criticality 81: 149; System Criticality 82: 3; System Criticality 87: 51; System Criticality 91: 132 |  | 9
FA_PEVC | C | SystemSelector 05: 27; System Criticality 20: 22; System Criticality 21: 60; System Criticality 22: 1; System Criticality 24: 42; System Criticality 25: 23; System Criticality 27: 40; System Criticality 28: 116; System Criticality 29: 39; System Criticality 30: 103; System Criticality 40: 6; System Criticality 41: 10; System Criticality 42: 11; System Criticality 43: 3; System Criticality 44: 14; System Criticality 45: 6; System Criticality 46: 39; System Criticality 47: 35; System Criticality 51: 6; System Criticality 52: 58; System Criticality 53: 14; System Criticality 54: 17; System Criticality 56: 11; System Criticality 57: 29; System Criticality 58: 2; System Criticality 60: 24; System Criticality 62: 5; System Criticality 63: 28; System Criticality 64: 39; System Criticality 65: 25; System Criticality 66: 18; System Criticality 67: 41; System Criticality 81: 18; System Criticality 87: 9; System Criticality 91: 72
FA_PEVD | C | System Criticality 81: 3
FA_PEVG | C | System Criticality 20: 143; System Criticality 21: 213; System Criticality 22: 11; System Criticality 24: 371; System Criticality 25: 248; System Criticality 27: 22; System Criticality 28: 28; System Criticality 29: 6; System Criticality 30: 208; System Criticality 40: 8; System Criticality 41: 46; System Criticality 42: 138; System Criticality 43: 8; System Criticality 44: 81; System Criticality 45: 32; System Criticality 46: 22; System Criticality 47: 3; System Criticality 52: 3; System Criticality 53: 11; System Criticality 56: 52; System Criticality 57: 40; System Criticality 58: 56; System Criticality 60: 253; System Criticality 62: 2; System Criticality 64: 9; System Criticality 65: 30; System Criticality 66: 89; System Criticality 67: 2; System Criticality 81: 162; System Criticality 82: 2; System Criticality 87: 5; System Criticality 91: 27
FA_PEVL | C | System Criticality 20: 191; System Criticality 21: 36; System Criticality 22: 52; System Criticality 24: 48; System Criticality 25: 74; System Criticality 27: 24; System Criticality 28: 150; System Criticality 29: 11; System Criticality 30: 39; System Criticality 40: 10; System Criticality 42: 7; System Criticality 43: 7; System Criticality 44: 11; System Criticality 45: 15; System Criticality 46: 23; System Criticality 47: 10; System Criticality 51: 2; System Criticality 52: 8; System Criticality 56: 1; System Criticality 57: 13; System Criticality 58: 3; System Criticality 60: 25; System Criticality 63: 5; System Criticality 64: 5; System Criticality 66: 14; System Criticality 67: 29; System Criticality 81: 1
FA_PEVM | B | System Criticality 52: 4; System Criticality 81: 5
FA_PEVN | C | System Criticality 20: 16; System Criticality 25: 13; System Criticality 27: 10; System Criticality 28: 11; System Criticality 45: 2; System Criticality 46: 4; System Criticality 47: 4; System Criticality 52: 3; System Criticality 60: 2; System Criticality 64: 8
FA_PEVX | A | System Criticality 42: 1; System Criticality 87: 3
FA_PEVY | B | System Criticality 25: 1; System Criticality 27: 1; System Criticality 63: 22; System Criticality 64: 6; System Criticality 65: 5; System Criticality 66: 4; System Criticality 81: 26
FA_REBC | A | System Criticality 25: 2; System Criticality 43: 2
FA_REC | B | System Criticality 30: 4
FA_REDH | B | System Criticality 81: 6
FA_REDP | B | System Criticality 21: 3; System Criticality 27: 6; System Criticality 87: 2
FA_REEL | A | System Criticality 81: 3; System Criticality 87: 1
FA_REFA | A | System Criticality 21: 9; System Criticality 45: 3; System Criticality 87: 9
FA_REFC | B | System Criticality 24: 27; System Criticality 25: 13; System Criticality 30: 23; System Criticality 60: 4; System Criticality 65: 15; System Criticality 66: 2; System Criticality 67: 3; System Criticality 87: 6; System Criticality 91: 28
FA_REMC | B | System Criticality 27: 2; System Criticality 87: 1
FA_REMR | A | System Criticality 24: 6
FA_REMT | B | System Criticality 65: 10; System Criticality 87: 1
FA_RENG | A | System Criticality 27: 2; System Criticality 80: 2; System Criticality 91: 4
FA_REPC | B | SystemSelector 05: 5; System Criticality 21: 10; System Criticality 24: 10; System Criticality 28: 19; System Criticality 29: 15; System Criticality 30: 29; System Criticality 47: 14; System Criticality 51: 11; System Criticality 52: 34; System Criticality 53: 4; System Criticality 56: 16; System Criticality 57: 12; System Criticality 58: 2; System Criticality 60: 13; System Criticality 62: 2; System Criticality 65: 5; System Criticality 67: 14; System Criticality 81: 14; System Criticality 82: 2; System Criticality 87: 6; System Criticality 91: 13
FA_REPD | B | System Criticality 81: 6; System Criticality 87: 6
FA_RER | B | bar: System Criticality 56; System Criticality 67
FA_RETP | B | System Criticality 65: 5
FA_SEC | C | System Criticality 65: 6
FA_SEFB | C | System Criticality 20: 4; System Criticality 21: 24; System Criticality 22: 1; System Criticality 24: 11; System Criticality 25: 6; System Criticality 27: 9; System Criticality 28: 22; System Criticality 29: 11; System Criticality 30: 36; System Criticality 40: 4; System Criticality 41: 4; System Criticality 43: 4; System Criticality 45: 3; System Criticality 46: 2; System Criticality 47: 9; System Criticality 51: 9; System Criticality 52: 31; System Criticality 53: 4; System Criticality 57: 3; System Criticality 60: 10; System Criticality 62: 2; System Criticality 65: 3; System Criticality 67: 10; System Criticality 81: 25; System Criticality 91: 28
FA_SEFE | C | SystemSelector 05: 6; System Criticality 20: 2; System Criticality 21: 2; System Criticality 24: 6; System Criticality 25: 9; System Criticality 27: 4; System Criticality 29: 5; System Criticality 30: 6; System Criticality 45: 2; System Criticality 46: 6; System Criticality 47: 8; System Criticality 51: 2; System Criticality 60: 1; System Criticality 62: 2; System Criticality 63: 4; System Criticality 64: 2; System Criticality 65: 35; System Criticality 67: 2; System Criticality 81: 23; System Criticality 87: 25; System Criticality 91: 34
FA_SEFS | C | System Criticality 27: 4; System Criticality 46: 2; System Criticality 91: 12
FA_SEHF | B | System Criticality 21: 2; System Criticality 24: 9; System Criticality 25: 3; System Criticality 27: 2; System Criticality 30: 8; System Criticality 45: 1; System Criticality 60: 1; System Criticality 65: 30; System Criticality 67: 1; System Criticality 87: 4; System Criticality 91: 4
FA_SEHS | B | System Criticality 21: 6; System Criticality 28: 11; System Criticality 30: 19; System Criticality 52: 2; System Criticality 60: 8
FA_SEHT | B | System Criticality 20: 18; System Criticality 21: 3; System Criticality 25: 5; System Criticality 27: 2; System Criticality 30: 4; System Criticality 46: 3; System Criticality 57: 3; System Criticality 81: 6; System Criticality 91: 4
FA_SEL | A | SystemSelector 05: 2; System Criticality 22: 1; System Criticality 27: 2; System Criticality 46: 1; System Criticality 56: 7; System Criticality 58: 2; System Criticality 62: 2; System Criticality 67: 2; System Criticality 81: 2; System Criticality 87: 5; System Criticality 91: 16
FA_SEM | A | System Criticality 42: 1; System Criticality 43: 2; System Criticality 44: 1
FA_SENF | B | System Criticality 25: 3; System Criticality 60: 2
FA_SEPA | A | SystemSelector 05: 6; System Criticality 21: 6; System Criticality 28: 10; System Criticality 30: 20; System Criticality 52: 2; System Criticality 81: 18
FA_SEPC | C | System Criticality 20: 10; System Criticality 21: 1; System Criticality 25: 6; System Criticality 27: 7; System Criticality 28: 12; System Criticality 42: 1; System Criticality 45: 1; System Criticality 46: 3; System Criticality 47: 2; System Criticality 57: 6; System Criticality 60: 1; System Criticality 64: 4; System Criticality 87: 5
FA_SEPHC | B | System Criticality 21: 2
FA_SEPHS | C | System Criticality 20: 7; System Criticality 21: 8; System Criticality 24: 9; System Criticality 25: 14; System Criticality 27: 4; System Criticality 28: 6; System Criticality 29: 5; System Criticality 30: 9; System Criticality 40: 1; System Criticality 42: 1; System Criticality 43: 3; System Criticality 44: 1; System Criticality 45: 2; System Criticality 46: 1; System Criticality 47: 2; System Criticality 53: 2; System Criticality 57: 6; System Criticality 60: 17; System Criticality 63: 6; System Criticality 64: 22; System Criticality 65: 5; System Criticality 66: 2; System Criticality 67: 6; System Criticality 87: 2; System Criticality 91: 16
FA_SES | C | System Criticality 24: 16; System Criticality 47: 16; System Criticality 51: 8; System Criticality 52: 32
FA_SETAC | B | SystemSelector 05: 2; System Criticality 21: 2; System Criticality 24: 10; System Criticality 28: 5; System Criticality 29: 4; System Criticality 30: 6; System Criticality 51: 3; System Criticality 52: 6; System Criticality 53: 1; System Criticality 56: 1; System Criticality 62: 3; System Criticality 67: 2; System Criticality 81: 9; System Criticality 87: 4; System Criticality 91: 1
FA_SETAP | B | System Criticality 28: 3; System Criticality 56: 6; System Criticality 57: 3; System Criticality 58: 2; System Criticality 60: 1; System Criticality 65: 5; System Criticality 67: 3; System Criticality 82: 3 |  | 12
FA_SETPC | A | System Criticality 57: 1; System Criticality 81: 5; System Criticality 87: 5
FA_SEZ | C | System Criticality 63: 2; System Criticality 64: 1; System Criticality 65: 30; System Criticality 66: 1; System Criticality 87: 1; System Criticality 91: 28
FA_SQFC | B | System Criticality 81: 21
FA_SQFDF | A | System Criticality 78: 357; System Criticality 87: 4; System Criticality 91: 12 |  | 2
FA_SQFDG | A | System Criticality 78: 600; System Criticality 87: 2; System Criticality 91: 24 |  | 2
FA_SQFDS | A | System Criticality 78: 35; System Criticality 81: 1
FA_SQFFD | A | System Criticality 81: 5; System Criticality 91: 12
FA_SQFFH | A | System Criticality 81: 3
FA_SQFFM | A | System Criticality 81: 19
FA_SQFFY | A | System Criticality 81: 109
FA_SQFRA | A | System Criticality 60: 1; System Criticality 78: 136; System Criticality 81: 29; System Criticality 82: 1; System Criticality 91: 8
FA_SQFRE | A | System Criticality 53: 18
FA_SQMT | C | System Criticality 24: 2
FA_SQTA | A | System Criticality 78: 11; System Criticality 81: 15; System Criticality 87: 5 |  | 3
FA_SQTB | A | System Criticality 78: 4; System Criticality 81: 45; System Criticality 91: 8; System Criticality 98: 34 |  | 6
FA_SQTE | A | System Criticality 83: 11; System Criticality 99: 1 |  | 4
FA_SQTL | A | System Criticality 98: 262 |  | 32
FA_SQTOF | B | [66 empty] | 2
FA_SQTP | C | System Criticality 98: 12 |  | 92
FA_SQTS | B | System Criticality 83: 9; System Criticality 97: 12; System Criticality 98: 2 |  | 55
FA_SQTV | C | System Criticality 76: 18; System Criticality 83: 1; System Criticality 96: 82
FA_SQTW | B | [66 empty] | 17
FA_SQTY | A | System Criticality 78: 4
FA_SYLH | C | 8 | 3 | 8 | 6 | 6 | 3 | 6 | 7 | 7 | 6 | 5 | 3 | 6 | 5 | 5 | 4 | 5 | 4 | 4 | 6 | 4 | 3 | 3 | 3 | 4 | 7 | 6 | 3 | 5 | 5 | 5 | 2 | 5 | 4 | 5 | 5 | 5 | 4 | 3 | 6 |  | 3 | 5 | 3 | 4 | 4 | 9 | 4 | 5 | 5 | 3 | 4 | 6 | 3 | 2 | 3 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 26
FA_WEHY | C | System Criticality 30: 2

## FCodeToUMCL+
Count of Functional location |  | Failure code Criticality
Object type2 | UMCL PLUS | A | B | C | Grand Total
FA_CFBC | 63741 |  | 2 |  | 2
FA_CFSGW | 63750 |  |  | 5 | 5
FA_CFSSE | 63759 |  | 104 |  | 104
| (blank) |  | 4 |  | 4
FA_CFSSF | 63760 |  |  | 19 | 19
FA_CFSST | 63757 |  | 110 |  | 110
FA_EECF | 1494 |  |  | 398 | 398
FA_EECH | 1450 |  |  | 46 | 46
| (blank) |  |  | 18 | 18
FA_EECMD | 1392 | 7 |  |  | 7
FA_EECMI | 1731 |  |  | 6 | 6
| 63774 |  |  | 373 | 373
FA_EECMS | 63773 | 1 |  |  | 1
FA_EECO | 1664 |  |  | 18 | 18
FA_EEPBA | 63762 |  |  | 868 | 868
FA_EEPBV | 1336 |  | 47 |  | 47
FA_EEPCS | 1331 |  |  | 5 | 5
FA_EEPNE | 1383 |  |  | 118 | 118
FA_EEPNN | 1394 |  | 8 |  | 8
FA_EEPS | 63765 |  | 171 |  | 171
FA_EEPU | 1721 | 4 |  |  | 4
FA_EETB | 1322 | 13 |  |  | 13
| 1721 | 2 |  |  | 2
FA_EETC | 1325 | 4 |  |  | 4
FA_EETD | 1324 |  |  | 70 | 70
FA_EETFW | 63771 |  | 20 |  | 20
FA_EETGA | 1384 |  | 10 |  | 10
FA_EETI | 1456 |  | 9 |  | 9
FA_EETM | 63767 |  |  | 910 | 910
FA_EETO | (blank) |  | 4 |  | 4
FA_EETP | 1380 |  | 3 |  | 3
FA_EETR | 1654 |  | 2 |  | 2
FA_EETW | 1660 |  |  | 140 | 140
FA_EETY | 1337 |  |  | 28 | 28
FA_INAM | 1581 |  | 15 |  | 15
FA_INAP | (blank) |  | 10 |  | 10
FA_INDC | 63784 |  | 8 |  | 8
FA_INDFD | 1372 | 20 |  |  | 20
FA_INDFS | 1740 |  | 204 |  | 204
FA_INDI | (blank) |  |  | 1249 | 1249
FA_INDMS | 1569 |  | 1378 |  | 1378
| 1905 |  | 8 |  | 8
FA_INDMT | 1720 |  | 1 |  | 1
| 1905 |  | 2408 |  | 2408
| (blank) |  | 1 |  | 1
FA_INDS | 41348 |  |  | 1048 | 1048
FA_INDT | 1370 |  | 33 |  | 33
FA_INSC | 1351 |  | 8 |  | 8
FA_INSJ | 1459 | 734 |  |  | 734
FA_INSL | 63786 |  |  | 206 | 206
FA_INSS | 63787 |  | 3 |  | 3
FA_INSY | 33425 | 19 |  |  | 19
FA_PEA | 70849 |  |  | 123 | 123
| (blank) |  |  | 2 | 2
FA_PEG | 1999 |  |  | 5 | 5
| 2114 |  |  | 11202 | 11202
| (blank) |  |  | 17 | 17
FA_PEL | 71011 | 2 |  |  | 2
FA_PEM | 2019 |  | 134 |  | 134
FA_PEO | 1657 |  |  | 351 | 351
FA_PESC | 1735 | 502 |  |  | 502
FA_PESR | 1326 | 49 |  |  | 49
FA_PESV | 1742 | 15 |  |  | 15
FA_PET | 1720 | 363 |  |  | 363
FA_PEVB | 1722 |  |  | 4906 | 4906
| 1729 |  |  | 1 | 1
| 1731 |  |  | 628 | 628
FA_PEVC | 1724 |  |  | 1013 | 1013
FA_PEVD | 1725 |  |  | 3 | 3
FA_PEVG | 1722 |  |  | 4 | 4
| 1729 |  |  | 2318 | 2318
| 1731 |  |  | 9 | 9
FA_PEVL | 1730 |  |  | 814 | 814
FA_PEVM | 1732 |  | 9 |  | 9
FA_PEVN | 1723 |  |  | 12 | 12
| 1733 |  |  | 61 | 61
FA_PEVX | 109918 | 4 |  |  | 4
FA_PEVY | 1723 |  | 65 |  | 65
FA_REBC | 71013 | 4 |  |  | 4
FA_REC | 1341 |  | 4 |  | 4
FA_REDH | 1544 |  | 6 |  | 6
FA_REDP | 1545 |  | 11 |  | 11
FA_REEL | 1338 | 4 |  |  | 4
FA_REFA | 1396 | 21 |  |  | 21
FA_REFC | 1397 |  | 121 |  | 121
FA_REMC | 1358 |  | 3 |  | 3
FA_REMR | 1360 | 6 |  |  | 6
FA_REMT | 1361 |  | 11 |  | 11
FA_RENG | 1427 | 8 |  |  | 8
FA_REPC | 1641 |  | 246 |  | 246
| 1644 |  | 4 |  | 4
FA_REPD | 1644 |  | 12 |  | 12
FA_RER | (blank) |  | 2 |  | 2
FA_RETP | (blank) |  | 5 |  | 5
FA_SEC | 1771 |  |  | 6 | 6
FA_SEFB | 33433 |  |  | 275 | 275
FA_SEFE | 1410 |  |  | 186 | 186
FA_SEFS | 1414 |  |  | 6 | 6
| 1757 |  |  | 12 | 12
FA_SEHF | 1432 |  | 65 |  | 65
FA_SEHS | 1436 |  | 46 |  | 46
FA_SEHT | 1439 |  | 40 |  | 40
| 1450 |  | 8 |  | 8
FA_SEL | 1467 | 42 |  |  | 42
FA_SEM | 2058 | 4 |  |  | 4
FA_SENF | 41394 |  | 5 |  | 5
FA_SEPA | 1752 | 62 |  |  | 62
FA_SEPC | 1773 |  |  | 59 | 59
FA_SEPHC | 1772 |  | 2 |  | 2
FA_SEPHS | 1662 |  |  | 157 | 157
FA_SES | 1762 |  |  | 72 | 72
FA_SETAC | 1715 |  | 59 |  | 59
FA_SETAP | 41396 |  | 38 |  | 38
FA_SETPC | 63830 | 11 |  |  | 11
FA_SEZ | 1663 |  |  | 63 | 63
FA_SQFC | (blank) |  | 21 |  | 21
FA_SQFDF | 33419 | 375 |  |  | 375
FA_SQFDG | 1402 | 577 |  |  | 577
| (blank) | 51 |  |  | 51
FA_SQFDS | 33434 | 36 |  |  | 36
FA_SQFFD | 2054 | 17 |  |  | 17
FA_SQFFH | 1477 | 3 |  |  | 3
FA_SQFFM | 1471 | 19 |  |  | 19
FA_SQFFY | 1478 | 109 |  |  | 109
FA_SQFRA | 1488 | 175 |  |  | 175
FA_SQFRE | 1465 | 18 |  |  | 18
FA_SQMT | (blank) |  |  | 2 | 2
FA_SQTA | (blank) | 34 |  |  | 34
FA_SQTB | 1679 | 97 |  |  | 97
FA_SQTE | 1697 | 16 |  |  | 16
FA_SQTL | 1702 | 294 |  |  | 294
FA_SQTOF | 1685 |  | 2 |  | 2
FA_SQTP | (blank) |  |  | 104 | 104
FA_SQTS | 1706 |  | 78 |  | 78
FA_SQTV | 1681 |  |  | 101 | 101
FA_SQTW | 41448 |  | 17 |  | 17
FA_SQTY | 33399 | 4 |  |  | 4
FA_SYLH | (blank) |  |  | 313 | 313
FA_WEHY | (blank) |  |  | 2 | 2
Grand Total |  | 3726 | 5585 | 28352 | 37663

## FCodeToUMCL+ToISO
Count of Functional location |  |  | Failure code Criticality
Object type2 | UMCL PLUS | ISO CODE | A | B | C | Grand Total
FA_CFBC | 63741 | BICR |  | 2 |  | 2
FA_CFSGW | 63750 | BIFE |  |  | 5 | 5
FA_CFSSE | 63759 | STGN |  | 104 |  | 104
| (blank) | (blank) |  | 4 |  | 4
FA_CFSSF | 63760 | BISF |  |  | 19 | 19
FA_CFSST | 63757 | BISB |  | 110 |  | 110
FA_EECF | 1494 | LIEL |  |  | 398 | 398
FA_EECH | 1450 | HBEH |  |  | 46 | 46
| (blank) | (blank) |  |  | 18 | 18
FA_EECMD | 1392 | EMDC | 7 |  |  | 7
FA_EECMI | 1731 | MAEL |  |  | 6 | 6
| 63774 | EMAC |  |  | 373 | 373
FA_EECMS | 63773 | EMAC | 1 |  |  | 1
FA_EECO | 1664 | SKEL |  |  | 18 | 18
FA_EEPBA | 63762 | ESCB |  |  | 868 | 868
FA_EEPBV | 1336 | VACB |  | 47 |  | 47
FA_EEPCS | 1331 | CAAN |  |  | 5 | 5
FA_EEPNE | 1383 | EBEL |  |  | 118 | 118
FA_EEPNN | 1394 | EREL |  | 8 |  | 8
FA_EEPS | 63765 | SWSS |  | 171 |  | 171
FA_EEPU | 1721 | UPUB | 4 |  |  | 4
FA_EETB | 1322 | BAEL | 13 |  |  | 13
| 1721 | UPUB | 2 |  |  | 2
FA_EETC | 1325 | BCEL | 4 |  |  | 4
FA_EETD | 1324 | BBEL |  |  | 70 | 70
FA_EETFW | 63771 | PTOT |  | 20 |  | 20
FA_EETGA | 1384 | (blank) |  | 10 |  | 10
FA_EETI | 1456 | ISEL |  | 9 |  | 9
FA_EETM | 63767 | (blank) |  |  | 910 | 910
FA_EETO | (blank) | (blank) |  | 4 |  | 4
FA_EETP | 1380 | CPEL |  | 3 |  | 3
FA_EETR | 1654 | RCEL |  | 2 |  | 2
FA_EETW | 1660 | SG__ |  |  | 140 | 140
FA_EETY | 1337 | (blank) |  |  | 28 | 28
FA_INAM | 1581 | PSFS |  | 15 |  | 15
FA_INAP | (blank) | (blank) |  | 10 |  | 10
FA_INDC | 63784 | CLCP |  | 8 |  | 8
FA_INDFD | 1372 | DAWD | 20 |  |  | 20
FA_INDFS | 1740 | VCSO |  | 204 |  | 204
FA_INDI | (blank) | (blank) |  |  | 1249 | 1249
FA_INDMS | 1569 | PS__ |  | 54 |  | 54
|  | (blank) |  | 1324 |  | 1324
| 1905 | PSTT |  | 8 |  | 8
FA_INDMT | 1720 | PSTW |  | 1 |  | 1
| 1905 | DEVD |  | 190 |  | 190
|  | PSFT |  | 239 |  | 239
|  | PSLT |  | 367 |  | 367
|  | PSPT |  | 156 |  | 156
|  | PSTT |  | 534 |  | 534
|  | TXGA |  | 922 |  | 922
| (blank) | (blank) |  | 1 |  | 1
FA_INDS | 41348 | PSHS |  |  | 400 | 400
|  | PSSG |  |  | 648 | 648
FA_INDT | 1370 | (blank) |  | 33 |  | 33
FA_INSC | 1351 | CLLC |  | 8 |  | 8
FA_INSJ | 1459 | JBGE | 734 |  |  | 734
FA_INSL | 63786 | CLCP |  |  | 206 | 206
FA_INSS | 63787 | (blank) |  | 3 |  | 3
FA_INSY | 33425 | FGCP | 19 |  |  | 19
FA_PEA | 70849 | VASA |  |  | 123 | 123
| (blank) | (blank) |  |  | 2 | 2
FA_PEG | 1999 | PICA |  |  | 5 | 5
| 2114 | PICA |  |  | 11202 | 11202
| (blank) | (blank) |  |  | 17 | 17
FA_PEL | 71011 | PIPG | 2 |  |  | 2
FA_PEM | 2019 | DC |  | 134 |  | 134
FA_PEO | 1657 | ROGN |  |  | 351 | 351
FA_PESC | 1735 | VASC | 502 |  |  | 502
FA_PESR | 1326 | BDGN | 49 |  |  | 49
FA_PESV | 1742 | VASV | 15 |  |  | 15
FA_PET | 1720 | PSTW | 363 |  |  | 363
FA_PEVB | 1722 | VABA |  |  | 4906 | 4906
| 1729 | VAGA |  |  | 1 | 1
| 1731 | MAEL |  |  | 22 | 22
|  | VAXL |  |  | 38 | 38
|  | VCGN |  |  | 568 | 568
FA_PEVC | 1724 | VACH |  |  | 1013 | 1013
FA_PEVD | 1725 | VADI |  |  | 3 | 3
FA_PEVG | 1722 | VABA |  |  | 4 | 4
| 1729 | VAGA |  |  | 2318 | 2318
| 1731 | MAEL |  |  | 3 | 3
|  | VCGN |  |  | 6 | 6
FA_PEVL | 1730 | VAGL |  |  | 814 | 814
FA_PEVM | 1732 | VAMO |  | 9 |  | 9
FA_PEVN | 1723 | VABP |  |  | 12 | 12
| 1733 | VANE |  |  | 61 | 61
FA_PEVX | 109918 | (blank) | 4 |  |  | 4
FA_PEVY | 1723 | VABP |  | 65 |  | 65
FA_REBC | 71013 | BL | 4 |  |  | 4
FA_REC | 1341 | CF |  | 4 |  | 4
FA_REDH | 1544 | MOHY |  | 6 |  | 6
FA_REDP | 1545 | MOPN |  | 11 |  | 11
FA_REEL | 1338 | CEDE | 4 |  |  | 4
FA_REFA | 1396 | FAAX | 21 |  |  | 21
FA_REFC | 1397 | BL |  | 121 |  | 121
FA_REMC | 1358 | COCE |  | 3 |  | 3
FA_REMR | 1360 | CORE | 6 |  |  | 6
FA_REMT | 1361 | (blank) |  | 11 |  | 11
FA_RENG | 1427 | (blank) | 8 |  |  | 8
FA_REPC | 1641 | PUCE |  | 246 |  | 246
| 1644 | (blank) |  | 4 |  | 4
FA_REPD | 1644 | (blank) |  | 12 |  | 12
FA_RER | (blank) | (blank) |  | 2 |  | 2
FA_RETP | (blank) | (blank) |  | 5 |  | 5
FA_SEC | 1771 | VEHY |  |  | 6 | 6
FA_SEFB | 33433 | FIGE |  |  | 275 | 275
FA_SEFE | 1410 | FS |  |  | 186 | 186
FA_SEFS | 1414 | FS |  |  | 6 | 6
| 1757 | VECA |  |  | 12 | 12
FA_SEHF | 1432 | (blank) |  | 65 |  | 65
FA_SEHS | 1436 | HES |  | 46 |  | 46
FA_SEHT | 1439 | HEST |  | 40 |  | 40
| 1450 | HBEH |  | 8 |  | 8
FA_SEL | 1467 | LCFA | 42 |  |  | 42
FA_SEM | 2058 | STFL | 4 |  |  | 4
FA_SENF | 41394 | HBDF |  | 5 |  | 5
FA_SEPA | 1752 | VEAH | 62 |  |  | 62
FA_SEPC | 1773 | VEPC |  |  | 59 | 59
FA_SEPHC | 1772 | VEKO |  | 2 |  | 2
FA_SEPHS | 1662 | VESE |  |  | 157 | 157
FA_SES | 1762 | VEFP |  |  | 72 | 72
FA_SETAC | 1715 | TAFX |  | 59 |  | 59
FA_SETAP | 41396 | VESU |  | 38 |  | 38
FA_SETPC | 63830 | (blank) | 11 |  |  | 11
FA_SEZ | 1663 | SIGN |  |  | 63 | 63
FA_SQFC | (blank) | (blank) |  | 21 |  | 21
FA_SQFDF | 33419 | FGBF | 367 |  |  | 367
|  | FGBH | 8 |  |  | 8
FA_SQFDG | 1402 | FGAB | 18 |  |  | 18
|  | FGAS | 17 |  |  | 17
|  | FGBH | 542 |  |  | 542
| (blank) | (blank) | 51 |  |  | 51
FA_SQFDS | 33434 | DESM | 36 |  |  | 36
FA_SQFFD | 2054 | PUFF | 17 |  |  | 17
FA_SQFFH | 1477 | LCHR | 3 |  |  | 3
FA_SQFFM | 1471 | LCFM | 19 |  |  | 19
FA_SQFFY | 1478 | LCHY | 109 |  |  | 109
FA_SQFRA | 1488 | FGMA | 175 |  |  | 175
FA_SQFRE | 1465 | LCSS | 18 |  |  | 18
FA_SQMT | (blank) | (blank) |  |  | 2 | 2
FA_SQTA | (blank) | (blank) | 34 |  |  | 34
FA_SQTB | 1679 | CMBE | 97 |  |  | 97
FA_SQTE | 1697 | TCRA | 16 |  |  | 16
FA_SQTL | 1702 | TCSP | 294 |  |  | 294
FA_SQTOF | 1685 | CMRC |  | 2 |  | 2
FA_SQTP | (blank) | (blank) |  |  | 104 | 104
FA_SQTS | 1706 | TCTS |  | 78 |  | 78
FA_SQTV | 1681 | TCCA |  |  | 101 | 101
FA_SQTW | 41448 | BICG |  | 17 |  | 17
FA_SQTY | 33399 | (blank) | 4 |  |  | 4
FA_SYLH | (blank) | (blank) |  |  | 313 | 313
FA_WEHY | (blank) | (blank) |  |  | 2 | 2
Grand Total |  |  | 3726 | 5585 | 28352 | 37663

## FCodeToUMCL+ToISOToFCode+
Count of Functional location |  |  |  | Failure code Criticality
Object type2 | UMCL PLUS | ISO CODE | FAILURE CODE PLUS | A | B | C | Grand Total
FA_CFBC | 63741 | BICR | CONTROL ROOM |  | 2 |  | 2
FA_CFSGW | 63750 | BIFE | WALL OR FENCE |  |  | 5 | 5
FA_CFSSE | 63759 | STGN | EQUIPMENT SUPPORT STRUCTURE |  | 104 |  | 104
| (blank) | (blank) | (blank) |  | 4 |  | 4
FA_CFSSF | 63760 | BISF | STRUCTURAL FOUNDATION |  |  | 19 | 19
FA_CFSST | 63757 | BISB | STRUCTURAL BASE |  | 110 |  | 110
FA_EECF | 1494 | LIEL | LIGHT FITTING |  |  | 398 | 398
FA_EECH | 1450 | HBEH | ELECTRIC HEATER |  |  | 46 | 46
| (blank) | (blank) | (blank) |  |  | 18 | 18
FA_EECMD | 1392 | EMDC | DC ELECTRIC MOTOR | 6 |  |  | 6
|  |  | (blank) | 1 |  |  | 1
FA_EECMI | 1731 | MAEL | MOV VALVE - MOV |  |  | 6 | 6
| 63774 | EMAC | AC INDUCTION ELECTRIC MOTOR |  |  | 373 | 373
FA_EECMS | 63773 | EMAC | AC SYNCHRONOUS ELECTRIC MOTOR | 1 |  |  | 1
FA_EECO | 1664 | SKEL | ELECTRIC SOCKET OUTLET |  |  | 18 | 18
FA_EEPBA | 63762 | ESCB | AIR CIRCUIT BREAKER |  |  | 868 | 868
FA_EEPBV | 1336 | VACB | VACUUM CIRCUIT BREAKER |  | 47 |  | 47
FA_EEPCS | 1331 | CAAN | SACRIFICIAL ANODE |  |  | 5 | 5
FA_EEPNE | 1383 | EBEL | EARTHING BAR |  |  | 118 | 118
FA_EEPNN | 1394 | EREL | NEUTRAL GROUND RESISTOR |  | 8 |  | 8
FA_EEPS | 63765 | SWSS | START / STOP SWITCH |  | 171 |  | 171
FA_EEPU | 1721 | UPUB | UNINTERRUPTIBLE POWER SUPPLY | 4 |  |  | 4
FA_EETB | 1322 | BAEL | BATTERY | 12 |  |  | 12
|  |  | (blank) | 1 |  |  | 1
| 1721 | UPUB | UNINTERRUPTIBLE POWER SUPPLY | 2 |  |  | 2
FA_EETC | 1325 | BCEL | BATTERY CHARGER | 4 |  |  | 4
FA_EETD | 1324 | BBEL | BUS DUCT / BUS BAR |  |  | 70 | 70
FA_EETFW | 63771 | PTOT | WET TRANSFORMER |  | 20 |  | 20
FA_EETGA | 1384 | (blank) | AC ELECTRIC GENERATOR |  | 10 |  | 10
FA_EETI | 1456 | ISEL | ELECTRIC ISOLATOR |  | 9 |  | 9
FA_EETM | 63767 | (blank) | MOTOR CONTROL CENTER |  |  | 910 | 910
FA_EETO | (blank) | (blank) | (blank) |  | 4 |  | 4
FA_EETP | 1380 | CPEL | ELECTRICAL PANEL |  | 3 |  | 3
FA_EETR | 1654 | RCEL | POWER RECTIFIER |  | 2 |  | 2
FA_EETW | 1660 | SG__ | SWITCHGEAR |  |  | 121 | 121
|  |  | (blank) |  |  | 19 | 19
FA_EETY | 1337 | (blank) | ELECTRIC CABLE |  |  | 28 | 28
FA_INAM | 1581 | PSFS | FLOW METER |  | 15 |  | 15
FA_INAP | (blank) | (blank) | (blank) |  | 10 |  | 10
FA_INDC | 63784 | CLCP | LOCAL CONTROLLER |  | 8 |  | 8
FA_INDFD | 1372 | DAWD | DAMPER | 20 |  |  | 20
FA_INDFS | 1740 | VCSO | SOLENOID VALVE |  | 204 |  | 204
FA_INDI | (blank) | (blank) | (blank) |  |  | 1249 | 1249
FA_INDMS | 1569 | PS__ | SENSING ELEMENT |  | 15 |  | 15
|  |  | (blank) |  | 39 |  | 39
|  | (blank) | SENSING ELEMENT |  | 1324 |  | 1324
| 1905 | PSTT | TRANSMITTER - TEMPERATURE (RESISTIVE TEMPERATURE DEVICE TYPE) |  | 8 |  | 8
FA_INDMT | 1720 | PSTW | THERMOWELL |  | 1 |  | 1
| 1905 | DEVD | VIB VIBRATION TRANSMITTER |  | 190 |  | 190
|  | PSFT | Transmitter - Flow (Coriolis type) |  | 22 |  | 22
|  |  | Transmitter - Flow (Orifice Plate type) |  | 5 |  | 5
|  |  | Transmitter - Flow (Turbine type) |  | 1 |  | 1
|  |  | Transmitter - Flow (Ultrasonic type) |  | 10 |  | 10
|  |  | Transmitter - Flow (Vortex type) |  | 36 |  | 36
|  |  | (blank) |  | 165 |  | 165
|  | PSLT | Transmitter - Level (Displacer type) |  | 6 |  | 6
|  |  | Transmitter - Level (Guided Wave Radar type) |  | 148 |  | 148
|  |  | Transmitter - Level (Nucleonic type) |  | 10 |  | 10
|  |  | (blank) |  | 203 |  | 203
|  | PSPT | TRANSMITTER - PRESSURE (DIFFERENTIAL PRESSURE TYPE) |  | 138 |  | 138
|  |  | (blank) |  | 18 |  | 18
|  | PSTT | TRANSMITTER - TEMPERATURE (RESISTIVE TEMPERATURE DEVICE TYPE) |  | 466 |  | 466
|  |  | (blank) |  | 68 |  | 68
|  | TXGA | TRANSMITTER |  | 920 |  | 920
|  |  | (blank) |  | 2 |  | 2
| (blank) | (blank) | (blank) |  | 1 |  | 1
FA_INDS | 41348 | PSHS | INSTRUMENT SWITCH (HAND OPERATED) |  |  | 400 | 400
|  | PSSG | INSTRUMENT SWITCH |  |  | 648 | 648
FA_INDT | 1370 | (blank) | TRANSDUCER |  | 33 |  | 33
FA_INSC | 1351 | CLLC | PLC PANEL |  | 7 |  | 7
|  |  | Progammable Logic Controller |  | 1 |  | 1
FA_INSJ | 1459 | JBGE | JUNCTION BOX | 734 |  |  | 734
FA_INSL | 63786 | CLCP | LOCAL CONTROL PANEL |  |  | 206 | 206
FA_INSS | 63787 | (blank) | OPERATOR STATION |  | 3 |  | 3
FA_INSY | 33425 | FGCP | Master Fire Panel Master Firel Panel | 19 |  |  | 19
FA_PEA | 70849 | VASA | PRESSURE REGULATOR |  |  | 11 | 11
|  |  | SELF-ACTUATING VALVE |  |  | 112 | 112
| (blank) | (blank) | (blank) |  |  | 2 | 2
FA_PEG | 1999 | PICA | PIPING |  |  | 5 | 5
| 2114 | PICA | PIPING |  |  | 11089 | 11089
|  |  | (blank) |  |  | 113 | 113
| (blank) | (blank) | (blank) |  |  | 17 | 17
FA_PEL | 71011 | PIPG | PIG LAUNCHER / RECEIVER | 2 |  |  | 2
FA_PEM | 2019 | DC | MANIFOLD |  | 111 |  | 111
|  |  | (blank) |  | 23 |  | 23
FA_PEO | 1657 | ROGN | RESTRICTIVE ORIFICE |  |  | 351 | 351
FA_PESC | 1735 | VASC | CONVENTIONAL PRESSURE SAFETY VALVE | 489 |  |  | 489
|  |  | Reg - High Serv Pressure Safety Valve - Reg - High Service | 12 |  |  | 12
|  |  | Reg - Low Serv Pressure Safety Valve - Reg - Low Service | 1 |  |  | 1
FA_PESR | 1326 | BDGN | RUPTURE DISC | 49 |  |  | 49
FA_PESV | 1742 | VASV | VACUUM RELIEF PRESSURE SAFETY VALVE | 15 |  |  | 15
FA_PET | 1720 | PSTW | THERMOWELL | 363 |  |  | 363
FA_PEVB | 1722 | VABA | BALL VALVE |  |  | 4906 | 4906
| 1729 | VAGA | GATE VALVE |  |  | 1 | 1
| 1731 | MAEL | MOV VALVE - MOV |  |  | 22 | 22
|  | VAXL | BDV VALVE - EMERGENCY SHUTDOWN |  |  | 38 | 38
|  | VCGN | CONTROL VALVE CONTROL - GENERAL |  |  | 568 | 568
FA_PEVC | 1724 | VACH | CHECK VALVE |  |  | 1013 | 1013
FA_PEVD | 1725 | VADI | DIAPHRAM VALVE |  |  | 3 | 3
FA_PEVG | 1722 | VABA | BALL VALVE |  |  | 4 | 4
| 1729 | VAGA | GATE VALVE |  |  | 2318 | 2318
| 1731 | MAEL | MOV VALVE - MOV |  |  | 3 | 3
|  | VCGN | CONTROL VALVE CONTROL - GENERAL |  |  | 6 | 6
FA_PEVL | 1730 | VAGL | GLOBE VALVE |  |  | 814 | 814
FA_PEVM | 1732 | VAMO | MULTIPLE ORIFICE VALVE |  | 9 |  | 9
FA_PEVN | 1723 | VABP | BUTTERFLY VALVE |  |  | 12 | 12
| 1733 | VANE | NEEDLE VALVE |  |  | 61 | 61
FA_PEVX | 109918 | (blank) | DIVERTER VALVE | 2 |  |  | 2
|  |  | (blank) | 2 |  |  | 2
FA_PEVY | 1723 | VABP | BUTTERFLY VALVE |  | 65 |  | 65
FA_REBC | 71013 | BL | CENTRIFUGAL BLOWER | 4 |  |  | 4
FA_REC | 1341 | CF | CENTRIFUGE |  | 4 |  | 4
FA_REDH | 1544 | MOHY | HYDRAULIC MOTOR |  | 6 |  | 6
FA_REDP | 1545 | MOPN | PNEUMATIC MOTOR |  | 11 |  | 11
FA_REEL | 1338 | CEDE | STANDBY ENGINE LIQUID FUEL COMBUSTION ENGINE - STANDBY | 4 |  |  | 4
FA_REFA | 1396 | FAAX | AXIAL FAN | 21 |  |  | 21
FA_REFC | 1397 | BL | CENTRIFUGAL FAN |  | 121 |  | 121
FA_REMC | 1358 | COCE | CENTRIFUGAL COMPRESSOR |  | 3 |  | 3
FA_REMR | 1360 | CORE | RECIPROCATING COMPRESSOR | 6 |  |  | 6
FA_REMT | 1361 | (blank) | ROTARY COMPRESSOR |  | 11 |  | 11
FA_RENG | 1427 | (blank) | GAS TURBINE | 6 |  |  | 6
|  |  | SOLAR GAS TURBINE | 2 |  |  | 2
FA_REPC | 1641 | PUCE | CENTRIFUGAL PUMP |  | 233 |  | 233
|  |  | FIREWATER CENTRIFUGAL PUMP - FIREWATER |  | 13 |  | 13
| 1644 | (blank) | POSITIVE DISPLACEMENT PUMP |  | 4 |  | 4
FA_REPD | 1644 | (blank) | POSITIVE DISPLACEMENT PUMP |  | 12 |  | 12
FA_RER | (blank) | (blank) | (blank) |  | 2 |  | 2
FA_RETP | (blank) | (blank) | (blank) |  | 5 |  | 5
FA_SEC | 1771 | VEHY | HYDROCYCLONE |  |  | 6 | 6
FA_SEFB | 33433 | FIGE | BASKET STRAINER FILTER |  |  | 275 | 275
FA_SEFE | 1410 | FS | ELEMENT FILTER |  |  | 186 | 186
FA_SEFS | 1414 | FS | SCREEN FILTER |  |  | 6 | 6
| 1757 | VECA | COALESCER FILTER |  |  | 12 | 12
FA_SEHF | 1432 | (blank) | FINNED COIL HEAT EXCHANGER |  | 65 |  | 65
FA_SEHS | 1436 | HES | SPIRAL HEAT EXCHANGER |  | 46 |  | 46
FA_SEHT | 1439 | HEST | SHELL & TUBE HEAT EXCHANGER |  | 39 |  | 39
|  |  | (blank) |  | 1 |  | 1
| 1450 | HBEH | ELECTRIC HEATER |  | 8 |  | 8
FA_SEL | 1467 | LCFA | LOSS CONTROL - FLAME ARRESTOR | 42 |  |  | 42
FA_SEM | 2058 | STFL | FLARE | 4 |  |  | 4
FA_SENF | 41394 | HBDF | FIRED HEATER FURNACE |  | 5 |  | 5
FA_SEPA | 1752 | VEAH | ACCUMULATOR | 62 |  |  | 62
FA_SEPC | 1773 | VEPC | CYLINDER |  |  | 41 | 41
|  |  | (blank) |  |  | 18 | 18
FA_SEPHC | 1772 | VEKO | CONDENSER |  | 2 |  | 2
FA_SEPHS | 1662 | VESE | SEPARATOR VESSEL |  |  | 157 | 157
FA_SES | 1762 | VEFP | PULSATION DAMPENER |  |  | 72 | 72
FA_SETAC | 1715 | TAFX | CONE ROOF ATMOSPHERIC TANK |  | 59 |  | 59
FA_SETAP | 41396 | VESU | PIT / SUMP |  | 38 |  | 38
FA_SETPC | 63830 | (blank) | CYLINDRICAL PRESSURE TANK | 11 |  |  | 11
FA_SEZ | 1663 | SIGN | SILENCER / MUFFLER |  |  | 62 | 62
|  |  | (blank) |  |  | 1 | 1
FA_SQFC | (blank) | (blank) | (blank) |  | 21 |  | 21
FA_SQFDF | 33419 | FGBF | FLAME DETECTORS (UR / IR / CCTV TYPES) | 367 |  |  | 367
|  | FGBH | HEAT DETECTOR | 8 |  |  | 8
FA_SQFDG | 1402 | FGAB | NO DEVICE FIRE AND GAS DETECTOR - HYDROCARBON | 18 |  |  | 18
|  | FGAS | FIXED GAS DETECTOR (ELECTROCHEMICAL H2S) | 17 |  |  | 17
|  | FGBH | FIXED GAS DETECTOR (POINT INFRARED) | 542 |  |  | 542
| (blank) | (blank) | (blank) | 51 |  |  | 51
FA_SQFDS | 33434 | DESM | SMOKE DETECTOR (HIGH SENSITIVITY) | 35 |  |  | 35
|  |  | SMOKE DETECTOR (OPTICAL) | 1 |  |  | 1
FA_SQFFD | 2054 | PUFF | FIREWATER DELUGE SYSTEM | 17 |  |  | 17
FA_SQFFH | 1477 | LCHR | FIRE HOSE | 3 |  |  | 3
FA_SQFFM | 1471 | LCFM | FIRE WATER/FOAM MONITOR | 19 |  |  | 19
FA_SQFFY | 1478 | LCHY | FIRE HYDRANT | 109 |  |  | 109
FA_SQFRA | 1488 | FGMA | MANUALLY ACTIVATED CALL POINTS | 175 |  |  | 175
FA_SQFRE | 1465 | LCSS | SAFETY SHOWER OR EYE BATH | 18 |  |  | 18
FA_SQMT | (blank) | (blank) | (blank) |  |  | 2 | 2
FA_SQTA | (blank) | (blank) | (blank) | 34 |  |  | 34
FA_SQTB | 1679 | CMBE | NON DIRECTIONAL BEACON | 97 |  |  | 97
FA_SQTE | 1697 | TCRA | TELECOMMUNICATION CABINET | 16 |  |  | 16
FA_SQTL | 1702 | TCSP | LOUDSPEAKER | 294 |  |  | 294
FA_SQTOF | 1685 | CMRC | MF HF RADIO MF HF - FIXED RADIO |  | 2 |  | 2
FA_SQTP | (blank) | (blank) | (blank) |  |  | 104 | 104
FA_SQTS | 1706 | TCTS | TELEPHONE SYSTEMS EQUIPMENT |  | 78 |  | 78
FA_SQTV | 1681 | TCCA | CCTV CAMERA UNIT |  |  | 101 | 101
FA_SQTW | 41448 | BICG | WIRELESS ACCESS / GATEWAY |  | 17 |  | 17
FA_SQTY | 33399 | (blank) | RECEIVER / TRANSMITTER | 4 |  |  | 4
FA_SYLH | (blank) | (blank) | (blank) |  |  | 313 | 313
FA_WEHY | (blank) | (blank) | (blank) |  |  | 2 | 2
Grand Total |  |  |  | 3726 | 5585 | 28352 | 37663

## Tables
Tables for input risks |  |  | Lookup table for determining which system to put the following locations into |  |  |  |  | Lookup table for defining MAH Barrier typical criticalities and used in data validation for ease / consistency of input. Table from BP Guide 100041 Rev B08. |  |  |  |  | Table used to remove Integrity Only codes from Maintenance scope - source P Powney email 17 Oct 2017 'Failure Class coding for WND Maintenance Build' |  |  |  | Table used to identify tags with a shutdown function, derived from Engineering Numbering Specification
Impact Codes | Likelihood Values | ValidRisks | FA_SYLH not in a System Special Case Handling |  |  | Use system | Lookup check | Combined_for_data_validation | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Failure Code ID | Description | Split | PP Discipline | Tag Abbreviation | Tag Abb Description
A | 1 | Not Assessed | R-SYSTEM-00-NV | GIZA FAYOUM SYSTEM 00 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P2 ¦ Structural Integrity ¦ Primary Structures - All Components | P2 | Structural Integrity | Primary Structures - All Components | A | FA_CFBC | CONTROL ROOM | I | STRU | LZT | LEVEL TRANSMITTER (SIS)
B | 2 | E3 | R-SYSTEM-05-NV | GIZA FAYOUM SYSTEM 05 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P2 ¦ Structural Integrity ¦ Secondary Structures - Single component failure results in hydrocarbon LOPC | P2 | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | FA_CFBE | ELECTRICAL SUBSTATION | I | STRU | PZT | PRESSURE - TRANSMITTER (SIS)
C | 3 | E4 | R-SYSTEM-13-NV | GIZA FAYOUM SYSTEM 13 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P2B ¦ Structural Integrity ¦ Secondary Structures - Single component failure results in object dropping >3m | P2B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | FA_CFBI | INSTRUMENT HOUSE | I | STRU | XZV | MISCELLANEOUS - ON/OFF VALVE (SIS)
D | 4 | E5 | R-SYSTEM-20-NV | GIZA FAYOUM SYSTEM 20 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P2 ¦ Structural Integrity ¦ Secondary Structures - Single component failure has no immediate consequence | P2 | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | FA_CFBL | LIVING ACCOMMODATION | I | STRU | MPZS | PUMP MOTOR - SIS STOP ORDER
E | 5 | E6 | R-SYSTEM-21-NV | GIZA FAYOUM SYSTEM 21 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P2 ¦ Structural Integrity ¦ Tertiary Structures - Failure may result in fall >3m | P2 | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | FA_CFBO | OFFICE BUILDING | I | STRU | TZE | TEMPERATURE - SENSING ELEMENT (SIS)
F | 6 | E7 | R-SYSTEM-22-NV | GIZA FAYOUM SYSTEM 22 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P2 ¦ Structural Integrity ¦ Tertiary Structures - Failure may result in fall 1 - 3m | P2 | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | FA_CFDL | LAGOON | I | STRU | TZT | TEMPERATURE - TRANSMITTER (SIS)
G | 7 | F3 | R-SYSTEM-23-NV | GIZA FAYOUM SYSTEM 23 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P2 ¦ Structural Integrity ¦ Tertiary Structures - Failure may result in fall <1m | P2 | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | FA_CFDO | OUTFALL | I | STRU | TZW | TEMPERATURE - WELL (SIS)
H | 8 | F4 | R-SYSTEM-24-NV | GIZA FAYOUM SYSTEM 24 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P3 ¦ Stability loading control & watertight integrity ¦ Ballast Pumps | P3 | Stability loading control & watertight integrity | Ballast Pumps | A | FA_CFSGA | ACCESS CONTROL GATE | I | STRU | PZI | PRESSURE - INDICATOR (SIS)
|  | F5 | R-SYSTEM-25-NV | GIZA FAYOUM SYSTEM 25 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P3 ¦ Stability loading control & watertight integrity ¦ Sea Chest Valves | P3 | Stability loading control & watertight integrity | Sea Chest Valves | A | FA_CFSGB | BRIDGE | I | STRU | TZI | TEMPERATURE - INDICATOR (SIS)
|  | F6 | R-SYSTEM-27-NV | GIZA FAYOUM SYSTEM 27 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P3 ¦ Stability loading control & watertight integrity ¦ Loading Computer | P3 | Stability loading control & watertight integrity | Loading Computer | A | FA_CFSGC | CONTAINMENT | I | STRU | LZI | LEVEL INDICATOR (SIS)
|  | F7 | R-SYSTEM-28-NV | GIZA FAYOUM SYSTEM 28 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P3 ¦ Stability loading control & watertight integrity ¦ Tank/Draft Monitoring systems | P3 | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | FA_CFSGP | PARKING LOT | I | STRU | XZY | MISCELLANEOUS - ON/OFF VALVE (SIS) SIGNAL CONVERTOR OR SOLENOID OR POSITIONER
|  | G3 | R-SYSTEM-29-NV | GIZA FAYOUM SYSTEM 29 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P3 ¦ Stability loading control & watertight integrity ¦ Ballast/Cargo/Slop tank Valve control monitoring system | P3 | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | FA_CFSGR | ROAD | I | STRU | XZVS | MISCELLANEOUS - ON/OFF VALVE (SIS) COMPOSITE POINT
|  | G4 | R-SYSTEM-30-NV | GIZA FAYOUM SYSTEM 30 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P3 ¦ Stability loading control & watertight integrity ¦ Bilge System Alarms CCR | P3 | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | FA_CFSGS | STORAGE YARD | I | STRU | HZS | HAND (MANUAL) - SWITCH (SIS)
|  | G5 | R-SYSTEM-40-NV | GIZA FAYOUM SYSTEM 40 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P3 ¦ Stability loading control & watertight integrity ¦ Ballast Pump Hydraulic Power | P3 | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | FA_CFSGW | WALL OR FENCE | I | STRU | XZZSC | MISCELLANEOUS - ON/OFF VALVE (SIS) CLOSED LIMIT SWITCH
|  | G6 | R-SYSTEM-41-NV | GIZA FAYOUM SYSTEM 41 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P3 ¦ Stability loading control & watertight integrity ¦ Down-flooding Points | P3 | Stability loading control & watertight integrity | Down-flooding Points | A | FA_CFSGT | WASTE STORAGE | I | STRU | BDZV | VALVE - BLOW DOWN (SIS)
|  | G7 | R-SYSTEM-42-NV | GIZA FAYOUM SYSTEM 42 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P3 ¦ Stability loading control & watertight integrity ¦ Tank Hatches | P3 | Stability loading control & watertight integrity | Tank Hatches | B | FA_CFSPW | FIRE / BLAST WALL | I | STRU | PZZSC | PRESSURE - CONTROL VALVE CLOSED LIMIT SWITCH (SIS)
|  | H3 | R-SYSTEM-43-NV | GIZA FAYOUM SYSTEM 43 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P3 ¦ Stability loading control & watertight integrity ¦ Cargo transfer/loading system | P3 | Stability loading control & watertight integrity | Cargo transfer/loading system | A | FA_CFSPD | FIRE DOOR | M | MECH | FZI | FLOW - INDICATOR (SIS)
|  | H4 | R-SYSTEM-44-NV | GIZA FAYOUM SYSTEM 44 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P3 ¦ Station Keeping ¦ Chain Stoppers | P3 | Station Keeping | Chain Stoppers | A | FA_CFSSA | ANCHOR | I | STRU | FZZSC | FLOW - CONTROL VALVE CLOSED LIMIT SWITCH (SIS)
|  | H5 | R-SYSTEM-45-NV | GIZA FAYOUM SYSTEM 45 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P3 ¦ Station Keeping ¦ Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | P3 | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | FA_CFSSD | DERRICK OR FRAME | I | STRU | ZZSC | POSITION / DIMENSION - SWITCH (CLOSED) (SIS)
|  | H6 | R-SYSTEM-46-NV | GIZA FAYOUM SYSTEM 46 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P3 ¦ Station Keeping ¦ Suction Piles | P3 | Station Keeping | Suction Piles | A | FA_CFSSE | EQUIPMENT SUPPORT STRUCTURE | I | STRU | XZZSO | MISCELLANEOUS - ON/OFF VALVE (SIS) OPEN LIMIT SWITCH
|  | H7 | R-SYSTEM-47-NV | GIZA FAYOUM SYSTEM 47 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P3 ¦ Swivel Stack Assembly ¦ Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | P3 | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | FA_CFSSP | PEDESTAL | I | STRU | BDZVS | VALVE - BLOW DOWN, COMPOSITE POINT (SIS)
|  |  | R-SYSTEM-48-NV | GIZA FAYOUM SYSTEM 48 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P3 ¦ Swivel Stack Assembly ¦ Swivel Seals (Primary and Secondary Seals) | P3 | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | FA_CFSSI | PILE | I | STRU | TZZSC | TEMPERATURE - CONTROL VALVE CLOSED LIMIT SWITCH (SIS)
|  |  | R-SYSTEM-49-NV | GIZA FAYOUM SYSTEM 49 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P3 ¦ Swivel Stack Assembly ¦ Fibre Optic Ring Joint | P3 | Swivel Stack Assembly | Fibre Optic Ring Joint | A | FA_CFSSS | STABILISATION OR GUIDANCE EQUIPMENT | I | STRU | FZT | FLOW - TRANSMITTER (SIS)
|  |  | R-SYSTEM-50-NV | GIZA FAYOUM SYSTEM 50 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P3 ¦ Swivel Fluid Barrier System ¦ HPU Reservoir | P3 | Swivel Fluid Barrier System | HPU Reservoir | A | FA_CFSST | STRUCTURAL BASE | I | STRU | SZI | SPEED - INDICATOR (SIS)
|  |  | R-SYSTEM-51-NV | GIZA FAYOUM SYSTEM 51 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P3 ¦ Swivel Fluid Barrier System ¦ HPU Pumps, filters and automatic controls | P3 | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | FA_CFSSF | STRUCTURAL FOUNDATION | I | STRU | PZY | PRESSURE - SIGNAL CONVERTOR OR POSITIONER OR SOLENOID (SIS)
|  |  | R-SYSTEM-52-NV | GIZA FAYOUM SYSTEM 52 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P3 ¦ Swivel Fluid Barrier System ¦ N2 hydraulic Accumulators | P3 | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | FA_EEPCI | IMPRESSED CURRENT CATHODE | B | ELEC | BDZY | VALVE - BLOW DOWN SIGNAL CONVERTOR OR POSITIONER OR SOLENOID (SIS)
|  |  | R-SYSTEM-53-NV | GIZA FAYOUM SYSTEM 53 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P3 ¦ Swivel/Turret Pipework ¦ Hard piping, PSVs, Valves, etc. | P3 | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | FA_EEPCS | SACRIFICIAL ANODE | B | ELEC | FZE | FLOW ELEMENT (SIS)
|  |  | R-SYSTEM-54-NV | GIZA FAYOUM SYSTEM 54 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P3 ¦ Swivel/Turret Pipework ¦ Flexible Hoses Required | P3 | Swivel/Turret Pipework | Flexible Hoses Required | A | FA_EEPBA | AIR CIRCUIT BREAKER | M | ELEC | ZZSO | POSITION / DIMENSION - SWITCH (OPEN) (SIS)
|  |  | R-SYSTEM-55-NV | GIZA FAYOUM SYSTEM 55 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P3 ¦ Turret Chain Table ¦ Anchor Mooring Leg | P3 | Turret Chain Table | Anchor Mooring Leg | A | FA_EEPBG | GAS CIRCUIT BREAKER | M | ELEC | FZY | FLOW - SIGNAL CONVERTOR OR POSITIONER OR SOLENOID (SIS)
|  |  | R-SYSTEM-56-NV | GIZA FAYOUM SYSTEM 56 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P3 ¦ Turret Chain Table ¦ Riser/Umbilical Installation and Maintenance System | P3 | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | FA_EEPBL | LIQUID CIRCUIT BREAKER | M | ELEC | XZL | MISCELLANEOUS - LAMP (SIS)
|  |  | R-SYSTEM-57-NV | GIZA FAYOUM SYSTEM 57 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P3 ¦ Turret Chain Table ¦ (hydraulic winch, wire rope, and HPU) | P3 | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | FA_EEPBV | VACUUM CIRCUIT BREAKER | M | ELEC | PZAHH | PRESSURE - ALARM HIGH HIGH (SIS)
|  |  | R-SYSTEM-58-NV | GIZA FAYOUM SYSTEM 58 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P3 ¦ Turret Chain Table ¦ Adjusting Mooring Chain Tension | P3 | Turret Chain Table | Adjusting Mooring Chain Tension | A | FA_EEPE | ELECTRICAL DISCONNECT SWITCH | M | ELEC | PZALL | PRESSURE - ALARM LOW LOW (SIS)
|  |  | R-SYSTEM-59-NV | GIZA FAYOUM SYSTEM 59 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P3 ¦ Main Turret Bearing ¦ Grease Lubrication System (grease pump, | P3 | Main Turret Bearing | Grease Lubrication System (grease pump, | A | FA_EEPNE | EARTHING BAR | M | ELEC | DZS | CONFIRMED FIRE (FGS OUTPUT TO SIS)
|  |  | R-SYSTEM-60-NV | GIZA FAYOUM SYSTEM 60 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P3 ¦ Main Turret Bearing ¦ metering valves, injector divider valves, etc.) | P3 | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | FA_EEPNN | NEUTRAL GROUND RESISTOR | M | ELEC | XZZLC | MISCELLANEOUS - ON/OFF VALVE (SIS) CLOSED LIMIT INDICATION
|  |  | R-SYSTEM-61-NV | GIZA FAYOUM SYSTEM 61 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P3 ¦ Main Turret Bearing ¦ Main Bearing, Cover, Bearing Studs etc. | P3 | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | FA_EEPP | PROTECTIVE RELAY | M | ELEC | VZT | VIBRATION / MACHINERY ANALYSIS - TRANSMITTER (SIS)
|  |  | R-SYSTEM-62-NV | GIZA FAYOUM SYSTEM 62 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Wellhead integrity ¦ Annulus Swab | P4 | Wellhead integrity | Annulus Swab | B | FA_EEPS | START / STOP SWITCH | M | ELEC | XZZLO | MISCELLANEOUS - ON/OFF VALVE (SIS) OPEN LIMIT INDICATION
|  |  | R-SYSTEM-63-NV | GIZA FAYOUM SYSTEM 63 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Wellhead integrity ¦ Annulus Master | P4 | Wellhead integrity | Annulus Master | B | FA_EEPA | SURGE ARRESTOR | M | ELEC | DZSHH | CONFIRMED HIGH HIGH GAS (FGS OUTPUT TO SIS)
|  |  | R-SYSTEM-64-NV | GIZA FAYOUM SYSTEM 64 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Wellhead integrity ¦ Crossover | P4 | Wellhead integrity | Crossover | B | FA_EEPU | UNINTERRUPTIBLE POWER SUPPLY | M | ELEC | MOVZSO | VALVE - MOTOR OPERATED OPEN LIMIT SWITCH (SIS)
|  |  | R-SYSTEM-65-NV | GIZA FAYOUM SYSTEM 65 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Wellhead integrity ¦ Production Swab | P4 | Wellhead integrity | Production Swab | B | FA_EETB | BATTERY | M | ELEC | VZI | VIBRATION / MACHINERY ANALYSIS - INDICATOR (SIS)
|  |  | R-SYSTEM-66-NV | GIZA FAYOUM SYSTEM 66 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Wellhead integrity ¦ Production Master | P4 | Wellhead integrity | Production Master | B | FA_EETC | BATTERY CHARGER | M | ELEC | TZY | TEMPERATURE - SIGNAL CONVERTOR OR POSITIONER OR SOLENOID (SIS)
|  |  | R-SYSTEM-81-NV | GIZA FAYOUM SYSTEM 81 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Wellhead integrity ¦ Production Wing | P4 | Wellhead integrity | Production Wing | B | FA_EETD | BUS DUCT / BUS BAR | M | ELEC | TZAHH | TEMPERATURE - ALARM HIGH HIGH (SIS)
|  |  | R-SYSTEM-82-NV | GIZA FAYOUM SYSTEM 82 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Wellhead integrity ¦ SCSSV | P4 | Wellhead integrity | SCSSV | A | FA_EETGA | AC ELECTRIC GENERATOR | M | ELEC | ZJB | JUNCTION BOX - SAFETY INSTRUMENTED SYSTEM
|  |  | R-SYSTEM-83-NV | GIZA FAYOUM SYSTEM 83 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Production Tree | P4 | Subsea Integrity | Production Tree | A | FA_EETGD | DC ELECTRIC GENERATOR | M | ELEC | LZE | LEVEL - PRIMARY ELEMENT OR RADIOACTIVE SOURCE (SIS)
|  |  | R-SYSTEM-84-NV | GIZA FAYOUM SYSTEM 84 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Gas Injection Tree | P4 | Subsea Integrity | Gas Injection Tree | A | FA_EETI | ELECTRIC ISOLATOR | M | ELEC | BDZVI | BLOWDOWN VALVE TRIPPED BY SIS FLAG
|  |  | R-SYSTEM-85-NV | GIZA FAYOUM SYSTEM 85 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Water Injection Tree | P4 | Subsea Integrity | Water Injection Tree | A | FA_EETT | ELECTRICAL CAPACITOR | M | ELEC | ZZT | POSITION / DIMENSION / MACHINERY ANALYSIS - TRANSMITTER (SIS)
|  |  | R-SYSTEM-86-NV | GIZA FAYOUM SYSTEM 86 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Process Gas Pipeline | P4 | Subsea Integrity | Process Gas Pipeline | A | FA_EETP | ELECTRICAL PANEL | M | ELEC | PZAL | PRESSURE - ALARM LOW (SIS)
|  |  | R-SYSTEM-87-NV | GIZA FAYOUM SYSTEM 87 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Oil Production Pipeline | P4 | Subsea Integrity | Oil Production Pipeline | A | FA_EETS | ELECTRICAL TRANSFER SWITCH | M | ELEC | MOVZLC | VALVE - MOTOR OPERATED CLOSED LIMIT INDICATION (SIS)
|  |  | R-SYSTEM-88-NV | GIZA FAYOUM SYSTEM 88 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Water Injection Pipeline | P4 | Subsea Integrity | Water Injection Pipeline | B | FA_EETM | MOTOR CONTROL CENTER | M | ELEC | FZALL | FLOW - ALARM LOW LOW (SIS)
|  |  | R-SYSTEM-89-NV | GIZA FAYOUM SYSTEM 89 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Pig Launcher / Receiver | P4 | Subsea Integrity | Subsea Pig Launcher / Receiver | A | FA_EETO | POWER / CONTROL MODULE | M | ELEC | MOVZLO | VALVE - MOTOR OPERATED OPEN LIMIT INDICATION (SIS)
|  |  | R-SYSTEM-90-NV | GIZA FAYOUM SYSTEM 90 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Anchor Pile | P4 | Subsea Integrity | Subsea Anchor Pile | A | FA_EETV | POWER INVERTER | M | ELEC | MOVZSC | VALVE - MOTOR OPERATED CLOSED LIMIT SWITCH (SIS)
|  |  | R-SYSTEM-91-NV | GIZA FAYOUM SYSTEM 91 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Buoyancy Tank | P4 | Subsea Integrity | Subsea Buoyancy Tank | A | FA_EETR | POWER RECTIFIER | M | ELEC | XZVI | ON/OFF VALVE TRIPPED BY SIS FLAG
|  |  | R-SYSTEM-92-NV | GIZA FAYOUM SYSTEM 92 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Pipeline Crossing Support | P4 | Subsea Integrity | Subsea Pipeline Crossing Support | B | FA_EETY | POWER SUPPLY | M | ELEC | PDZT | PRESSURE DIFFERENTIAL - TRANSMITTER (SIS)
|  |  | R-SYSTEM-93-NV | GIZA FAYOUM SYSTEM 93 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Electrical Flying Lead | P4 | Subsea Integrity | Subsea Electrical Flying Lead | B | FA_EETA | REACTOR / INDUCTOR | M | ELEC | PDZI | PRESSURE DIFFERENTIAL - INDICATOR (SIS)
|  |  | R-SYSTEM-94-NV | GIZA FAYOUM SYSTEM 94 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Electrical Junction Box | P4 | Subsea Integrity | Subsea Electrical Junction Box | B | FA_EETH | ELECTRICAL SLIP RING | M | ELEC | XZSC | MISCELLANEOUS - ON/OFF VALVE, CLOSED LIMIT SWITCH
|  |  | R-SYSTEM-95-NV | GIZA FAYOUM SYSTEM 95 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Extension Umbilical | P4 | Subsea Integrity | Subsea Extension Umbilical | B | FA_EETL | SOLAR PANEL | M | ELEC | XZSO | MISCELLANEOUS - ON/OFF VALVE, OPEN LIMIT SWITCH
|  |  | R-SYSTEM-96-NV | GIZA FAYOUM SYSTEM 96 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Flowline Buckle Initiator | P4 | Subsea Integrity | Subsea Flowline Buckle Initiator | B | FA_EETW | SWITCHGEAR | M | ELEC | XZS | MISCELLANEOUS - SWITCH (SIS)
|  |  | R-SYSTEM-97-NV | GIZA FAYOUM SYSTEM 97 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Flowline Holdback Pile | P4 | Subsea Integrity | Subsea Flowline Holdback Pile | A | FA_EETFD | DRY TRANSFORMER | M | ELEC | EEHZS | ELECTRIC HEATER - SIS STOP ORDER
|  |  | R-SYSTEM-98-NV | GIZA FAYOUM SYSTEM 98 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Production Flexible Riser | P4 | Subsea Integrity | Subsea Production Flexible Riser | A | FA_EETFE | ENCAPSULATED TRANSFORMER | M | ELEC | SZT | SPEED - TRANSMITTER (SIS)
|  |  | R-SYSTEM-99-NV | GIZA FAYOUM SYSTEM 99 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Gas Injection Flexible Riser | P4 | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | FA_EETFW | WET TRANSFORMER | M | ELEC | VZSHH | VIBRATION / MACHINERY ANALYSIS - SWITCH HIGH HIGH (SIS)
|  |  | R-SYSTEM-67-NV | GIZA FAYOUM SYSTEM 67 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Water Injection Flexible Riser | P4 | Subsea Integrity | Subsea Water Injection Flexible Riser | A | FA_EETQ | VARIABLE FREQUENCY DRIVE | M | ELEC | VZSH | VIBRATION / MACHINERY ANALYSIS - SWITCH HIGH (SIS)
|  |  | R-SYSTEM-76-NV | GIZA FAYOUM SYSTEM 76 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Service Flexible Riser | P4 | Subsea Integrity | Subsea Service Flexible Riser | A | FA_EEHC | AIR CONDITIONING UNIT | M | HVAC | SZY | SPEED - SIGNAL CONVERTOR (SIS)
|  |  | R-SYSTEM-77-NV | GIZA FAYOUM SYSTEM 77 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Gas Injection Flexible Spur | P4 | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | FA_EEHH | AIR HANDLING UNIT | M | HVAC | VZSS | VIBRATION TRANSMITTER START-UP OVERRIDE APPLY/REMOVE (SET)
|  |  | R-SYSTEM-78-NV | GIZA FAYOUM SYSTEM 78 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Water Injection Flexible Spur | P4 | Subsea Integrity | Subsea Water Injection Flexible Spur | B | FA_EEHV | CONSTANT VOLUME UNIT | M | HVAC | VZY | VIBRATION / MACHINERY ANALYSIS - SIGNAL CONVERTOR (SIS)
|  |  | R-SYSTEM-79-NV | GIZA FAYOUM SYSTEM 79 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Production Flowline Termination Assembly | P4 | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | FA_EECH | ELECTRIC HEATER | M | ELEC | VZE | VIBRATION / MACHINERY ANALYSIS - PRIMARY ELEMENT (SIS)
|  |  | R-SYSTEM-80-NV | GIZA FAYOUM SYSTEM 80 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Gas Injection Flowline Termination Assembly | P4 | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | FA_EECMI | AC INDUCTION ELECTRIC MOTOR | M | ELEC | HZA | HAND (MANUAL) - ALARM (SIS)
|  |  | E-SYSTEM-00-NV | RAVEN SYSTEM 00 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Water Injection Flowline Termination Assembly | P4 | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | FA_EECMS | AC SYNCHRONOUS ELECTRIC MOTOR | M | ELEC | MCEXC | CENTRIFUGE MOTOR - MISC SWITCHGEAR STATUS (E.G. SIS STOP LATCHED)
|  |  | E-SYSTEM-05-NV | RAVEN SYSTEM 05 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Service Flowline Termination Assembly | P4 | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | FA_EECMD | DC ELECTRIC MOTOR | M | ELEC | XZA | MISCELLANEOUS - ALARM (SIS)
|  |  | E-SYSTEM-13-NV | RAVEN SYSTEM 13 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Riser Gas Lift Module | P4 | Subsea Integrity | Subsea Riser Gas Lift Module | A | FA_EECO | ELECTRIC SOCKET OUTLET | M | ELEC | BDZZSC | VALVE - BLOW DOWN CLOSED LIMIT SWITCH (SIS)
|  |  | E-SYSTEM-20-NV | RAVEN SYSTEM 20 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Distribution (Hydraulic Control) Unit | P4 | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | FA_EECF | LIGHT FITTING | M | ELEC | BDZZSO | VALVE - BLOW DOWN OPEN LIMIT SWITCH (SIS)
|  |  | E-SYSTEM-21-NV | RAVEN SYSTEM 21 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Hydraulic/Chemical Flying Lead | P4 | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | FA_EECT | TRACE HEATING CIRCUIT | M | ELEC | MPXC | PUMP MOTOR - MISC SWITCHGEAR STATUS (E.G. SIS STOP LATCHED)
|  |  | E-SYSTEM-22-NV | RAVEN SYSTEM 22 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Main Umbilical | P4 | Subsea Integrity | Subsea Main Umbilical | B | FA_INAA | GAS ANALYSER | M | INST | MKEZS | FAN MOTOR - SIS STOP ORDER
|  |  | E-SYSTEM-23-NV | RAVEN SYSTEM 23 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Hydraulic Power Unit | P4 | Subsea Integrity | Subsea Hydraulic Power Unit | A | FA_INAC | GAS CHROMATOGRAPH | M | INST | MSEZS | SCREW ELEVATOR MOTOR - SIS STOP ORDER
|  |  | E-SYSTEM-24-NV | RAVEN SYSTEM 24 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Control Panel | P4 | Subsea Integrity | Subsea Control Panel | B | FA_INAL | LIQUID CHROMATOGRAPH | M | INST
|  |  | E-SYSTEM-25-NV | RAVEN SYSTEM 25 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Production Inline Tee Assembly | P4 | Subsea Integrity | Subsea Production Inline Tee Assembly | A | FA_INAS | LIQUID ANALYSER | M | INST
|  |  | E-SYSTEM-27-NV | RAVEN SYSTEM 27 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Gas Injection Inline Tee Assembly | P4 | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | FA_INDFA | ACTUATOR | M | INST
|  |  | E-SYSTEM-28-NV | RAVEN SYSTEM 28 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Water Injection Inline Tee Assembly | P4 | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | FA_INDFD | DAMPER | M | HVAC
|  |  | E-SYSTEM-29-NV | RAVEN SYSTEM 29 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Service Inline Tee Assembly | P4 | Subsea Integrity | Subsea Service Inline Tee Assembly | B | FA_INDFS | SOLENOID VALVE | M | INST
|  |  | E-SYSTEM-30-NV | RAVEN SYSTEM 30 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Infield Umbilical | P4 | Subsea Integrity | Subsea Infield Umbilical | B | FA_INDI | INDICATOR | M | INST
|  |  | E-SYSTEM-40-NV | RAVEN SYSTEM 40 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Master Control System | P4 | Subsea Integrity | Subsea Master Control System | A | FA_INDS | INSTRUMENT SWITCH | M | INST
|  |  | E-SYSTEM-41-NV | RAVEN SYSTEM 41 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Multiphase Flowmeter | P4 | Subsea Integrity | Subsea Multiphase Flowmeter | B | FA_INDC | LOCAL CONTROLLER | M | INST
|  |  | E-SYSTEM-42-NV | RAVEN SYSTEM 42 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Manifold | P4 | Subsea Integrity | Subsea Manifold | A | FA_INDP | PRINTER / RECORDER | M | INST
|  |  | E-SYSTEM-43-NV | RAVEN SYSTEM 43 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Anchor Pile (Manifold Support Structure) | P4 | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | FA_INDT | TRANSDUCER | M | INST
|  |  | E-SYSTEM-44-NV | RAVEN SYSTEM 44 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Manifold Support Structure | P4 | Subsea Integrity | Subsea Manifold Support Structure | B | FA_INDMT | TRANSMITTER | M | INST
|  |  | E-SYSTEM-45-NV | RAVEN SYSTEM 45 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Riser Tower Monitoring System | P4 | Subsea Integrity | Subsea Riser Tower Monitoring System | B | FA_INDMS | SENSING ELEMENT | M | INST
|  |  | E-SYSTEM-46-NV | RAVEN SYSTEM 46 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Riser Tower | P4 | Subsea Integrity | Subsea Riser Tower | A | FA_INSP | CONDITION MONITORING SYSTEM PANEL | M | INST
|  |  | E-SYSTEM-47-NV | RAVEN SYSTEM 47 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Rigid Riser | P4 | Subsea Integrity | Subsea Rigid Riser | A | FA_INSD | DISTRIBUTED CONTROL PANEL | M | INST
|  |  | E-SYSTEM-48-NV | RAVEN SYSTEM 48 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Riser Base | P4 | Subsea Integrity | Subsea Riser Base | A | FA_INSJ | JUNCTION BOX | M | INST
|  |  | E-SYSTEM-49-NV | RAVEN SYSTEM 49 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Control Module | P4 | Subsea Integrity | Subsea Control Module | B | FA_INSL | LOCAL CONTROL PANEL | M | INST
|  |  | E-SYSTEM-50-NV | RAVEN SYSTEM 50 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Production Spool Piece | P4 | Subsea Integrity | Subsea Production Spool Piece | A | FA_INSM | METEOROLOGICAL SYSTEM PANEL | M | INST
|  |  | E-SYSTEM-51-NV | RAVEN SYSTEM 51 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Gas Injection Spool Piece | P4 | Subsea Integrity | Subsea Gas Injection Spool Piece | A | FA_INSS | OPERATOR STATION | M | INST
|  |  | E-SYSTEM-52-NV | RAVEN SYSTEM 52 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Water Injection Spool Piece | P4 | Subsea Integrity | Subsea Water Injection Spool Piece | B | FA_INSC | PLC PANEL | M | INST
|  |  | E-SYSTEM-53-NV | RAVEN SYSTEM 53 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Service Spool Piece | P4 | Subsea Integrity | Subsea Service Spool Piece | A | FA_INSY | SAFETY INSTRUMENT SYSTEM PANEL | M | INST
|  |  | E-SYSTEM-54-NV | RAVEN SYSTEM 54 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Umbilical | P4 | Subsea Integrity | Subsea Umbilical | B | FA_INST | TERMINATION RACK | M | INST
|  |  | E-SYSTEM-55-NV | RAVEN SYSTEM 55 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Subsea Integrity ¦ Subsea Production Tree Jumper | P4 | Subsea Integrity | Subsea Production Tree Jumper | B | FA_PEP | BLOWOUT PREVENTER | N | TBC
|  |  | E-SYSTEM-56-NV | RAVEN SYSTEM 56 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | P4.5 | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | FA_PEI | BUCKLE INITIATOR | N | TBC
|  |  | E-SYSTEM-57-NV | RAVEN SYSTEM 57 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | P4 | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | FA_PEH | BUNKERING HOSE | I | PIPE
|  |  | E-SYSTEM-58-NV | RAVEN SYSTEM 58 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework operating at temperature greater than 120o C | P4 | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | FA_PEB | BUOYANCY DEVICE | N | TBC
|  |  | E-SYSTEM-59-NV | RAVEN SYSTEM 59 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for highly toxic substances | P4 | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | FA_PED | DIVERTER | I | PIPE
|  |  | E-SYSTEM-60-NV | RAVEN SYSTEM 60 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework with corrosion resistant linings | P4 | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | FA_PEC | DUCT | M | HVAC
|  |  | E-SYSTEM-61-NV | RAVEN SYSTEM 61 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework associated with fire water delivery systems | P4 | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | FA_PEE | EXPANSION DEVICE | I | PIPE
|  |  | E-SYSTEM-62-NV | RAVEN SYSTEM 62 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Process Containment Integrity ¦ Bilge and ballast pipework | P4 | Process Containment Integrity | Bilge and ballast pipework | A | FA_PEM | MANIFOLD | I | PIPE
|  |  | E-SYSTEM-63-NV | RAVEN SYSTEM 63 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | P4 | Process Containment Integrity | All other pressure Equipment and pipework | C | FA_PEL | PIG LAUNCHER / RECEIVER | I | MECH
|  |  | E-SYSTEM-64-NV | RAVEN SYSTEM 64 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Process Containment Integrity ¦ Supports for criticality A pressure systems | P4 | Process Containment Integrity | Supports for criticality A pressure systems | A | FA_PEG | PIPING | I | PIPE
|  |  | E-SYSTEM-65-NV | RAVEN SYSTEM 65 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Process Containment Integrity ¦ Insulation installed on criticality A pressure systems | P4 | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | FA_PEO | RESTRICTIVE ORIFICE | I | INST
|  |  | E-SYSTEM-66-NV | RAVEN SYSTEM 66 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Process Containment Integrity ¦ Painting on criticality A pressure systems | P4 | Process Containment Integrity | Painting on criticality A pressure systems | A | FA_PER | RISER | N | TBC
|  |  | E-SYSTEM-81-NV | RAVEN SYSTEM 81 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Process Containment Integrity ¦ Bolting on criticality A pressure systems | P4 | Process Containment Integrity | Bolting on criticality A pressure systems | A | FA_PESC | CONVENTIONAL PRESSURE SAFETY VALVE | B | MECH
|  |  | E-SYSTEM-82-NV | RAVEN SYSTEM 82 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Process Containment Integrity ¦ All other supports, paint and bolting | P4 | Process Containment Integrity | All other supports, paint and bolting | C | FA_PESP | PILOT OPERATED PRESSURE SAFETY VALVE | B | MECH
|  |  | E-SYSTEM-83-NV | RAVEN SYSTEM 83 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Gas Generator | P4 | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | FA_PESR | RUPTURE DISC | B | MECH
|  |  | E-SYSTEM-84-NV | RAVEN SYSTEM 84 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Alternators | P4 | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | FA_PESV | VACUUM RELIEF PRESSURE SAFETY VALVE | B | MECH
|  |  | E-SYSTEM-85-NV | RAVEN SYSTEM 85 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Power Turbine | P4 | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | FA_PEA | SELF-ACTUATING VALVE | M | INST
|  |  | E-SYSTEM-86-NV | RAVEN SYSTEM 86 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ All Casing joints, fittings and seals | P4 | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | FA_PEW | SWIVEL | N | TBC
|  |  | E-SYSTEM-87-NV | RAVEN SYSTEM 87 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ All Shaft Seals | P4 | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | FA_PET | THERMOWELL | I | INST
|  |  | E-SYSTEM-88-NV | RAVEN SYSTEM 88 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ All coupling members | P4 | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | FA_PEZ | TUBING HANGER | N | TBC
|  |  | E-SYSTEM-89-NV | RAVEN SYSTEM 89 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Pressurized Enclosures | P4 | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | FA_PEQ | TURRET EQUIPMENT | N | TBC
|  |  | E-SYSTEM-90-NV | RAVEN SYSTEM 90 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Fire & Gas System | P4 | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | FA_PEU | UMBILICAL | B | PIPE
|  |  | E-SYSTEM-91-NV | RAVEN SYSTEM 91 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ All Shaft Seals System Ancillaries | P4 | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | FA_PEVB | BALL VALVE | M | MECH
|  |  | E-SYSTEM-92-NV | RAVEN SYSTEM 92 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | P4 | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | FA_PEVY | BUTTERFLY VALVE | M | MECH
|  |  | E-SYSTEM-93-NV | RAVEN SYSTEM 93 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | P4 | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | FA_PEVC | CHECK VALVE | M | MECH
|  |  | E-SYSTEM-94-NV | RAVEN SYSTEM 94 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Auxiliaries like (cleaning system, control system, utilities) | P4 | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | FA_PEVD | DIAPHRAGM VALVE | M | MECH
|  |  | E-SYSTEM-95-NV | RAVEN SYSTEM 95 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | P4 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | FA_PEVG | GATE VALVE | M | MECH
|  |  | E-SYSTEM-96-NV | RAVEN SYSTEM 96 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | P4 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | FA_PEVL | GLOBE VALVE | M | MECH
|  |  | E-SYSTEM-97-NV | RAVEN SYSTEM 97 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Diesel Driven Packages ¦ Diesel Engine | P4 | Diesel Driven Packages | Diesel Engine | B | FA_PEVM | MULTIPLE ORIFICE VALVE | M | MECH
|  |  | E-SYSTEM-98-NV | RAVEN SYSTEM 98 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Diesel Driven Packages ¦ Alternators | P4 | Diesel Driven Packages | Alternators | B | FA_PEVN | NEEDLE VALVE | M | MECH
|  |  | E-SYSTEM-99-NV | RAVEN SYSTEM 99 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Diesel Driven Packages ¦ All Fuel system Joints, Fittings and Seals | P4 | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | FA_PEVS | SUBSURFACE SAFETY VALVE | N | TBC
|  |  | E-SYSTEM-67-NV | RAVEN SYSTEM 67 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Diesel Driven Packages ¦ All coupling members | P4 | Diesel Driven Packages | All coupling members | B | FA_PEVH | SHEAR VALVE | M | MECH
|  |  | E-SYSTEM-76-NV | RAVEN SYSTEM 76 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Diesel Driven Packages ¦ All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | P4 | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | FA_PEX | X-MAS TREE / WELLHEAD | N | TBC
|  |  | E-SYSTEM-77-NV | RAVEN SYSTEM 77 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Diesel Driven Packages ¦ All other Systems (governor, control, utilities, etc.) | P4 | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | FA_REBC | BLOWER, CENTRIFUGAL | M | MECH
|  |  | E-SYSTEM-78-NV | RAVEN SYSTEM 78 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Oil Storage & Offloading ¦ Export Booster Pumps | P4 | Oil Storage & Offloading | Export Booster Pumps | A | FA_REBR | ROTARY LOBE BLOWER | M | MECH
|  |  | E-SYSTEM-79-NV | RAVEN SYSTEM 79 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Oil Storage & Offloading ¦ Export Hose | P4 | Oil Storage & Offloading | Export Hose | A | FA_REC | CENTRIFUGE | M | MECH
|  |  | E-SYSTEM-80-NV | RAVEN SYSTEM 80 NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Oil Storage & Offloading ¦ Marine Growth Prevention Equipment | P4 | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | FA_REEG | GAS FUEL COMBUSTION ENGINE | M | MECH
|  |  | E-NOPARENT | NO PARENT OR SYSTEM IDENTIFIED | FA_SYLH | N/A | N/A | P4 ¦ Oil Storage & Offloading ¦ Cargo Tank Cleaning Systems | P4 | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | FA_REEL | LIQUID FUEL COMBUSTION ENGINE | M | MECH
|  |  | R-NOPARENT | NO PARENT OR SYSTEM IDENTIFIED | FA_SYLH | N/A | N/A | P4 ¦ Oil Storage & Offloading ¦ Cargo & Ballast Hydraulic Valve Control | P4 | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | FA_REMA | AXIAL COMPRESSOR | M | MECH
|  |  | R-NOTVALIDATED | GIZA FAYOUM NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Oil Storage & Offloading ¦ Marine Hydraulic systems (pumps, power units and storage tanks) | P4 | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | FA_REMC | CENTRIFUGAL COMPRESSOR | M | MECH
|  |  | E-NOTVALIDATED | RAVEN NON VALIDATED TAGS | FA_SYLH | N/A | N/A | P4 ¦ Oil Storage & Offloading ¦ Void Tank Gas Detection | P4 | Oil Storage & Offloading | Void Tank Gas Detection | A | FA_REMR | RECIPROCATING COMPRESSOR | M | MECH
|  |  | BP-WND | BP WEST NILE DELTA | FA_SYLH | N/A | N/A | P4 ¦ Oil Storage & Offloading ¦ Void Tank Dehumidification systems | P4 | Oil Storage & Offloading | Void Tank Dehumidification systems | B | FA_REMT | ROTARY COMPRESSOR | M | MECH
|  |  | GFR-CIVILS | CIVILS AND STRUCTURES | FA_SYLH | N/A | N/A | P4 ¦ Oil Storage & Offloading ¦ Hydrocarbon Tanks | P4 | Oil Storage & Offloading | Hydrocarbon Tanks | A | FA_REFA | AXIAL FAN | M | MECH
|  |  | GFR-CIVILS-ARCH | ARCHITECTURAL | FA_SYLH | N/A | N/A | P4 ¦ Oil Storage & Offloading ¦ Ballast Tanks | P4 | Oil Storage & Offloading | Ballast Tanks | A | FA_REFC | CENTRIFUGAL FAN | M | MECH
|  |  | GFR-CIVILS-CIV | ON SHORE CIVIL | FA_SYLH | N/A | N/A | P4 ¦ Oil Storage & Offloading ¦ Void Tanks | P4 | Oil Storage & Offloading | Void Tanks | B | FA_REDH | HYDRAULIC MOTOR | M | MECH
|  |  | GFR-CIVILS-MMH | MATERIALS AND MECHANICAL HANDLING | FA_SYLH | N/A | N/A | P5 ¦ Overpressure Protection ¦ PSV in hazardous or toxic duty | P5 | Overpressure Protection | PSV in hazardous or toxic duty | A | FA_REDP | PNEUMATIC MOTOR | M | MECH
|  |  | GFR-CIVILS-SITE | SITE PREPARATION | FA_SYLH | N/A | N/A | P5 ¦ Overpressure Protection ¦ PSV in non-hazardous, non-toxic service where pressure is above 50 barg | P5 | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | FA_REDT | TOP DRIVE | N | TBC
|  |  | GFR-COMMS | COMMS, NAV AND MONITORING | FA_SYLH | 83 | 83 | P5 ¦ Overpressure Protection ¦ PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | P5 | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | FA_REI | MIXER | M | MECH
|  |  | GFR-COMMS-ICSS | CONTROL AND MONITORING SYSTEMS (ICSS) | FA_SYLH | 76 | 76 | P5 ¦ Overpressure Protection ¦ PSV in non-hazardous, nontoxic service where inlet size 8” or above | P5 | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | FA_RETC | CLUTCH | M | MECH
|  |  | GFR-COMMS-NAV | NAV AIDS | FA_SYLH | 83 | 83 | P5 ¦ Overpressure Protection ¦ All other PSVs | P5 | Overpressure Protection | All other PSVs | B | FA_RETV | CONTINOUSLY VARIABLE TRANSMISSION | M | MECH
|  |  | GFR-COMMS-TELE | TELECOMMUNICATIONS | FA_SYLH | 83 | 83 | P5 ¦ Overpressure Protection ¦ NRV credited in the sizing case for a PSV | P5 | Overpressure Protection | NRV credited in the sizing case for a PSV | A | FA_RETP | COUPLING | M | MECH
|  |  | GFR-COND-PR | CONDENSATE PROCESSING | FA_SYLH | 20 | 20 | P5 ¦ Overpressure Protection ¦ NRV that protects against any E+ severity event. For example, damage to Equipment | P5 | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | FA_RETG | GEARBOX | M | MECH
|  |  | GFR-COND-PR-CPE | CONDENSATE PUMPING AND EXPORT | FA_SYLH | 21 | 21 | P5 ¦ Overpressure Protection ¦ NRVs where consequence/likelihood of failure combination leads to a turquoise risk | P5 | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | FA_RETH | HYDRAULIC / TORQUE CONVERTER | M | MECH
|  |  | GFR-COND-PR-CT | CONDENSATE TREATMENT | FA_SYLH | 21 | 21 | P5 ¦ Overpressure Protection ¦ All other NRVs | P5 | Overpressure Protection | All other NRVs | C | FA_REPB | BEAM PUMP | M | MECH
|  |  | GFR-GAS-PR | GAS PROCESSING | FA_SYLH | 22 | 22 | P5 ¦ Overpressure Protection ¦ ROs (or FOs) that restrict gas flow to flare | P5 | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | FA_REPC | CENTRIFUGAL PUMP | M | MECH
|  |  | GFR-GAS-PR-FGCT1 | FLASH GAS COMPRESSION TRAIN 1 RAVEN | FA_SYLH | 24 | 24 | P5 ¦ Overpressure Protection ¦ ROs (or FOs) that restrict flow to a PSV | P5 | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | FA_REPV | CONTROLLED VOLUME PUMP | M | MECH
|  |  | GFR-GAS-PR-GC | GAS COMPRESSION | FA_SYLH | 23 | 23 | P5 ¦ Overpressure Protection ¦ ROs in pump recirculation lines | P5 | Overpressure Protection | ROs in pump recirculation lines | B | FA_REPD | POSITIVE DISPLACEMENT PUMP | M | MECH
|  |  | GFR-GAS-PR-GE | GAS EXPORT | FA_SYLH | 27 | 27 | P5 ¦ Overpressure Protection ¦ Control valves credited in LOPA | P5 | Overpressure Protection | Control valves credited in LOPA | A | FA_REPG | PROGRESSIVE CAVITY PUMP | M | MECH
|  |  | GFR-GAS-PR-GIF | GAS IMPORT FACILITIES | FA_SYLH | 22 | 22 | P5 ¦ Overpressure Protection ¦ Bursting disks in hazardous or toxic duty | P5 | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | FA_REPR | RECIPROCATING PUMP | M | MECH
|  |  | GFR-GAS-PR-GT | GAS TREATMENT | FA_SYLH | 25 | 25 | P5 ¦ Overpressure Protection ¦ Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | P5 | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | FA_RER | RAKE / SCRAPER | M | MECH
|  |  | GFR-GAS-PR-GL | GAS LIFT | FA_SYLH | N/A | N/A | P5 ¦ Overpressure Protection ¦ Bursting disk relieving directly to flare (i.e. no PSV downstream) | P5 | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | FA_REZ | ROTARY DRUM FILTER | B | MECH
|  |  | GFR-PIPE | PIPELINES AND PIPING | FA_SYLH | 20 | 20 | P5 ¦ Overpressure Protection ¦ Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | P5 | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | FA_RES | SOOTBLOWER | M | MECH
|  |  | GFR-PIPE-CP | CATHODIC AND CORROSION PROTECTION | FA_SYLH | 92 | 92 | P5 ¦ Overpressure Protection ¦ Other bursting disks | P5 | Overpressure Protection | Other bursting disks | B | FA_REXA | AXIAL TURBO EXPANDER | M | MECH
|  |  | GFR-PIPE-HT | HEAT TRACING | FA_SYLH | 86 | 86 | P5 ¦ Overpressure Protection ¦ Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | P5 | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | FA_REXC | CENTRIFUGAL TURBO EXPANDER | M | MECH
|  |  | GFR-PIPE-PIG | PIGGING | FA_SYLH | 20 | 20 | P5 ¦ Overpressure Protection ¦ Vacuum breakers in hazardous or toxic duty | P5 | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | FA_RENG | GAS TURBINE | M | MECH
|  |  | GFR-RELIEF | RELIEF AND FLARE | FA_SYLH | 41 | 41 | P5 ¦ Overpressure Protection ¦ Other Vacuum breakers not covered by the descriptions above. | P5 | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | FA_RENS | STEAM TURBINE | M | MECH
|  |  | GFR-RELIEF-AFV | ATMOSPHERIC FLARE AND VENT | FA_SYLH | 43 | 43 | P5 ¦ Overpressure Protection ¦ Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | P5 | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | FA_REUC | CHEMICAL INJECTION SYSTEM | M | MECH
|  |  | GFR-RELIEF-HPF | HP FLARE | FA_SYLH | 42 | 42 | P5 ¦ Blowdown vent and flare ¦ Blowdown valves in hazardous or toxic duty | P5 | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | FA_REUH | HYDRAULIC SYSTEM | M | MECH
|  |  | GFR-RELIEF-LPF | LP FLARE | FA_SYLH | 44 | 44 | P5 ¦ Blowdown vent and flare ¦ Blowdown valves in non-hazardous, nontoxic duty | P5 | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | FA_SEA | AIR DRYER | I | STRU
|  |  | GFR-SAFETY | SAFETY | FA_SYLH | 77 | 77 | P5 ¦ Blowdown vent and flare ¦ Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | P5 | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | FA_SEI | BIN / HOPPER | I | MECH
|  |  | GFR-SAFETY-ELP | EARTHING AND LIGHTING PROTECTION | FA_SYLH | 90 | 90 | P5 ¦ Blowdown vent and flare ¦ FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | P5 | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | FA_SEBF | FIRETUBE BOILER | I | MECH
|  |  | GFR-SAFETY-EPL | EMERGENCY, ESSENTIAL POWER AND LIGHTING | FA_SYLH | 84 | 84 | P5 ¦ Blowdown vent and flare ¦ All other FOVs | P5 | Blowdown vent and flare | All other FOVs | B | FA_SEBH | WASTE HEAT BOILER | I | MECH
|  |  | GFR-SAFETY-EPS | ESCAPE AND PERSONNEL SAFETY | FA_SYLH | 77 | 77 | P5 ¦ Blowdown vent and flare ¦ HP Flare KO Drum | P5 | Blowdown vent and flare | HP Flare KO Drum | A | FA_SEBW | WATERTUBE BOILER | I | MECH
|  |  | GFR-SAFETY-FDC | FOAM AND DRY CHEMICAL | FA_SYLH | 79 | 79 | P5 ¦ Blowdown vent and flare ¦ HP Flare KO Drum Pumps (at a component level, align with P4-D) | P5 | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | FA_SEC | CYCLONE | I | MECH
|  |  | GFR-SAFETY-FGD | FIRE AND GAS DETECTION | FA_SYLH | 78 | 78 | P5 ¦ Blowdown vent and flare ¦ HP Flare KO Drum Heaters | P5 | Blowdown vent and flare | HP Flare KO Drum Heaters | A | FA_SED | DRAIN POT | I | MECH
|  |  | GFR-SAFETY-FW | FIRE WATER | FA_SYLH | 81 | 81 | P5 ¦ Blowdown vent and flare ¦ LP Flare KO Drum | P5 | Blowdown vent and flare | LP Flare KO Drum | A | FA_SEE | EJECTOR / EDUCTOR | I | MECH
|  |  | GFR-SAFETY-NHES | EXTINGUISHING SYSTEMS | FA_SYLH | 79 | 79 | P5 ¦ Blowdown vent and flare ¦ LP Flare KO Drum Pumps (at a component level, align with P4-D) | P5 | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | FA_SEFB | BASKET STRAINER FILTER | B | MECH
|  |  | GFR-SAFETY-SDS | SHUTDOWN SYSTEMS | FA_SYLH | 77 | 77 | P5 ¦ Blowdown vent and flare ¦ KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | P5 | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | FA_SEFC | COALESCER FILTER | I | MECH
|  |  | GFR-SUBSEA | SUBSEA | FA_SYLH | 05 | 05 | P5 ¦ Blowdown vent and flare ¦ Flare tip ignition systems | P5 | Blowdown vent and flare | Flare tip ignition systems | A | FA_SEFP | ELECTROSTATIC PRECIPITATOR FILTER | B | MECH
|  |  | GFR-SUBSEA-SST | SUBSEA STRUCTURE AND TEMPLATE | FA_SYLH | 13 | 13 | P5 ¦ Blowdown vent and flare ¦ Flare system XXVs that are not covered under FOVs | P5 | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | FA_SEFE | ELEMENT FILTER | M | MECH
|  |  | GFR-TEMP | TEMPORARY ITEMS | FA_SYLH | N/A | N/A | P5 ¦ Blowdown vent and flare ¦ Flare tips | P5 | Blowdown vent and flare | Flare tips | A | FA_SEFM | MEDIA FILTER | M | MECH
|  |  | GFR-TEMP-GEN | GENERAL EQUIPMENT | FA_SYLH | N/A | N/A | P5 ¦ Blowdown vent and flare ¦ Any Equipment that maintains the barrier between wet and dry fluids | P5 | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | FA_SEFR | REVERSE OSMOSIS FILTER | M | MECH
|  |  | GFR-TEMP-TEQ | TEMPORARY EQUIPMENT | FA_SYLH | N/A | N/A | P5 ¦ Blowdown vent and flare ¦ Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | P5 | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | FA_SEFS | SCREEN FILTER | M | MECH
|  |  | GFR-UTIL | UTILITIES | FA_SYLH | 53 | 53 | P5 ¦ Blowdown vent and flare ¦ Other vents | P5 | Blowdown vent and flare | Other vents | C | FA_SEL | FLAME ARRESTOR | M | MECH
|  |  | GFR-UTIL-AF | ACCOMMODATION FACILITIES | FA_SYLH | N/A | N/A | P5 ¦ Blowdown vent and flare ¦ Equipment providing early indication of blockages within flare header | P5 | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | FA_SEM | FLARE | I | MECH
|  |  | GFR-UTIL-BAT | BATTERY NO-BREAK | FA_SYLH | 88 | 88 | P5 ¦ Blowdown vent and flare ¦ Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | P5 | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | FA_SENF | FIRED HEATER FURNACE | I | MECH
|  |  | GFR-UTIL-BGWS | BLACK AND GREY WATER AND SEWAGE | FA_SYLH | 82 | 82 | P5 ¦ Blowdown vent and flare ¦ Flare pipework and headers (align with barrier P4) | P5 | Blowdown vent and flare | Flare pipework and headers (align with barrier P4) | A | FA_SENI | INCINERATOR FURNACE | I | MECH
|  |  | GFR-UTIL-CD | CLOSED DRAINS | FA_SYLH | 57 | 57 | P6 ¦ Digital security ¦ Fire walls Remote access servers Architecture Staging servers for Anti-virus and OS patches | P6 | Digital security | Fire walls Remote access servers Architecture Staging servers for Anti-virus and OS patches | A | FA_SENT | THERMAL OXIDIZER FURNACE | I | MECH
|  |  | GFR-UTIL-CHEM-INJ | CHEMICAL INJECTION | FA_SYLH | 47 | 47 | P6 ¦ Control systems - LoPs ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, p | P6 | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | FA_SEHC | CALORIFIER HEAT EXCHANGER | I | MECH
|  |  | GFR-UTIL-CM | COOLING MEDIUM | FA_SYLH | N/A | N/A | P6 ¦ Control systems - non LoPs, LOPA initiating causes ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI sc | P6 | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | FA_SEHF | FINNED COIL HEAT EXCHANGER | I | MECH
|  |  | GFR-UTIL-DEH | DIRECT ELECTRIC HEATING | FA_SYLH | N/A | N/A | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable | P6 | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | FA_SEHP | PLATE & FRAME HEAT EXCHANGER | I | MECH
|  |  | GFR-UTIL-DF | DIESEL FUEL | FA_SYLH | 62 | 62 | P7 ¦ SIS - LoP Components ¦ LoP Components: Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial | P7 | SIS - LoP Components | LoP Components: Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. Testing Equipment Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | FA_SEHR | RECUPERATOR HEAT EXCHANGER | I | MECH
|  |  | GFR-UTIL-FG | FUEL GAS | FA_SYLH | 40 | 40 | P7 ¦ SIS - Non LoP Components ¦ LoP Components: Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke | P7 | SIS - Non LoP Components | LoP Components: Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | FA_SEHT | SHELL & TUBE HEAT EXCHANGER | I | MECH
|  |  | GFR-UTIL-FW | FRESH WATER | FA_SYLH | 53 | 53 | P8 ¦ Alarms & operator response ¦ Instruments associated with Safety Related Alarms (credited in LOPA) - transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and po | P8 | Alarms & operator response | Instruments associated with Safety Related Alarms (credited in LOPA) - transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | FA_SEHS | SPIRAL HEAT EXCHANGER | I | MECH
|  |  | GFR-UTIL-HM | HEATING MEDIUM | FA_SYLH | 60 | 60 | P8 ¦ Alarms & operator response ¦ Instruments associated with non-Safety Related Alarms - transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distributio | P8 | Alarms & operator response | Instruments associated with non-Safety Related Alarms - transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | B | FA_SEY | HYDRAULIC HATCH | N | TBC
|  |  | GFR-UTIL-HO | HOT OIL | FA_SYLH | 60 | 60 | P9 ¦ Collision Prevention ¦ Navigation Aids, lights, sounders & UPS systems | P9 | Collision Prevention | Navigation Aids, lights, sounders & UPS systems | A | FA_SEV | LOUVRE | M | HVAC
|  |  | GFR-UTIL-HOD | HAZARDOUS OPEN DRAINS | FA_SYLH | 56 | 56 | P9 ¦ Export tanker birthing and position monitoring ¦ Mooring Hawser and Load Monitoring | P9 | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | FA_SEPA | ACCUMULATOR | I | MECH
|  |  | GFR-UTIL-HP | HYDRAULIC POWER | FA_SYLH | 05 | 05 | P9 ¦ Export tanker birthing and position monitoring ¦ Berthing System (TAOMS) | P9 | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | FA_SEPC | CYLINDER | I | MECH
|  |  | GFR-UTIL-HVAC | HVAC | FA_SYLH | 94 | 94 | M1 ¦ Bunding, Open and Closed Hazardous Drains ¦ Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | M1 | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | FA_SEPHC | CONDENSER VESSEL | I | MECH
|  |  | GFR-UTIL-HVD | HV DISTRIBUTION | FA_SYLH | 80 | 80 | M1 ¦ Bunding, Open and Closed Hazardous Drains ¦ Main Deck Coaming | M1 | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | FA_SEPHS | SEPARATOR VESSEL | I | MECH
|  |  | GFR-UTIL-HW | HOT WATER | FA_SYLH | N/A | N/A | M1 ¦ Bunding, Open and Closed Hazardous Drains ¦ Open Hazardous Drains Water seals | M1 | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | FA_SEPHV | VAPORISER VESSEL | I | MECH
|  |  | GFR-UTIL-IA | INSTRUMENT AIR | FA_SYLH | 63 | 63 | M1 ¦ Bunding, Open and Closed Hazardous Drains ¦ Close drain Drum Alarms | M1 | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | FA_SEPRX | FIXED BED REACTOR | I | MECH
|  |  | GFR-UTIL-IG | INERT GAS | FA_SYLH | 64 | 64 | M1 ¦ Bunding, Open and Closed Hazardous Drains ¦ Close drain Drum heating system (heating Coil, instrumentation, insulation) | M1 | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | FA_SEPRL | FLUIDISED BED REACTOR | I | MECH
|  |  | GFR-UTIL-LSO | LUBE AND SEAL OIL | FA_SYLH | N/A | N/A | M1 ¦ Bunding, Open and Closed Hazardous Drains ¦ Secondary containments | M1 | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | FA_SEPRR | REGENERATOR REACTOR | I | MECH
|  |  | GFR-UTIL-LVD | LV DISTRIBUTION | FA_SYLH | 80 | 80 | M1 ¦ Bunding, Open and Closed Hazardous Drains ¦ Helideck Drainage | M1 | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | FA_SEPVA | ABSORBER COLUMN | I | MECH
|  |  | GFR-UTIL-MP | MAIN POWER GENERATION | FA_SYLH | 91 | 91 | M1 ¦ Bunding, Open and Closed Hazardous Drains ¦ Rodding | M1 | Bunding, Open and Closed Hazardous Drains | Rodding | A | FA_SEPVC | CONTACTOR COLUMN | I | MECH
|  |  | GFR-UTIL-MRSI | MEG REGEN, STORAGE AND INJECTION | FA_SYLH | 28 | 28 | M2 ¦ Passive Fire Protection ¦ PFP where applied | M2 | Passive Fire Protection | PFP where applied | A | FA_SEPVS | SCRUBBER COLUMN | I | MECH
|  |  | GFR-UTIL-NHOD | NON-HAZARDOUS OPEN DRAINS | FA_SYLH | 58 | 58 | M2 ¦ Blast Overpressure Protection ¦ Blast Walls | M2 | Blast Overpressure Protection | Blast Walls | A | FA_SEPVT | STRIPPER COLUMN | I | MECH
|  |  | GFR-UTIL-PA | PLANT AIR | FA_SYLH | 65 | 65 | M2 ¦ Blast Overpressure Protection ¦ Blast Doors | M2 | Blast Overpressure Protection | Blast Doors | A | FA_SES | PULSATION DAMPENER | B | MECH
|  |  | GFR-UTIL-PW | POTABLE WATER | FA_SYLH | 53 | 53 | M2 ¦ Temporary refuge integrity ¦ External Temporary Refuge doors | M2 | Temporary refuge integrity | External Temporary Refuge doors | A | FA_SEZ | SILENCER / MUFFLER | M | MECH
|  |  | GFR-UTIL-STOR | STORAGE | FA_SYLH | N/A | N/A | M2 ¦ Temporary refuge integrity ¦ Internal Temporary Fire Refuge doors | M2 | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | FA_SER | STATIC MIXER | I | MECH
|  |  | GFR-UTIL-SW | SEAWATER | FA_SYLH | 54 | 54 | M3 ¦ Alarm Annunciation System: ¦ External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | M3 | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | FA_SETAC | CLOSED ROOF ATMOSPHERIC TANK | I | MECH
|  |  | GFR-UTIL-WELS | WORKSHOP EQUIPMENT, LAB AND STORAGE | FA_SYLH | N/A | N/A | M3 ¦ Personnel Address (PA) System ¦ Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | M3 | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | FA_SETAF | FLOATING ROOF ATMOSPHERIC TANK | I | MECH
|  |  | GFR-WAT-PR | WATER PROCESSING | FA_SYLH | 67 | 67 | M3 ¦ Marine, Aircraft and Helicopter Radio System ¦ Antenna Receiver/transmitter Batteries Sat comms | M3 | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | FA_SETAO | OPEN ROOF ATMOSPHERIC TANK | I | MECH
|  |  | GFR-WAT-PR-PWRI | WATER RE-INJECTION | FA_SYLH | 67 | 67 | M3 ¦ Telecommunications ¦ Class A Telecommunication UPS & Shut down | M3 | Telecommunications | Class A Telecommunication UPS & Shut down | A | FA_SETAR | RESERVOIR | I | MECH
|  |  | GFR-WAT-PR-PWT | PRODUCED WATER TREATMENT | FA_SYLH | 67 | 67 | M3 ¦ Electronic Muster System ¦ Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | M3 | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | FA_SETAP | PIT / SUMP | I | MECH
|  |  | GFR | GIZA FAYOUM & RAVEN | FA_SYLH | N/A | N/A | M3 ¦ Facility Emergency Telephone & Hot line systems ¦ Call control - PABX/IPT Ex telephones Designated emergency phones (Control rooms muster points etc.) Interconnecting cable plant and networks | M3 | Facility Emergency Telephone & Hot line systems | Call control - PABX/IPT Ex telephones Designated emergency phones (Control rooms muster points etc.) Interconnecting cable plant and networks | A | FA_SETPC | CYLINDRICAL PRESSURISED TANK | I | MECH
|  |  | GFR-GAS-PR-FGCT2 | FLASH GAS COMPRESSION TRAIN 2 RAVEN | FA_SYLH | 24 | 24 | M3 ¦ Facility radio system ¦ Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | M3 | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | FA_SETPS | SPHERICAL PRESSURISED TANK | I | MECH
|  |  | GFR-GAS-PR-FGC | FLASH GAS COMPRESSION | FA_SYLH | 24 | 24 | M3 ¦ Emergency Power ¦ Emergency Generator | M3 | Emergency Power | Emergency Generator | A | FA_SQL | LABORATORY EQUIPMENT | M | INST
|  |  | GFR-DEL | GFR DEL STATUS | FA_SYLH | N/A | N/A | M3 ¦ Emergency Power ¦ Hull Generators | M3 | Emergency Power | Hull Generators | A | FA_SQMT | MAINTENANCE TOOL | M | MECH
|  |  | GFR-NOPARENT | GFR NO PARENT IDENTIFIED | FA_SYLH | N/A | N/A | M3 ¦ Emergency Power ¦ Hull Generators (2 out of 3) | M3 | Emergency Power | Hull Generators (2 out of 3) | B | FA_SQMC | PORTABLE COMPRESSOR | N | TBC
|  |  | GFR-NOTVALIDATED | GFR NON VALIDATED TAGS | FA_SYLH | N/A | N/A | M3 ¦ Emergency Power ¦ UPS Systems | M3 | Emergency Power | UPS Systems | A | FA_SQMG | PORTABLE GENERATOR | N | TBC
|  |  | GFR-COND-PR-PS | PROCESS SEPARATION | FA_SYLH | 20 | 20 | M3 ¦ Emergency Lighting ¦ Emergency Lighting - battery backed | M3 | Emergency Lighting | Emergency Lighting - battery backed | A | FA_SQML | PORTABLE LIGHT PLANT | N | TBC
|  |  | GFR-COND-PR-PR | PROCESS RECEPTION | FA_SYLH | 22 | 22 | M3 ¦ Emergency Lighting ¦ Emergency Lighting - supplied from Emergency Generator Switchboard | M3 | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | FA_SQMD | TESTING DEVICE | M | INST
|  |  | GFR-UTIL-TO | THERMAL OXIDIZER | FA_SYLH | 54 | 54 | M3 ¦ Emergency Lighting ¦ Emergency Lighting - Emergency Hand Torches in switchgear rooms | M3 | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | FA_SQMW | WELDING MACHINE | N | TBC
|  |  | GFR-SUBSEA-SSCS | SUBSEA CONTROL SYSTEMS | FA_SYLH | 05 | 05 | M4 ¦ Ignition Prevention ¦ For Equipment in Zone 0 and Zone 1 | M4 | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | FA_SQR | OIL SPILL RESPONSE EQUIPMENT | M | SAFE
|  |  | GFR-SOFT | GFR SOFT TAGS | FA_SYLH | N/A | N/A | M4 ¦ Ignition Prevention ¦ For Equipment in Zone 2 | M4 | Ignition Prevention | For Equipment in Zone 2 | B | FA_SQNL | NAVIGATION LIGHT | M | ELEC
|  |  | GFR-GAS-PR-GTT1 | GAS TREATMENT TRAIN 1 RAVEN | FA_SYLH | 25 | 25 | M4 ¦ Ignition Prevention ¦ Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | M4 | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | FA_SQNP | POSITIONING EQUIPMENT | M | ELEC
|  |  | GFR-GAS-PR-GTT2 | GAS TREATMENT TRAIN 2 RAVEN | FA_SYLH | 25 | 25 | M4 ¦ Inert Gas Blanketing ¦ IGG Generator | M4 | Inert Gas Blanketing | IGG Generator | A | FA_SQNB | SIGNAL BUOY | M | ELEC
|  |  | GFR-GAS-PR-GEA | GAS EXPORT TRAIN A GIZA FAYOUM | FA_SYLH | 27 | 27 | M4 ¦ Inert Gas Blanketing ¦ IGG Generator Diesel Oil Supply Pumps | M4 | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | FA_SQFC | EQUIPMENT CABINET | M | ELEC
|  |  | GFR-GAS-PR-GEB | GAS EXPORT TRAIN B GIZA FAYOUM | FA_SYLH | 27 | 27 | M4 ¦ Inert Gas Blanketing ¦ Isolation valves on locked valve register | M4 | Inert Gas Blanketing | Isolation valves on locked valve register | A | FA_SQFDD | DUST DETECTOR | M | INST
|  |  | GFR-COMMS-TELE-RS | RADIO SYSTEM (INCLUDING SAT COM) | FA_SYLH | 99 | 99 | M5 ¦ Lifesaving Equipment ¦ Emergency escape breathing devices | M5 | Lifesaving Equipment | Emergency escape breathing devices | A | FA_SQFDG | FIXED GAS DETECTOR | M | INST
|  |  | GFR-COMMS-TELE-CCTV | CCTV - SECURITY | FA_SYLH | 96 | 96 | M5 ¦ Lifesaving Equipment ¦ Grab bags and smoke hoods | M5 | Lifesaving Equipment | Grab bags and smoke hoods | B | FA_SQFDF | FLAME DETECTOR | M | INST
|  |  | GFR-COMMS-TELE-AC | ACCESS CONTROL | FA_SYLH | 95 | 95 | M5 ¦ Lifesaving Equipment ¦ Lifejackets | M5 | Lifesaving Equipment | Lifejackets | A | FA_SQFDM | MOTION DETECTOR | M | INST
|  |  | GFR-COMMS-TELE-NW | LAN - VOIP NETWORK | FA_SYLH | 97 | 97 | M5 ¦ Lifesaving Equipment ¦ Lifebuoys | M5 | Lifesaving Equipment | Lifebuoys | B | FA_SQFDH | PERSONAL H2S MONITOR | M | SAFE
|  |  | GFR-COMMS-TELE-PA | PUBLIC ADDRESS AND GENERAL ALARM (PAGA) | FA_SYLH | 98 | 98 | M5 ¦ Lifesaving Equipment ¦ Line-throwing Device | M5 | Lifesaving Equipment | Line-throwing Device | B | FA_SQFDR | PERSONAL RADIATION MONITOR | M | SAFE
|  |  | GFR-RELIEF-HPWF | HP WET FLARE | FA_SYLH | 41 | 41 | M5 ¦ Lifesaving Equipment ¦ Helicopter Crash Equipment | M5 | Lifesaving Equipment | Helicopter Crash Equipment | B | FA_SQFDP | PORTABLE GAS MONITOR | M | SAFE
|  |  | GFR-UTIL-FGLP | FUEL GAS LP | FA_SYLH | 40 | 40 | M5 ¦ Lifesaving Equipment ¦ Fireman Outfits | M5 | Lifesaving Equipment | Fireman Outfits | A | FA_SQFDS | SMOKE DETECTOR | M | INST
|  |  | GFR-UTIL-FGHP | FUEL GAS HP | FA_SYLH | 45 | 45 | M5 ¦ Lifesaving Equipment ¦ Emergency Breathing Air Compressor | M5 | Lifesaving Equipment | Emergency Breathing Air Compressor | B | FA_SQFFE | FIRE EXTINGUISHER | M | SAFE
|  |  | GFR-UTIL-MPM | MAIN POWER MANAGEMENT SYSTEM | FA_SYLH | 93 | 93 | M5 ¦ Lifesaving Equipment ¦ Storage Containers | M5 | Lifesaving Equipment | Storage Containers | C | FA_SQFFS | FIRE EXTINGUISHING SYSTEM | M | SAFE
|  |  | GFR-SAFETY-EMPL | EMERGENCY POWER AND LIGHTING | FA_SYLH | 87 | 87 | M5 ¦ Muster areas, escape and evacuation routes ¦ Station Bill | M5 | Muster areas, escape and evacuation routes | Station Bill | B | FA_SQFFF | FIRE FIGHTING FOAM SYSTEM | M | SAFE
|  |  | GFR-SAFETY-ESPL | ESSENTIAL POWER AND LIGHTING | FA_SYLH | 84 | 84 | M5 ¦ Muster areas, escape and evacuation routes ¦ Escape Routes | M5 | Muster areas, escape and evacuation routes | Escape Routes | A | FA_SQFFH | FIRE HOSE | M | SAFE
|  |  | GFR-UTIL-MRSI-RICH | RICH MEG REGEN, STORAGE AND INJECTION | FA_SYLH | 28 | 28 | M5 ¦ Muster areas, escape and evacuation routes ¦ Escape Route Doors | M5 | Muster areas, escape and evacuation routes | Escape Route Doors | A | FA_SQFFY | FIRE HYDRANT | M | SAFE
|  |  | GFR-UTIL-MRSI-LEAN | LEAN MEG REGEN, STORAGE AND INJECTION | FA_SYLH | 29 | 29 | M5 ¦ Muster areas, escape and evacuation routes ¦ Primary Muster Area | M5 | Muster areas, escape and evacuation routes | Primary Muster Area | A | FA_SQFFT | FIRE TRUCK | M | SAFE
|  |  | GFR-UTIL-CHEM-MEIN | CHEMICAL METHANOL INJECTION | FA_SYLH | 47 | 47 | M5 ¦ Muster areas, escape and evacuation routes ¦ Egress Routes | M5 | Muster areas, escape and evacuation routes | Egress Routes | A | FA_SQFFM | FIRE WATER/FOAM MONITOR | M | SAFE
|  |  | GFR-UTIL-CHEM-REBR | CHEMICAL REVERSE EMULSION BREAKER | FA_SYLH | 50 | 50 | M5 ¦ Muster areas, escape and evacuation routes ¦ Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | M5 | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | FA_SQFFD | FIREWATER DELUGE SYSTEM | M | SAFE
|  |  | GFR-UTIL-CHEM-OXSC | CHEMICAL OXYGEN SCAVENGER | FA_SYLH | 61 | 61 | M5 ¦ Muster areas, escape and evacuation routes ¦ Alternative Muster Areas | M5 | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | FA_SQFRD | AUTOMATED EXTERNAL DEFIBRILLATOR | M | SAFE
|  |  | GFR-UTIL-CHEM-MCIN | MEG CHEMICAL INJECTION | FA_SYLH | 52 | 52 | M5 ¦ Lifeboats ¦ Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | M5 | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | FA_SQFRB | BREATHING AIR BOTTLE | M | SAFE
|  |  | GFR-UTIL-CHEM-KIIN | KINETIC INHIBITOR INJECTION | FA_SYLH | 49 | 49 | M5 ¦ Lifeboats ¦ Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | M5 | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | FA_SQFRS | BREATHING AIR SYSTEM | M | SAFE
|  |  | GFR-UTIL-CHEM-CIIN | CORROSION INHIBITOR INJECTION | FA_SYLH | 48 | 48 | M5 ¦ Lifeboats ¦ Release Mechanism | M5 | Lifeboats | Release Mechanism | A | FA_SQFRC | DESCENT DEVICE | M | SAFE
|  |  | GFR-UTIL-CHEM-MISC | CHEMICALS - MISCELLANEOUS | FA_SYLH | 55 | 55 | M5 ¦ Lifeboats ¦ Deluge, Engine | M5 | Lifeboats | Deluge, Engine | A | FA_SQFRA | EMERGENCY ALARM DEVICE | M | SAFE
[8 empty] | M5 ¦ Lifeboats ¦ VHF Radio | M5 | Lifeboats | VHF Radio | A | FA_SQFRL | LIFEBOAT AND DAVIT | N | TBC
[8 empty] | M5 ¦ Lifeboats ¦ Emergency Beacons | M5 | Lifeboats | Emergency Beacons | A | FA_SQFRY | LIFEBUOY | M | SAFE
[8 empty] | M5 ¦ Means of escape to sea ¦ Life-rafts | M5 | Means of escape to sea | Life-rafts | A | FA_SQFRJ | LIFEJACKET | M | SAFE
[8 empty] | M5 ¦ Means of escape to sea ¦ Personal Davit Descent devices | M5 | Means of escape to sea | Personal Davit Descent devices | A | FA_SQFRR | LIFERAFT | M | SAFE
[8 empty] | M5 ¦ Means of escape to sea ¦ Embarkation Rope Ladders to Sea | M5 | Means of escape to sea | Embarkation Rope Ladders to Sea | A | FA_SQFRK | PERSONNEL BASKET | M | SAFE
[8 empty] | M5 ¦ Helideck ¦ Helideck Landing Area Net (as required) | M5 | Helideck | Helideck Landing Area Net (as required) | C | FA_SQFRT | RESCUE BOAT | N | TBC
[8 empty] | M5 ¦ Helideck ¦ Perimeter Net - (Integrity inspections) | M5 | Helideck | Perimeter Net - (Integrity inspections) | B | FA_SQFRE | SAFETY SHOWER OR EYE BATH | M | SAFE
[8 empty] | M5 ¦ Helideck ¦ Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | M5 | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | FA_SQFRP | SELF-CONTAINED BREATHING APPARATUS | M | SAFE
[8 empty] | M5 ¦ Helideck ¦ Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | M5 | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | FA_SQFRV | SURVIVAL SUIT | N | TBC
[8 empty] | M5 ¦ Helideck ¦ Firefighting Equipment (System) - including Foam (as required) | M5 | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | FA_SRFRN | VENTILATOR | M | SAFE
[8 empty] | M5 ¦ Helideck ¦ Helideck Equipment - Deck crew duties and helicopter Ops support | M5 | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | FA_SQTM | AMPLIFIER | M | TELE
[8 empty] | M5 ¦ Helideck ¦ Emergency Equipment - Helideck emergency response Equipment | M5 | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | FA_SQTN | ANTENNA | M | TELE
[8 empty] | M5 ¦ Helideck ¦ MET System (Meteorological Equipment) - On-board IMMS System | M5 | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | FA_SQTV | CCTV CAMERA UNIT | M | TELE
[8 empty] | M5 ¦ Rescue & Recovery Systems ¦ Place of Safety | M5 | Rescue & Recovery Systems | Place of Safety | B | FA_SQTC | COMPASS | M | TELE
[8 empty] | M5 ¦ Rescue & Recovery Systems ¦ Man Overboard Alarm | M5 | Rescue & Recovery Systems | Man Overboard Alarm | B | FA_SQTP | COMPUTER PERIPHERAL | M | TELE
[8 empty] | M5 ¦ Rescue & Recovery Systems ¦ Fast Rescue craft | M5 | Rescue & Recovery Systems | Fast Rescue craft | B | FA_SQTF | FACSIMILE MACHINE | M | TELE
[8 empty] | M5 ¦ Cranes ¦ Hoisting system | M5 | Cranes | Hoisting system | A | FA_SQTI | INTERCOM SYSTEM | M | TELE
[8 empty] | M5 ¦ Cranes ¦ Boom system | M5 | Cranes | Boom system | A | FA_SQTL | LOUDSPEAKER | M | TELE
[8 empty] | M5 ¦ Cranes ¦ Warning, recording & measuring systems | M5 | Cranes | Warning, recording & measuring systems | A | FA_SQTX | MULTIPLEXER | M | TELE
[8 empty] | M5 ¦ Cranes ¦ Structure | M5 | Cranes | Structure | A | FA_SQTB | NON DIRECTIONAL BEACON | M | TELE
[8 empty] | M5 ¦ Cranes ¦ Slewing system | M5 | Cranes | Slewing system | B | FA_SQTH | PATCH PANEL | M | TELE
[8 empty] | M5 ¦ Cranes ¦ Hydraulic system | M5 | Cranes | Hydraulic system | B | FA_SQTR | PROXIMITY READER | M | TELE
[8 empty] | M5 ¦ Cranes ¦ Prime mover system | M5 | Cranes | Prime mover system | B | FA_SQTA | PUBLIC ADDRESS AND ALARM SYSTEM | M | TELE
[8 empty] | M5 ¦ Cranes ¦ Access & walkways | M5 | Cranes | Access & walkways | A | FA_SQTD | RADAR | M | TELE
[8 empty] | M5 ¦ Cranes ¦ Maintenance Equipment | M5 | Cranes | Maintenance Equipment | C | FA_SQTOF | FIXED RADIO | M | TELE
[8 empty] | M5 ¦ Lifting system ¦ Runway beams | M5 | Lifting system | Runway beams | A | FA_SQTOP | PAGER | M | TELE
[8 empty] | M5 ¦ Lifting system ¦ Gantry crane | M5 | Lifting system | Gantry crane | A | FA_SQTOR | PORTABLE RADIO | M | TELE
[8 empty] | M5 ¦ Lifting system ¦ Lifeboat davit | M5 | Lifting system | Lifeboat davit | A | FA_SQTY | RECEIVER / TRANSMITTER | M | TELE
[8 empty] | M5 ¦ Lifting system ¦ Life-raft davit | M5 | Lifting system | Life-raft davit | A | FA_SQTT | SATELLITE EQUIPMENT | M | TELE
[8 empty] | M5 ¦ Lifting system ¦ General purpose/maintenance davit | M5 | Lifting system | General purpose/maintenance davit | B | FA_SQTE | TELECOMMUNICATION CABINET | M | TELE
[8 empty] | M5 ¦ Lifting system ¦ Winch (for lifting personnel) | M5 | Lifting system | Winch (for lifting personnel) | A | FA_SQTS | TELEPHONE OR MULTIMEDIA EQUIPMENT | M | TELE
[8 empty] | M5 ¦ Lifting system ¦ Winch (general purpose - not for lifting personnel) | M5 | Lifting system | Winch (general purpose - not for lifting personnel) | B | FA_SQTW | WIRELESS COMMUNICATION OR CONTROL EQUIPMENT | M | TELE
[8 empty] | M6 ¦ Fire & Gas systems ¦ Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | M6 | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | FA_SQUC | CLEANING EQUIPMENT | N | TBC
[8 empty] | M6 ¦ Fire & Gas systems ¦ Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | M6 | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | FA_SQUE | EXERCISE EQUIPMENT | N | TBC
[8 empty] | M6 ¦ Emergency Shutdown Systems ¦ XV/XXVs on emergency shutdown duty | M6 | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | FA_SQUG | GALLEY EQUIPMENT | M | ELEC
[8 empty] | M6 ¦ Riser ESDVs & EIVs ¦ Export/Import/Injection Riser ESDVs (XXVs) & actuators | M6 | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | FA_WECM | MOBILE CRANE | B | MECH
[8 empty] | M6 ¦ Riser ESDVs & EIVs ¦ Umbilical emergency ESDVs (XXVs) & actuators | M6 | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | FA_WECO | OVERHEAD CRANE | B | MECH
[8 empty] | M6 ¦ Riser ESDVs & EIVs ¦ Injection Flowline EIVs (XV) & actuators | M6 | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | FA_WECP | PEDESTAL CRANE | B | MECH
[8 empty] | M7 ¦ Fire protection ¦ Firewater pumps (main and jockey), drivers, their controls and control panels | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | FA_WECT | TOWER CRANE | B | MECH
[8 empty] | M7 ¦ Fire protection ¦ Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | FA_WELC | CABLE OR CHAIN | B | MECH
[8 empty] | M7 ¦ Fire protection ¦ Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | FA_WELB | CHAIN BLOCK | I | STRU
[8 empty] | M7 ¦ Fire protection ¦ Zone isolation valves | M7 | Fire protection | Zone isolation valves | A | FA_WELN | CONTAINER | B | MECH
[8 empty] | M7 ¦ Fire protection ¦ Sprinkler / Deluge Nozzle (≥10 per zone) | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | FA_WELD | DAVIT | B | MECH
[8 empty] | M7 ¦ Fire protection ¦ Sprinkler / Deluge Nozzle (<10 per zone) | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | FA_WELE | ELEVATOR | B | ELEC
[8 empty] | M7 ¦ Fire protection ¦ Pressure / level / flow instruments | M7 | Fire protection | Pressure / level / flow instruments | A | FA_WELF | FORKLIFT | M | MECH
[8 empty] | M7 ¦ Fire protection ¦ Control Valves | M7 | Fire protection | Control Valves | A | FA_WELH | HOIST | M | MECH
[8 empty] | M7 ¦ Fire protection ¦ Logic solvers | M7 | Fire protection | Logic solvers | A | FA_WELJ | JACK | M | MECH
[8 empty] | M7 ¦ Fire protection ¦ Accommodation hydrants (main fire-fighting mechanism) | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | FA_WELM | MAN LIFT / BASKET / CHERRY PICKER | B | STRU
[8 empty] | M7 ¦ Fire protection ¦ Accommodation hydrants (if sprinkler system present) | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | FA_WELT | MONORAIL / TROLLEY | M | MECH
[8 empty] | M7 ¦ Fire protection ¦ Fusible plug / fusible loop (≥3 per fire zone) | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | FA_WELS | SHEAVE OR PULLEY | M | MECH
[8 empty] | M7 ¦ Fire protection ¦ Fusible plug / fusible loop (<3 per zone) | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | FA_WELG | SLING | M | MECH
[8 empty] | M7 ¦ Miscellaneous fire protection systems ¦ Hose reels, nozzles and portable fire monitors | M7 | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | FA_WELP | SPREADER FRAME / BAR | M | MECH
[8 empty] | M7 ¦ Miscellaneous fire protection systems ¦ Mobile (wheeled) fire extinguishers | M7 | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | FA_WELW | WINCH | M | MECH
[8 empty] | M7 ¦ Miscellaneous fire protection systems ¦ Fixed CO2 Fire Extinguishing Systems | M7 | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | FA_WEHY | CONVEYOR | M | MECH
[8 empty] | M7 ¦ Miscellaneous fire protection systems ¦ Galley Fire Suppression System | M7 | Miscellaneous fire protection systems | Galley Fire Suppression System | A | FA_WEHR | CRUSHER / SHREDDER | M | MECH
[8 empty] | M7 ¦ Miscellaneous fire protection systems ¦ Water Mist Systems | M7 | Miscellaneous fire protection systems | Water Mist Systems | B | FA_WEHC | CUTTING DRILL | M | MECH
[13 empty] | FA_WEHS | SHAKER | M | MECH
[13 empty] | FA_WED | LOADING ARM | N | TBC
[13 empty] | FA_WESR | REMOTE OPERATED VEHICLE (ROV) | N | TBC
[13 empty] | FA_WEST | RUNNING TOOL | N | TBC
[13 empty] | FA_WETRA | AUTOMOBILE | M | MECH
[13 empty] | FA_WETRL | LAWNMOWER | M | MECH
[13 empty] | FA_WETRC | ROAD COMPACTOR | M | MECH
[13 empty] | FA_WETRS | ROAD SCRAPER | M | MECH
[13 empty] | FA_WETRW | ROAD SWEEPER | M | MECH
[13 empty] | FA_WETRO | TRACTOR | M | MECH
[13 empty] | FA_WETRR | TRAILER | M | MECH
[13 empty] | FA_WETRT | TRUCK | M | MECH
[13 empty] | FA_WETWB | BARGE | N | TBC
[13 empty] | FA_WETWF | MARINE FENDER | N | TBC
[13 empty] | FA_WETWT | MARINE THRUSTER | N | TBC
[13 empty] | FA_WETWV | MARINE VESSEL | N | TBC
[13 empty] | FA_PEVX | DIVERTER VALVE | M | MECH
[13 empty] | FA_PEN | METER PROVER | M | MECH
[13 empty] | FA_INAF | FLOW COMPUTER | M | INST
[13 empty] | FA_INAM | FLOW METER | M | INST
[13 empty] | FA_INAP | SAMPLER | M | INST
[13 empty] | FA_SYLH | SYSTEM LEVEL HIERARCHY | M | SYST
Note on N3: Author: Truncated to 254 characters due to 255 char limit in VLOOKUP function used to find things in this table