## Method
Methodology
In this spreadsheet, the criticality results for functional locations has been set in line with EG001-OP-PRO-00-3051
Step 1: Assign criticalities to system codes
This is shown in the Systems worksheet, where risk rankings from BP Risk Management Policy 000030 have been
assigned for each of the four categories Safety (S), Environment (E), Production (P) and Business non-financial (B)
These risk rankings are converted into equivalent A,B,C criticalities using the matrix in Annex D of BP Guide
Functional Location Criticality for SAP PM (GOO-RL-GLN-00002)
Rev 0 - Risk rankings have been estimated by AE as a starting point for review and agreement by BP
Step 2: Assign criticalities to failure codes
This is shown in the FailureCodes worksheet, where risk rankings have been allocated for each failure code.
Rev 0 - Risk rankings have been estimated by AE based on our experience, but in this case rankings have been
selected at the low end of the range of previously generated options due to concerns over 'criticality inflation'
inherent in the method outlined in EG001-OP-PRO-00-3051. To clarify, these are not the lowest possible rankings,
but the lowest of the range of rankings that AE had assigned within a failure class on initial review of the
functional location hierarchy for criticality. They do not yet have an individual commentary on the reasons for
selection of a ranking.

## FailureCodes
Only first character used in calculation
FailureCode | Description | Number found in MEL | SC_Impact | EC_Impact | PC_impact | BC_Impact | Criticality S | Criticality E | Criticality P | Criticality B |  | Criticality Overall
FA_CFBC | CONTROL ROOM | 2 | E3 | H3 | H3 | H3 | B | C | C | C | → | B
FA_CFSGA | ACCESS CONTROL GATE | 0 | G6 | H6 | H6 | H6 | B | C | C | C | → | B
FA_CFSGW | WALL OR FENCE | 5 | G6 | H6 | H6 | H6 | B | C | C | C | → | B
FA_CFSSE | EQUIPMENT SUPPORT STRUCTURE | 108 | E5 | H5 | H5 | G5 | A | C | C | C | → | A
FA_CFSSF | STRUCTURAL FOUNDATION | 19 | F5 | H5 | H5 | H5 | B | C | C | C | → | B
FA_CFSST | STRUCTURAL BASE | 110 | E7 | H7 | H7 | G7 | A | C | C | B | → | A | Likelihood too high?
FA_EECF | LIGHT FITTING | 398 | H7 | H7 | H7 | H7 | C | C | C | C | → | C | All lighting non-emergency lighting by default
FA_EECH | ELECTRIC HEATER | 64 | G5 | H5 | G5 | H5 | C | C | C | C | → | C | Least critical assumed
FA_EECMD | DC ELECTRIC MOTOR | 7 | E6 | H6 | F6 | H6 | A | C | B | C | → | A
FA_EECMI | AC INDUCTION ELECTRIC MOTOR | 379 | H6 | H6 | H6 | H6 | C | C | C | C | → | C | Lowest assumed
FA_EECMS | AC SYNCHRONOUS ELECTRIC MOTOR | 1 | E6 | H6 | F6 | H6 | A | C | B | C | → | A
FA_EECO | ELECTRIC SOCKET OUTLET | 18 | H6 | H6 | H6 | H6 | C | C | C | C | → | C
FA_EECT | TRACE HEATING CIRCUIT | 0 |  |  |  |  | #N/A | #N/A | #N/A | #N/A | → | #N/A
FA_EEPBA | AIR CIRCUIT BREAKER | 868 | H6 | H6 | H6 | H6 | C | C | C | C | → | C | Least critical assumed
FA_EEPBV | VACUUM CIRCUIT BREAKER | 47 | F6 | H6 | F6 | H6 | B | C | B | C | → | B | Aligned to non-spare circuit code
FA_EEPCS | SACRIFICIAL ANODE | 5 | H5 | H5 | H5 | G5 | C | C | C | C | → | C
FA_EEPNE | EARTHING BAR | 118 | H6 | H6 | H6 | H6 | C | C | C | C | → | C
FA_EEPNN | NEUTRAL GROUND RESISTOR | 8 | F6 | H6 | F6 | G6 | B | C | B | B | → | B
FA_EEPS | START / STOP SWITCH | 171 | F6 | H6 | F6 | H6 | B | C | B | C | → | B
FA_EEPU | UNINTERRUPTIBLE POWER SUPPLY | 4 | E7 | H7 | F7 | F7 | A | C | A | A | → | A | D7 for safety changed to E7 to be within valid range
FA_EETA | REACTOR / INDUCTOR | 0 |  |  |  |  | #N/A | #N/A | #N/A | #N/A | → | #N/A
FA_EETB | BATTERY | 15 | E7 | H7 | F7 | F7 | A | C | A | A | → | A
FA_EETC | BATTERY CHARGER | 4 | E7 | H7 | F7 | F7 | A | C | A | A | → | A
FA_EETD | BUS DUCT / BUS BAR | 70 | F3 | H3 | F3 | G3 | C | C | C | C | → | C
FA_EETFW | WET TRANSFORMER | 20 | H4 | H4 | F4 | F4 | C | C | B | B | → | B
FA_EETGA | AC ELECTRIC GENERATOR | 10 | G5 | H5 | F5 | G5 | C | C | B | C | → | B
FA_EETI | ELECTRIC ISOLATOR | 9 | G6 | H6 | H6 | H6 | B | C | C | C | → | B
FA_EETM | MOTOR CONTROL CENTER | 910 | H6 | H6 | H6 | H6 | C | C | C | C | → | C
FA_EETO | POWER / CONTROL MODULE | 4 | F6 | H6 | F6 | H6 | B | C | B | C | → | B
FA_EETP | ELECTRICAL PANEL | 3 | E4 | H4 | F4 | F4 | B | C | B | B | → | B
FA_EETQ | VARIABLE FREQUENCY DRIVE | 0 |  |  |  |  | #N/A | #N/A | #N/A | #N/A | → | #N/A
FA_EETR | POWER RECTIFIER | 2 | H4 | H4 | F4 | F4 | C | C | B | B | → | B
FA_EETW | SWITCHGEAR | 140 | H6 | H6 | H6 | H6 | C | C | C | C | → | C
FA_EETY | POWER SUPPLY | 28 | G4 | H4 | G4 | H4 | C | C | C | C | → | C
FA_INAM | FLOW METER | 15 | H6 | H6 | G6 | H6 | C | C | B | C | → | B
FA_INAP | SAMPLER | 10 | H7 | H7 | H7 | G7 | C | C | C | B | → | B
FA_INDC | LOCAL CONTROLLER | 8 | H6 | H6 | F6 | H6 | C | C | B | C | → | B
FA_INDFD | DAMPER | 20 | E7 | H7 | H7 | G7 | A | C | C | B | → | A | Likelihood changed from 8 to 7 to be within valid range
FA_INDFS | SOLENOID VALVE | 204 | H6 | H6 | F6 | H6 | C | C | B | C | → | B
FA_INDI | INDICATOR | 1249 | H7 | H7 | H7 | H7 | C | C | C | C | → | C
FA_INDMS | SENSING ELEMENT | 1386 | H6 | H6 | F6 | H6 | C | C | B | C | → | B
FA_INDMT | TRANSMITTER | 2410 | H5 | H5 | F5 | H5 | C | C | B | C | → | B | Lowest critically selected here
FA_INDP | PRINTER / RECORDER | 0 |  |  |  |  | #N/A | #N/A | #N/A | #N/A | → | #N/A
FA_INDS | INSTRUMENT SWITCH | 1048 | H6 | H6 | H6 | H6 | C | C | C | C | → | C | Lowest critically selected here
FA_INDT | TRANSDUCER | 33 | H5 | H5 | F5 | H5 | C | C | B | C | → | B
FA_INSC | PLC PANEL | 8 | G7 | H7 | H7 | H7 | B | C | C | C | → | B
FA_INSD | DISTRIBUTED CONTROL PANEL | 0 |  |  |  |  | #N/A | #N/A | #N/A | #N/A | → | #N/A
FA_INSJ | JUNCTION BOX | 734 | F7 | H7 | H7 | H7 | A | C | C | C | → | A
FA_INSL | LOCAL CONTROL PANEL | 206 | H5 | H5 | H5 | H5 | C | C | C | C | → | C | Lowest critically selected here
FA_INSS | OPERATOR STATION | 3 | G7 | H7 | H7 | H7 | B | C | C | C | → | B
FA_INST | TERMINATION RACK | 0 |  |  |  |  | #N/A | #N/A | #N/A | #N/A | → | #N/A
FA_INSY | SAFETY INSTRUMENT SYSTEM PANEL | 19 | E7 | H7 | G7 | G7 | A | C | B | B | → | A
FA_PEA | SELF-ACTUATING VALVE | 125 | H5 | H5 | G5 | G5 | C | C | C | C | → | C | Lowest critically selected here
FA_PEG | PIPING | 11224 | G4 | H4 | G4 | G4 | C | C | C | C | → | C | Based on least critical pipework by default
FA_PEL | PIG LAUNCHER / RECEIVER | 2 | H5 | H5 | E5 | F5 | C | C | A | B | → | A
FA_PEM | MANIFOLD | 134 | H4 | H4 | F4 | G4 | C | C | B | C | → | B
FA_PEO | RESTRICTIVE ORIFICE | 351 | H4 | H4 | H4 | H4 | C | C | C | C | → | C | Lowest critically selected here
FA_PESC | CONVENTIONAL PRESSURE SAFETY VALVE | 502 | E5 | F5 | F5 | H5 | A | B | B | C | → | A
FA_PESR | RUPTURE DISC | 49 | E5 | F5 | F5 | H5 | A | B | B | C | → | A
FA_PESV | VACUUM RELIEF PRESSURE SAFETY VALVE | 15 | E5 | F5 | F5 | H5 | A | B | B | C | → | A
FA_PET | THERMOWELL | 363 | E5 | H5 | F5 | H5 | A | C | B | C | → | A | Arguably high, reviewed example on a SIL
FA_PEVB | BALL VALVE | 5535 | G5 | G5 | G5 | H5 | C | C | C | C | → | C | Lowest critically selected here
FA_PEVC | CHECK VALVE | 1013 | G5 | G5 | G5 | H5 | C | C | C | C | → | C | Lowest critically selected here
FA_PEVD | DIAPHRAGM VALVE | 3 | G5 | G5 | G5 | H5 | C | C | C | C | → | C
FA_PEVG | GATE VALVE | 2331 | G5 | G5 | G5 | H5 | C | C | C | C | → | C | Lowest criticality selected here
FA_PEVL | GLOBE VALVE | 814 | G5 | G5 | G5 | H5 | C | C | C | C | → | C | Lowest criticality selected here
FA_PEVM | MULTIPLE ORIFICE VALVE | 9 | G6 | G6 | G6 | H6 | B | B | B | C | → | B
FA_PEVN | NEEDLE VALVE | 73 | H5 | H5 | H5 | H5 | C | C | C | C | → | C
FA_PEVX | DIVERTER VALVE | 4 | E5 | F5 | F5 | F5 | A | B | B | B | → | A
FA_PEVY | BUTTERFLY VALVE | 65 | G6 | G6 | G6 | H6 | B | B | B | C | → | B
FA_REBC | BLOWER, CENTRIFUGAL | 4 | E7 | H7 | G7 | G7 | A | C | B | B | → | A | D safety risk reset to E to be within valid range
FA_REC | CENTRIFUGE | 4 | G7 | H7 | G7 | G7 | B | C | B | B | → | B
FA_REDH | HYDRAULIC MOTOR | 6 | G7 | G7 | G7 | H7 | B | B | B | C | → | B
FA_REDP | PNEUMATIC MOTOR | 11 | G7 | G7 | G7 | H7 | B | B | B | C | → | B
FA_REEL | LIQUID FUEL COMBUSTION ENGINE | 4 | E7 | H7 | E7 | G7 | A | C | A | B | → | A | D safety risk reset to E to be within valid range
FA_REFA | AXIAL FAN | 21 | E7 | G7 | F7 | F7 | A | B | A | A | → | A
FA_REFC | CENTRIFUGAL FAN | 121 | G7 | H7 | G7 | G7 | B | C | B | B | → | B
FA_REMC | CENTRIFUGAL COMPRESSOR | 3 | G6 | G6 | F6 | F6 | B | B | B | B | → | B
FA_REMR | RECIPROCATING COMPRESSOR | 6 | G6 | G6 | E6 | F6 | B | B | A | B | → | A
FA_REMT | ROTARY COMPRESSOR | 11 | G6 | G6 | F6 | F6 | B | B | B | B | → | B
FA_RENG | GAS TURBINE | 8 | F7 | G7 | E7 | F7 | A | B | A | A | → | A
FA_REPC | CENTRIFUGAL PUMP | 250 | H7 | H7 | G7 | G7 | C | C | B | B | → | B | Lowest criticality that wasn't a warehouse spare
FA_REPD | POSITIVE DISPLACEMENT PUMP | 12 | G6 | G6 | F6 | F6 | B | B | B | B | → | B
FA_RER | RAKE / SCRAPER | 2 | G6 | G6 | G6 | G6 | B | B | B | B | → | B
FA_RETG | GEARBOX | 0 | H6 | H6 | F6 | H6 | C | C | B | C | → | B
FA_RETP | COUPLING | 5 | F6 | H6 | F6 | H6 | B | C | B | C | → | B
FA_REUC | CHEMICAL INJECTION SYSTEM | 0 | H7 | H7 | G7 | G7 | C | C | B | B | → | B
FA_SEC | CYCLONE | 6 | H5 | G5 | G5 | G5 | C | C | C | C | → | C
FA_SEE | EJECTOR / EDUCTOR | 0 |  |  |  |  | #N/A | #N/A | #N/A | #N/A | → | #N/A
FA_SEFB | BASKET STRAINER FILTER | 275 | H7 | H7 | H7 | H7 | C | C | C | C | → | C | Lowest critically selected here
FA_SEFE | ELEMENT FILTER | 186 | H7 | H7 | H7 | H7 | C | C | C | C | → | C | Lowest critically selected here
FA_SEFS | SCREEN FILTER | 18 | H7 | H7 | H7 | H7 | C | C | C | C | → | C | Lowest critically selected here
FA_SEHF | FINNED COIL HEAT EXCHANGER | 65 | H5 | H5 | F5 | H5 | C | C | B | C | → | B
FA_SEHS | SPIRAL HEAT EXCHANGER | 46 | H5 | H5 | F5 | H5 | C | C | B | C | → | B
FA_SEHT | SHELL & TUBE HEAT EXCHANGER | 48 | G5 | H5 | G5 | G5 | C | C | C | C | → | C | Lowest critically selected here
FA_SEL | FLAME ARRESTOR | 42 | E5 | H5 | H5 | H5 | A | C | C | C | → | A
FA_SEM | FLARE | 4 | E5 | G5 | E5 | F5 | A | C | A | B | → | A
FA_SENF | FIRED HEATER FURNACE | 5 | H5 | G5 | F5 | G5 | C | C | B | C | → | B
FA_SEPA | ACCUMULATOR | 62 | E5 | H5 | H5 | G5 | A | C | C | C | → | A
FA_SEPC | CYLINDER | 59 | H5 | H5 | H5 | G5 | C | C | C | C | → | C | Lowest critically selected here
FA_SEPHC | CONDENSER VESSEL | 2 | H5 | H5 | F5 | G5 | C | C | B | C | → | B
FA_SEPHS | SEPARATOR VESSEL | 157 | H5 | H5 | G5 | G5 | C | C | C | C | → | C
FA_SES | PULSATION DAMPENER | 72 | G5 | H5 | G5 | H5 | C | C | C | C | → | C
FA_SETAC | CLOSED ROOF ATMOSPHERIC TANK | 59 | H5 | H5 | G5 | G5 | C | C | C | C | → | C
FA_SETAP | PIT / SUMP | 38 | H5 | G5 | G5 | G5 | C | C | C | C | → | C | Lowest critically selected here
FA_SETPC | CYLINDRICAL PRESSURISED TANK | 11 | E5 | H5 | G5 | F5 | A | C | C | B | → | A | D safety risk reset to E to be within valid range
FA_SEZ | SILENCER / MUFFLER | 63 | H5 | G5 | H5 | H5 | C | C | C | C | → | C
FA_SQFC | EQUIPMENT CABINET | 21 | E4 | H4 | H4 | H4 | B | C | C | C | → | B
FA_SQFDF | FLAME DETECTOR | 375 | F7 | H7 | H7 | H7 | A | C | C | C | → | A | Lowest critically selected here
FA_SQFDG | FIXED GAS DETECTOR | 628 | F7 | H7 | H7 | H7 | A | C | C | C | → | A
FA_SQFDS | SMOKE DETECTOR | 36 | F7 | H7 | H7 | H7 | A | C | C | C | → | A
FA_SQFFD | FIREWATER DELUGE SYSTEM | 17 | E7 | H7 | F7 | F7 | A | C | A | A | → | A | D safety risk reset to E to be within valid range
FA_SQFFH | FIRE HOSE | 3 | E7 | H7 | H7 | F7 | A | C | C | A | → | A | D safety risk reset to E to be within valid range
FA_SQFFM | FIRE WATER/FOAM MONITOR | 19 | E6 | H6 | H6 | H6 | A | C | C | C | → | A | D safety risk reset to E to be within valid range
FA_SQFFY | FIRE HYDRANT | 109 | E5 | H5 | H5 | F5 | A | C | C | B | → | A | D safety risk reset to E to be within valid range
FA_SQFRA | EMERGENCY ALARM DEVICE | 175 | F7 | H7 | H7 | H7 | A | C | C | C | → | A
FA_SQFRE | SAFETY SHOWER OR EYE BATH | 18 | E5 | H5 | H5 | H5 | A | C | C | C | → | A
FA_SQMT | MAINTENANCE TOOL | 2 | H7 | H7 | H7 | H7 | C | C | C | C | → | C
FA_SQTA | PUBLIC ADDRESS AND ALARM SYSTEM | 34 | F7 | H7 | H7 | H7 | A | C | C | C | → | A
FA_SQTB | NON DIRECTIONAL BEACON | 97 | F7 | H7 | H7 | H7 | A | C | C | C | → | A
FA_SQTE | TELECOMMUNICATION CABINET | 16 | E7 | H7 | H7 | G7 | A | C | C | B | → | A
FA_SQTH | PATCH PANEL | 0 |  |  |  |  | #N/A | #N/A | #N/A | #N/A | → | #N/A
FA_SQTL | LOUDSPEAKER | 294 | E7 | H7 | H7 | G7 | A | C | C | B | → | A
FA_SQTN | ANTENNA | 0 |  |  |  |  | #N/A | #N/A | #N/A | #N/A | → | #N/A
FA_SQTOF | FIXED RADIO | 2 | E7 | H7 | G7 | G7 | A | C | B | B | → | A | D safety risk reset to E to be within valid range
FA_SQTP | COMPUTER PERIPHERAL | 104 | H7 | H7 | H7 | H7 | C | C | C | C | → | C
FA_SQTS | TELEPHONE OR MULTIMEDIA EQUIPMENT | 78 | E7 | H7 | H7 | G7 | A | C | C | B | → | A
FA_SQTV | CCTV CAMERA UNIT | 101 | H7 | H7 | H7 | H7 | C | C | C | C | → | C
FA_SQTW | WIRELESS COMMUNICATION OR CONTROL EQUIPMENT | 17 | E7 | H7 | G7 | H7 | A | C | B | C | → | A
FA_SQTY | RECEIVER / TRANSMITTER | 4 | E7 | H7 | G7 | G7 | A | C | B | B | → | A | 8 Likelihood reset to 7 to sit in valid range
FA_SYLH | SYSTEM LEVEL HIERARCHY | 313 | E7 | E7 | E7 | E7 | A | A | A | A | → | A
FA_WECO | OVERHEAD CRANE | 0 |  |  |  |  | #N/A | #N/A | #N/A | #N/A | → | #N/A
FA_WEHY | CONVEYOR | 2 | H6 | H6 | H6 | G6 | C | C | C | B | → | B
Note on F4: Financial
Note on G4: Non-Financial

## Systems
0
Reference Data from ASSET-C | [5 empty] | INPUT FIELDS |  |  |  | Calculated / Output Fields | [6 empty] | 0
Functional location | Function Location Description | System No | Tag Abbreviation | Utilities System YorN | Comment | S | E | P | B | Criticality S | Criticality E | Criticality P | Criticality B | Leading to | Criticality Overall | Notes on Criticality Selection
E-SYSTEM-00 | GENERAL / NON SPECIFIC SYSTEM SYS 00 | 00 | SYS | N |  | H3 | H3 | H3 | H3 | C | C | C | C | → | C | Notes on approach to assessment. Based on initial discussion, GF & R are treated as a single unit, i.e. there is no attempt to split out events into GF and R having different impact levels on either asset. Therefore a common production rate figure is used based on combined production levels of $1million per day shutdown of Raven, $200,000 per day shutdown of GF, i.e. all asessment is based on $1.2M/day of loss. Put another way, a system event is treated as affecting both sites and common production. Loss of a system is considered largely in terms of its primary function / objective, so production focussed systems are not treated as having a safety function, and are assumed to generate a safe shutdown when losing their primary function. e.g. Loss of reception facilites function causes loss of production but has no direct safety impact. Loss of a safety system (e.g. firewater) is considered as having a safety impact and may also have a knock-on production impact if unavailable
E-SYSTEM-01 | RESERVED FOR SUBSEA USE | 01 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed | 0
E-SYSTEM-02 | RESERVED FOR SUBSEA USE | 02 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-03 | RESERVED FOR SUBSEA USE | 03 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-04 | RESERVED FOR SUBSEA USE | 04 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-05 | CONTROL UMBILICALS AND HPU SYS 05 | 05 | SYS | N |  | H3 | H3 | H3 | H3 | C | C | C | C | → | C | Not assessed
E-SYSTEM-06 | RESERVED FOR SUBSEA USE | 06 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-07 | RESERVED FOR SUBSEA USE | 07 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-08 | RESERVED FOR SUBSEA USE | 08 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-09 | RESERVED FOR SUBSEA USE | 09 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-10 | RESERVED FOR SUBSEA USE | 10 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-11 | RESERVED FOR SUBSEA USE | 11 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-12 | RESERVED FOR SUBSEA USE | 12 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-13 | SUBSEA - WELLHEAD AND TEST SEPARATOR | 13 | SYS | N |  | H3 | H3 | H3 | H3 | C | C | C | C | → | C | Not assessed
E-SYSTEM-14 | RESERVED FOR SUBSEA USE | 14 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-15 | RESERVED FOR SUBSEA USE | 15 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-16 | RESERVED FOR SUBSEA USE | 16 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-17 | RESERVED FOR SUBSEA USE | 17 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-18 | RESERVED FOR SUBSEA USE | 18 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-19 | RESERVED FOR SUBSEA USE | 19 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-20 | PROCESS SEPARATION SYS 20 | 20 | SYS | N |  | H7 | H7 | F7 | G7 | C | C | A | B | → | A | Loss of system primary function = no production feed into rest of system, loss of production output. Safety - minimal impact on assumption of safe shutdown Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen multiple times in life of facility (7)
E-SYSTEM-21 | PROCESS CONDENSATE HANDLING SYS 21 | 21 | SYS | N |  | H7 | H7 | F7 | G7 | C | C | A | B | → | A | Loss of system primary function = no production feed into rest of system, loss of production output. Safety - minimal impact on assumption of safe shutdown Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen multiple times in life of facility (7)
E-SYSTEM-22 | PROCESS RECEPTION SYS 22 | 22 | SYS | N |  | H7 | H7 | F7 | G7 | C | C | A | B | → | A | Loss of system primary function = no production feed into rest of system, loss of production output. Safety - minimal impact on assumption of safe shutdown Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen multiple times in life of facility (7)
E-SYSTEM-23 | PROCESS COMPRESSION MAIN | 23 | SYS | N |  | H7 | H7 | F7 | G7 | C | C | A | B | → | A | Loss of system primary function = no production feed into rest of system, loss of production output. Safety - minimal impact on assumption of safe shutdown Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen multiple times in life of facility (7)
E-SYSTEM-24 | FLASH GAS COMPRESSION SYS 24 | 24 | SYS | N |  | H7 | H7 | F7 | G7 | C | C | A | B | → | A | Loss of system primary function = no production feed into rest of system, loss of production output. Safety - minimal impact on assumption of safe shutdown Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen multiple times in life of facility (7)
E-SYSTEM-25 | GAS TREATMENT SYS 25 | 25 | SYS | N |  | H7 | H7 | F7 | G7 | C | C | A | B | → | A | Loss of system primary function = no production feed into rest of system, loss of production output. Safety - minimal impact on assumption of safe shutdown Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen multiple times in life of facility (7)
E-SYSTEM-26 | RESERVED FOR ONSHORE USE | 26 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-27 | GAS EXPORT SYS 27 | 27 | SYS | N |  | H7 | H7 | F7 | G7 | C | C | A | B | → | A | Loss of system primary function = no production feed into rest of system, loss of production output. Safety - minimal impact on assumption of safe shutdown Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen multiple times in life of facility (7)
E-SYSTEM-28 | RICH MEG SYS 28 | 28 | SYS | N |  | H7 | H7 | F7 | G7 | C | C | A | B | → | A | Loss of system primary function = unable to meet export gas spec leading to shutdown of production Safety - minimal impact on assumption of safe shutdown Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen multiple times in life of facility (7)
E-SYSTEM-29 | LEAN MEG SYS 29 | 29 | SYS | N |  | H7 | H7 | F7 | G7 | C | C | A | B | → | A | Loss of system primary function = unable to meet export gas spec leading to shutdown of production Safety - minimal impact on assumption of safe shutdown Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen multiple times in life of facility (7)
E-SYSTEM-30 | MEG REGENERATION SYS 30 | 30 | SYS | N |  | H7 | H7 | F7 | G7 | C | C | A | B | → | A | Loss of system primary function = unable to meet export gas spec leading to shutdown of production Safety - minimal impact on assumption of safe shutdown Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen multiple times in life of facility (7)
E-SYSTEM-31 | RESERVED FOR ONSHORE USE | 31 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-32 | RESERVED FOR ONSHORE USE | 32 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-33 | RESERVED FOR ONSHORE USE | 33 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-34 | RESERVED FOR ONSHORE USE | 34 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-35 | RESERVED FOR ONSHORE USE | 35 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-36 | RESERVED FOR ONSHORE USE | 36 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-37 | RESERVED FOR ONSHORE USE | 37 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-38 | RESERVED FOR ONSHORE USE | 38 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-39 | RESERVED FOR ONSHORE USE | 39 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-40 | LP FUEL GAS SYS 40 | 40 | SYS | N |  | E4 | H7 | F7 | G7 | B | C | A | B | → | A | Loss of system primary function = loss of main power generation cascading to production shutdown. Safety - Loss of fuel gas blanking in drains treatment, leading to explosion/fire 1-2 death potential at lower probability Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen multiple times in life of facility (7)
E-SYSTEM-41 | PROCESS - HP WET FLARE | 41 | SYS | N |  | E6 | H6 | F6 | F6 | A | C | B | B | → | A | Loss of system primary function = loss of main power generation cascading to production shutdown. Safety - Loss of fuel gas blanking in drains treatment, leading to explosion/fire 1-2 death potential at lower probability Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - short term diversion of senior management to manage issue/event Likelihood - considered likely to happen once or twice in life of facility (7)
E-SYSTEM-42 | PROCESS - HP FLARE | 42 | SYS | N |  | E6 | H6 | F6 | F6 | A | C | B | B | → | A | Loss of system primary function = loss of main power generation cascading to production shutdown. Safety - Loss of fuel gas blanking in drains treatment, leading to explosion/fire 1-2 death potential at lower probability Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - short term diversion of senior management to manage issue/event Likelihood - considered likely to happen once or twice in life of facility (7)
E-SYSTEM-43 | PROCESS - VENT AND BLOW DOWN | 43 | SYS | N |  | E6 | H6 | F6 | F6 | A | C | B | B | → | A | Loss of system primary function = loss of main power generation cascading to production shutdown. Safety - Loss of fuel gas blanking in drains treatment, leading to explosion/fire 1-2 death potential at lower probability Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - short term diversion of senior management to manage issue/event Likelihood - considered likely to happen once or twice in life of facility (7)
E-SYSTEM-44 | PROCESS - LP FLARE | 44 | SYS | N |  | E6 | H6 | F6 | F6 | A | C | B | B | → | A | Loss of system primary function = loss of main power generation cascading to production shutdown. Safety - Loss of fuel gas blanking in drains treatment, leading to explosion/fire 1-2 death potential at lower probability Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - short term diversion of senior management to manage issue/event Likelihood - considered likely to happen once or twice in life of facility (7)
E-SYSTEM-45 | UTILITIES - FUEL GAS | 45 | SYS | N |  | E4 | H7 | F7 | G7 | B | C | A | B | → | A | Loss of system primary function = loss of main power generation cascading to production shutdown. Safety - Loss of fuel gas blanking in drains treatment, leading to explosion/fire 1-2 death potential at lower probability Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen multiple times in life of facility (7)
E-SYSTEM-46 | UTILITIES - FUEL GAS HP | 46 | SYS | N |  | E4 | H7 | F7 | G7 | B | C | A | B | → | A | Loss of system primary function = loss of main power generation cascading to production shutdown. Safety - Loss of fuel gas blanking in drains treatment, leading to explosion/fire 1-2 death potential at lower probability Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen multiple times in life of facility (7)
E-SYSTEM-47 | CHEMICALS - METHANOL INJECTION | 47 | SYS | N |  | H5 | H5 | E5 | F5 | C | C | A | B | → | A | Loss of system primary function = unable ot maintain hydrate free flow leading to blockage, reduce production flow and or shutdown and loss of flowline(s) Safety - Assumed mininmal impact Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of weeks/months equivalent to fully recover from an event @ $400k/day, => impact level E range Business - Mid term diversion of local management to manage issue/event Likelihood - considered unlikely but could occur in lifetime of 10 similar facilities (5)
E-SYSTEM-48 | CHEMICALS - CORROSION INHIBITOR INJECTION | 48 | SYS | N |  | H5 | H5 | E5 | F5 | C | C | A | B | → | A | Loss of system primary function = Premature internal corrosion of process piepline eventually requiring pipework replacement or removal from service impacting production Safety - Assumed mininmal impact, RBI inspection prevents any LOPC. Environment - minimal impact on assumption of safe shutdown before LOPC Production - $1.2M per day shutdown, assumption of weeks/months equivalent to fully recover from an event @ $400k/day, => impact level E range Business - Mid term diversion of local management to manage issue/event Likelihood - considered unlikely but could occur in lifetime of 10 similar facilities (5)
E-SYSTEM-49 | CHEMICALS - KINETIC INHIBITOR INJECTION | 49 | SYS | N |  | H5 | H5 | E5 | F5 | C | C | A | B | → | A | Loss of system primary function = assumed similar to corrosion inhibitor Safety - Assumed mininmal impact, RBI inspection prevents any LOPC. Environment - minimal impact on assumption of safe shutdown before LOPC Production - $1.2M per day shutdown, assumption of weeks/months equivalent to fully recover from an event @ $400k/day, => impact level E range Business - Mid term diversion of local management to manage issue/event Likelihood - considered unlikely but could occur in lifetime of 10 similar facilities (5)
E-SYSTEM-50 | CHEMICALS - REVERSE EMULSION BREAKER | 50 | SYS | N |  | H5 | H5 | F5 | G5 | C | C | B | C | → | B | Loss of system primary function = reduced throughput through slower separation (no reference documentation found to understand this one) Safety - Assumed mininmal impact. Environment - minimal impact on assumption of safe shutdown before discharge of out of spec fluids. Production - $1.2M per day shutdown, assumption of 8 hours to recover from an incident ($400k), => impact level F range Business - Mid term diversion of local management to manage issue/event Likelihood - considered unlikely but could occur in lifetime of 10 similar facilities (5)
E-SYSTEM-51 | CHEMICAL INJECTION SYS 51 | 51 | SYS | N |  | H5 | H5 | F5 | G5 | C | C | B | C | → | B | Loss of system primary function = reduced throughput through slower separation Safety - Assumed mininmal impact. Environment - minimal impact on assumption of safe shutdown before discharge of out of spec fluids. Production - $1.2M per day shutdown, assumption of 8 hours to recover from an incident ($400k), => impact level F range Business - Mid term diversion of local management to manage issue/event Likelihood - considered unlikely but could occur in lifetime of 10 similar facilities (5)
E-SYSTEM-52 | MEG CHEMICAL INJECTION SYS 52 | 52 | SYS | N |  | H5 | H5 | F5 | G5 | C | C | B | C | → | B | Loss of system primary function = reduced throughput through slower separation Safety - Assumed mininmal impact. Environment - minimal impact on assumption of safe shutdown before discharge of out of spec fluids. Production - $1.2M per day shutdown, assumption of 8 hours to recover from an incident ($400k), => impact level F range Business - Mid term diversion of local management to manage issue/event Likelihood - considered unlikely but could occur in lifetime of 10 similar facilities (5)
E-SYSTEM-53 | POTABLE WATER SYS 53 | 53 | SYS | Y |  | F6 | H6 | G6 | H6 | B | C | B | C | → | B | Loss of system primary function = lack of potable water to systems demand (tankered supply). Loss of supply to chemicals / slurry dilution, and water seal on LP flare stack. Safety - Assumed mininmal impact rom potable in isolation (drinking supplies will be bottled water) BUT supplies safety showers which would become unavailable. Environment - minimal impact on assumption of safe shutdown before discharge of out of spec fluids. Production - $1.2M per day shutdown, assumption of 8 hours to recover from an incident ($400k), => impact level G range Business - Mid term diversion of local management to manage issue/event Likelihood - considered could occur once or twice in lifetime of facility (6)
E-SYSTEM-54 | UTILITY WATER SYS 54 | 54 | SYS | Y |  | E6 | H6 | G6 | H6 | A | C | B | C | → | A | Loss of system primary function = Utility water tank also supplies firewater. Safety - Loss of firewater cover, potential for multiple fatalities. Environment - minimal impact on assumption of safe shutdown before discharge of out of spec fluids. Production - $1.2M per day shutdown, assumption of 8 hours to recover from an incident ($400k), => impact level G range Business - Mid term diversion of local management to manage issue/event Likelihood - considered could occur once or twice in lifetime of facility (5)
E-SYSTEM-55 | CHEMICALS - MISCELLANEOUS | 55 | SYS | N |  | H6 | H6 | G6 | G6 | C | C | B | B | → | B | Loss of system primary function = Utility water tank also supplies firewater. Safety - Assume safe shutdown and no loss of containment. Environment - Release of chemicals within local environment, unlikelt to spread offsite. Production - $1.2M per day shutdown, assumption of 6 hours to recover from an incident ($300k), => impact level G range Business - Mid term diversion of local management to manage issue/event Likelihood - considered could occur once or twice in lifetime of facility (6)
E-SYSTEM-56 | DRAINS - HAZARDOUS OPEN SYS 56 | 56 | SYS | N |  | G6 | H6 | G6 | G6 | B | C | B | B | → | B | Loss of system primary function = no safe route for contaminated water/ fluids Safety - Assume medium impact incident with personnel exposed to health effects. G Environment - Release of contaminated water within local environment, unlikely to spread offsite. - H Production - $1.2M per day shutdown, assumption of 6 hours to recover from an incident ($300k), => impact level G range Business - Mid term diversion of local management to manage issue/event Likelihood - considered could occur once or twice in lifetime of facility (6)
E-SYSTEM-57 | CLOSED DRAINS SYS 57 | 57 | SYS | N |  | E5 | G5 | F5 | G5 | A | C | B | C | → | A | Loss of system primary function = no safe disposal route for hazardous fluids Safety - Potential for gas release and explosion / fire with 1-2 fatalities E Environment - LOPC within local environment, unlikely to spread offsite. - G Production - $1.2M per day shutdown, assumption of 24 hours to recover from an incident ($1.2M), => impact level F range Business - Mid term diversion of local management to manage issue/event Likelihood - considered could occur in lifetime of 10 similar facilities (5)
E-SYSTEM-58 | NON-HAZARDOUS OPEN DRAINS SYS 58 | 58 | SYS | Y |  | G5 | H5 | G5 | H5 | C | C | C | C | → | C | Loss of system primary function = no safe disposal route for surface water Safety - medium level health/safety incident (slip/trip) - G Environment - <inimal impact, unlikely to spread offsite. - H Production - $1.2M per day shutdown, assumption of 4 hours to recover from an incident ($0.3M), => impact level G range Business - Mid term diversion of local management to manage issue/event Likelihood - considered could occur once or twice in lifetime of 10 facilities (5)
E-SYSTEM-59 | SANITARY WATER SYS 59 | 59 | SYS | Y |  | F6 | H6 | H6 | H6 | B | C | C | C | → | B | Copied from potable water Loss of system primary function = lack of potable water to systems demand (tankered supply). Loss of supply to chemicals / slurry dilution, and water seal on LP flare stack. Safety - Assumed mininmal impact rom potable in isolation (drinking supplies will be bottled water) BUT supplies safety showers which would become unavailable. Environment - minimal impact on assumption of safe shutdown before discharge of out of spec fluids. Production -Assumed no impact Business - Mid term diversion of local management to manage issue/event Likelihood - considered could occur once or twice in lifetime of facility (6)
E-SYSTEM-60 | HOT OIL SYS 60 | 60 | SYS | N |  | H7 | H7 | F7 | G7 | C | C | A | B | → | A | Loss of system primary function = loss of process heating where required leading to reduced throughput and/or shutdown of production Safety - assume safe shutdown, no safety impact, no loss of hot oil containment - H Environment - minimal impact on assumption of safe shutdown / no loss of oil to environment - H Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen multiple times in life of facility (7) (thermal cycling contributing to long term unreliability)
E-SYSTEM-61 | OXYGEN SCAVENGER SYS 61 | 61 | SYS | N |  | H6 | H6 | F6 | G6 | C | C | B | B | → | B | Loss of system primary function = unable to scavenge oxygen in MEG system, leading to off spec export gas and fines / reduced value of exports Safety - assume safe shutdown, no safety impact, no loss of scavenger containment - H Environment - minimal impact on assumption of safe shutdown - H Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen once or twice in life of facility (6)
E-SYSTEM-62 | DIESEL SYS 62 | 62 | SYS | N |  | E6 | H6 | F6 | G6 | A | C | B | B | → | A | Loss of system primary function = loss of diesel supply to day tanks including diesel driven firepumps, leading to eventual loss of firepump cover and essential / emrgency generation Safety - Eventual loss of firepump cover, E ( cascading to production shutdown.) Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $600k = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen once or twice in life of facility (6) (full escalation unlikely with use of temporary tanker supplies hoses if required?)
E-SYSTEM-63 | INSTRUMENT AIR SYS 63 | 63 | SYS | Y |  | E5 | H6 | F6 | G6 | A | C | B | B | → | A | Loss of system primary function = safe shutdown of multiple systems on loss of instrument air Safety - Minimal impact unless considering failure of pressure containment in system (e.g. missiling failed fitting), as a low probability event Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 24 hours to fully recover from an event, $1.2M = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen once or twice in life of facility (6)
E-SYSTEM-64 | INERT GAS SYS 64 | 64 | SYS | Y |  | E5 | H6 | F6 | G6 | A | C | B | B | → | A | Loss of system primary function = loss of inerting blanket in tanks Safety - potential to create explosive atmophere in tank voids, with explosion/fire risk on ignition. E Environment - minimal impact on assumption of safe shutdown, asphyxiation risk on loss of containment in confied spaces Production - $1.2M per day shutdown, assumption of 24 hours to fully recover from an event, $1.2M = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen once or twice in life of facility (6), potential to mitigate with temporary tankered / bottled supplies
E-SYSTEM-65 | PLANT/UTILITY AIR SYS 65 | 65 | SYS | Y |  | E5 | H6 | F6 | G6 | A | C | B | B | → | A | Copied form instrument air Loss of system primary function = safe shutdown of multiple systems on loss of instrument air Safety - Minimal impact unless considering failure of pressure containment in system (e.g. missiling failed fitting), as a low probability event Environment - minimal impact on assumption of safe shutdown Production - $1.2M per day shutdown, assumption of 24 hours to fully recover from an event, $1.2M = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen once or twice in life of facility (6)
E-SYSTEM-66 | THERMAL OXIDIZER SYS 66 | 66 | SYS | N |  | H6 | F6 | F6 | G6 | C | B | B | B | → | B | Loss of system primary function = loss of disposal route for combustible hazardous gases Safety - Assume safe shutdown / safe venting / dilution route if thermal oxidiser unavailalbe. H Environment - Assume likely to exceed permitted plant emissions of e.g. H2S. - F Production - $1.2M per day shutdown, assumption of 24 hours to fully recover from an event, $1.2M = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen once or twice in life of facility (6)
E-SYSTEM-67 | PRODUCED WATER SYS 67 | 67 | SYS | N |  | H6 | H6 | F6 | G6 | C | C | B | B | → | B | Loss of system primary function = unable to process produced water and route for disposal by tanker Safety - Assume safe shutdown on high levels in produced water tanks/drums. H Environment - Minimal, assuming shutdown and no tank overflow / loss of containments - H Production - $1.2M per day shutdown, assumption of 24 hours to fully recover from an event, $1.2M = impact level F Business - Mid term diversion of local management to manage issue/event Likelihood - considered likely to happen once or twice in life of facility (6)
E-SYSTEM-68 | RESERVED FOR ONSHORE USE | 68 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-69 | RESERVED FOR ONSHORE USE | 69 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-70 | RESERVED FOR ONSHORE USE | 70 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-71 | RESERVED FOR ONSHORE USE | 71 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-72 | RESERVED FOR ONSHORE USE | 72 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-73 | RESERVED FOR ONSHORE USE | 73 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-74 | RESERVED FOR ONSHORE USE | 74 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-75 | RESERVED FOR ONSHORE USE | 75 | SYS | N | System Not in Use | H3 | H3 | H3 | H3 | C | C | C | C |  | C | Not assessed
E-SYSTEM-76 | ICSS - PROCESS AUTOMATION SYSTEM | 76 | SYS | N |  | H7 | H7 | G7 | H7 | C | C | B | C | → | B | Loss of system primary function = process trip and plant shutdown, reset, faultfinding and restart. Safety - Assume safe shutdown from safety instrumented system / failsafe behaviour. H Environment - Minimal, assuming shutdown and no tank overflow / loss of containments - H Production - $1.2M per day shutdown, assumption of 8 hours to fully recover from an event, $0.4M = impact level G Business - short term diversion of local management to manage issue/event Likelihood - considered likely to happen several times in life of facility (7)
E-SYSTEM-77 | ICSS - SAFETY INSTRUMENTED SYSTEM ESD | 77 | SYS | N |  | E5 | G5 | F5 | G5 | A | C | B | C | → | A | Loss of system primary function = undetected loss of protection layer / shutdown, with potential for escalating event Safety - potential for explosion, fire, multiple fatalities - E+ Environment - G Production - $1.2M per day shutdown, assumption of 48 hours to fully recover from an event, $2.4M = impact level F Business - short term diversion of local management to manage issue/event Likelihood - considered likely to happen in lifetime of 10 facilities (5)
E-SYSTEM-78 | FIRE AND GAS DETECTION | 78 | SYS | N |  | E5 | G5 | E5 | E5 | A | C | A | A | → | A | Loss of system primary function = undetected gas release and / or fire, leading to escalating incident Safety - potential for explosion, fire, multiple fatalities - E+ Environment - G Production - $1.2M per day shutdown, assumption of 168 hours to fully recover from an event, $8.4M = impact level E Business - mid term diversion of senior management to manage issue/event - E Likelihood - considered a similar event may have occurred within life of 10 facilities (5)
E-SYSTEM-79 | SAFETY - FIRE FIGHTING | 79 | SYS | N |  | E5 | G5 | F5 | G5 | A | C | B | C | → | A | Loss of system primary function = unable to fight any fire incident Safety - potential for explosion, fire, multiple fatalities - E+ Environment - G Production - $1.2M per day shutdown, assumption of 48 hours to fully recover from an event, $2.4M = impact level F Business - mid term diversion of local management to manage issue/event - G Likelihood - considered a similar event may have occurred within life of 10 facilities (5)
E-SYSTEM-80 | NORMAL POWER | 80 | SYS | N |  | H7 | H7 | F7 | G7 | C | C | A | B | → | A | Loss of system primary function = Shutdown of normal operations Safety -minimal impact on 'fail safe' power trip assumptions - H Environment - minimal impact assumed - H Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $0.6M = impact level F Business - short term diversion of local management to manage issue/event - H Likelihood - considered amay happen several times in facility lifetime (7)
E-SYSTEM-81 | FIRE WATER SYS 81 | 81 | SYS | N |  | E5 | G5 | F5 | G5 | A | C | B | C | → | A | Loss of system primary function = unable to use firewater in any fire incident Safety - potential for explosion, fire, multiple fatalities - E+ Environment - G Production - $1.2M per day shutdown, assumption of 12 hours to fully recover from an event, $0.6M = impact level F Business - mid term diversion of local management to manage issue/event - G Likelihood - considered a similar event may have occurred within life of 10 facilities (5)
E-SYSTEM-82 | UTILITIES - SEWAGE SYSTEM | 82 | SYS | Y |  | H5 | G5 | H5 | G5 | C | C | C | C | → | C | Loss of system primary function = unable to treat and dispose of foul water Safety - Low impact incidents - H Environment - G Production - Minimal impact on loss of system - H Business - short term diversion of local management to manage issue/event - G Likelihood - considered a similar event may have occurred within life of 10 facilities (5)
E-SYSTEM-83 | TELECOMS (GENERAL) | 83 | SYS | N |  | G6 | H6 | F6 | G6 | B | C | B | B | → | B | Loss of system primary function = unable to communicate within / off site, loss of control, Safety - No immediate effect in isolation - G Environment - No impact Production - Loss of production management information, potentially unmetered production leading to financial loss equivalento 24hrs production - $1.2M, - F Business - mid term diversion of local management to manage issue/event - G Likelihood - considered a similar event may once or twice in facility life(6)
E-SYSTEM-84 | ESSENTIAL POWER | 84 | SYS | N |  | H6 | H6 | F6 | G6 | C | C | B | B | → | B | Loss of system primary function = unable to start process systems leading to loss of production Safety - No immediate effect in isolation - H Environment - No impact Production -Unable to startup until resolved, assume 12hr loss planned production = $600k, F Business - mid term diversion of local management to manage issue/event - G Likelihood - considered a similar event may once or twice in facility life(6)
E-SYSTEM-85 | ESSENTIAL LIGTING AND SMALL POWER | 85 | SYS | N |  | H6 | H6 | G6 | G6 | C | C | B | B | → | B | Loss of system primary function = unable to start process systems leading to loss of production Safety - No immediate effect in isolation - H Environment - No impact Production - Constrianed personnel working, assume equivalent to 8hr loss production to resolve = $400k, G Business - mid term diversion of local management to manage issue/event - G Likelihood - considered a similar event may once or twice in facility life(6)
E-SYSTEM-86 | TRACE HEATING | 86 | SYS | N |  | H3 | H3 | H3 | H3 | C | C | C | C | → | C | Not assessed
E-SYSTEM-87 | EMERGENCY POWER | 87 | SYS | N |  | F6 | H6 | G6 | G6 | B | C | B | B | → | B | Loss of system primary function = no electrical power supply in emergency, loss of all non-battery backed emergency systems Safety - Reduced ability to manage incident - F Environment - No impact Production - Unable to operate without emergency power backup, 8hr loss production to resolve = $400k, G Business - mid term diversion of local management to manage issue/event - G Likelihood - considered a similar event may once or twice in facility life(6)
E-SYSTEM-88 | UPS POWER | 88 | SYS | N |  | F6 | H6 | G6 | G6 | B | C | B | B | → | B | Loss of system primary function = no electrical power supply in emergency, loss of all non-independent battery backed emergency systems. Safety - Reduced ability to manage incident - F Environment - No impact Production - Unable to operate without emergency power backup, 8hr loss production to resolve = $400k, G Business - mid term diversion of local management to manage issue/event - G Likelihood - considered a similar event may once or twice in facility life(6)
E-SYSTEM-89 | NORMAL LIGHTING AND SMALL POWER | 89 | SYS | N |  | H7 | H7 | F6 | G6 | C | C | B | B | → | B | Loss of system primary function = loss of normal lighting, constraining personnel operations Safety - may lead to medium impact incident, - G Environment - No impact Production - Constrained personnel working, assume equivalent to 8hr loss production to resolve = $400k, G Business - mid term diversion of local management to manage issue/event - G Likelihood - considered a similar event may occur several times in facility life(6)
E-SYSTEM-90 | EARTHING AND LIGHTING PROTECTION | 90 | SYS | N |  | E4 | H5 | G5 | H5 | B | C | C | C | → | B | Loss of system primary function = loss of normal earthing, lightning protection to earth. Safety - electric shock hazard, 1-2 fatality potential, with low likelihood - E Environment - No impact - H Production - no immediate impact, potential for equipment damage through unmitigated lightning strike, guestimate repair / replacement costs $100k - G Business - short term diversion of local management to manage issue/event - H Likelihood - considered a similar event may occur in lifetime of several facilities (5)
E-SYSTEM-91 | POWER - MAIN GENERATION SYS 91 | 91 | SYS | N |  | H7 | H7 | F7 | H7 | C | C | A | C | → | A | Loss of system primary function = loss of normal power supplies, escalating to production shutdown and restart Safety - minimal impact, momentary loss of lighting in some areas - H Environment - No impact - H Production - Production trip and restart / ramp-up costs estimated at equivalent to 12 hrs production $600k - F Business - short term diversion of local management to manage issue/event - H Likelihood - considered a similar event may several times in facility lifetime (7)
E-SYSTEM-92 | CATHODIC PROTECTION | 92 | SYS | N |  | H5 | H5 | F5 | G5 | C | C | B | C | → | B | Loss of system primary function = loss of cathodic protection to structures and containment leading to accelerated corrosion. Assume corrosion is found by RBI before structural collapse / loss of containment imminent. Safety - minimal impact short term - H Environment - No impact - H Production - Costs of premature replacement of equipment / structures, assumed in range F Business - mid term diversion of local management to manage issue/event - G Likelihood - considered a similar event may occur once in lifetime of several facilities(5)
E-SYSTEM-93 | POWER MANAGEMENT SYSTEM | 93 | SYS | N |  | H6 | H6 | F6 | H6 | C | C | B | C | → | B | Loss of system primary function = poor electrical load management, uncontrolled load shedding could escalate to loss of main power with plant shudown and loss of production Safety - minimal impact short term - H Environment - No impact - H Production - Treat as power trip - F Business - short term diversion of local management to manage issue/event - H Likelihood - considered a similar event may occur once or twice in lifetime of facility(6)
E-SYSTEM-94 | UTILITIES - HVAC | 94 | SYS | Y |  | E6 | H6 | F6 | H6 | A | C | B | C | → | A | Loss of system primary function = loss of HVAC Safety - loss of atmosphere control in control rooms / safe areas leaving them vulnerable to gas ingress in emergency situation. - E+ Environment - No impact - H Production - Potential for control equipment to operate outside temperature range leading to shutdown escalating to production trip and shutdown. - F Business - short term diversion of local management to manage issue/event - H Likelihood - considered a similar event may occur once or twice in lifetime of facility(6)
E-SYSTEM-95 | ACCESS CONTROL | 95 | SYS | N |  | E5 | H5 | H5 | H3 | A | C | C | C | → | A | Loss of system primary function = Loss of control of personnel access to site. Note - assuming this is not a barrier to unauthorised/hostile site access via any boundary. Safety - Loss of control of personnel on site leading to incomplete evacuation or inaccurate mustering, leading to 1-2 fatalities - E Environment - H Production - H Business - medium term diversion of local management to manage issue/event - G Likelihood - considered a similar event may occur once in lifetime of several facilities(5)
E-SYSTEM-96 | CCTV - SECURITY | 96 | SYS | N |  | H7 | H7 | H7 | H7 | C | C | C | C | → | C | Loss of system primary function = loss of remote visual surveillance of site Safety - minimal impact on immediate loss - H Environment - minimal impact, not substitutig for operator walk rounds - H Production - no immediate impact on loss - H Business - short term diversion of local management to manage issue/event - H Likelihood - considered a similar event may occur several time in lofe of facility(7)
E-SYSTEM-97 | LAN - VOIP | 97 | SYS | N |  | G7 | G7 | H7 | G7 | B | B | C | B | → | B | Loss of system primary function = loss of routine voice and data communications (assuming no impact on Process Automation System components) Safety - loss of some emergency co-ordination facilities, not an immediate problem unless coincident with incident. G Environment - may lose ability to track/record emissions for duration leading industry standards non-compliance G Production - no immediate impact on loss - H Business - medium term diversion of local management to manage issue/event - G Likelihood - considered a similar event may occur several time in life of facility (7)
E-SYSTEM-98 | PAGA | 98 | SYS | N |  | E6 | H6 | H6 | F6 | A | C | C | B | → | A | Loss of system primary function = loss of routine voice and data communications Safety - In the event of incident, unable to alert personnel and direct to place of safety - E+ Environment - minimal impact, H Production - No direct impact unless decision to shutdown for loss of PAGA. H Business - Short term diversion of Senior Management time to manage issue/event Likelihood - considered a similar event may occur once or twice in life of facility (6)
E-SYSTEM-99 | RADIO SYSTEMS (INCLUDING SAT COM) | 99 | SYS | N |  | H3 | H3 | H3 | H3 | C | C | C | C | → | C | Loss of system primary function = loss of routine voice and data communications Safety - In the event of incident, unable to alert personnel and direct to place of safety - E+ Environment - minimal impact, H Production - No direct impact unless decision to shutdown for loss of PAGA. H Business - Short term diversion of Senior Management time to manage issue/event Likelihood - considered a similar event may occur once or twice in life of facility (6)
| NO-SYSTEM | N/A |  |  |  | H3 | H3 | H3 | H3 | C | C | C | C | → | C | Not assessed
| BLANK-SYSTEM |  |  |  |  | H3 | H3 | H3 | H3 | C | C | C | C | → | C | Not assessed

## Sheet1
FA_CFBC | FA_CFBC
FA_CFSGA | FA_CFSGW
FA_CFSGW | FA_CFSSE
FA_CFSSE | FA_CFSSF
FA_CFSSF | FA_CFSST
FA_CFSST | FA_EECF
FA_EECF | FA_EECH
FA_EECH | FA_EECMD
FA_EECMD | FA_EECMI
FA_EECMI | FA_EECMS
FA_EECMS | FA_EECO
FA_EECO | FA_EEPBA
FA_EEPBA | FA_EEPBV
FA_EEPBV | FA_EEPCS
FA_EEPCS | FA_EEPNE
FA_EEPNE | FA_EEPNN
FA_EEPNN | FA_EEPS
FA_EEPS | FA_EEPU
FA_EEPU | FA_EETB
FA_EETB | FA_EETC
FA_EETC | FA_EETD
FA_EETD | FA_EETFW
FA_EETFW | FA_EETGA
FA_EETGA | FA_EETI
FA_EETI | FA_EETM
FA_EETM | FA_EETO
FA_EETO | FA_EETP
FA_EETP | FA_EETR
FA_EETR | FA_EETW
FA_EETW | FA_EETY
FA_EETY | FA_INAM
FA_INAM | FA_INAP
FA_INAP | FA_INDC
FA_INDC | FA_INDFD
FA_INDFD | FA_INDFS
FA_INDFS | FA_INDI
FA_INDI | FA_INDMS
FA_INDMS | FA_INDMT
FA_INDMT | FA_INDS
FA_INDS | FA_INDT
FA_INDT | FA_INSC
FA_INSC | FA_INSJ
FA_INSJ | FA_INSL
FA_INSL | FA_INSS
FA_INSS | FA_INSY
FA_INSY | FA_PEA
FA_PEA | FA_PEG
FA_PEG | FA_PEL
FA_PEL | FA_PEM
FA_PEM | FA_PEO
FA_PEO | FA_PESC
FA_PESC | FA_PESR
FA_PESR | FA_PESV
FA_PESV | FA_PET
FA_PET | FA_PEVB
FA_PEVB | FA_PEVC
FA_PEVC | FA_PEVD
FA_PEVD | FA_PEVG
FA_PEVG | FA_PEVL
FA_PEVL | FA_PEVM
FA_PEVM | FA_PEVN
FA_PEVN | FA_PEVX
FA_PEVX | FA_PEVY
FA_PEVY | FA_REBC
FA_REBC | FA_REC
FA_REC | FA_REDH
FA_REDH | FA_REDP
FA_REDP | FA_REEL
FA_REEL | FA_REFA
FA_REFA | FA_REFC
FA_REFC | FA_REMC
FA_REMC | FA_REMR
FA_REMR | FA_REMT
FA_REMT | FA_RENG
FA_RENG | FA_REPC
FA_REPC | FA_REPD
FA_REPD | FA_RER
FA_RER | FA_RETP
FA_RETG | FA_SEC
FA_RETP | FA_SEFB
FA_REUC | FA_SEFE
FA_SEC | FA_SEFS
FA_SEFB | FA_SEHF
FA_SEFE | FA_SEHS
FA_SEFS | FA_SEHT
FA_SEHF | FA_SEL
FA_SEHS | FA_SEM
FA_SEHT | FA_SENF
FA_SEL | FA_SEPA
FA_SEM | FA_SEPC
FA_SENF | FA_SEPHC
FA_SEPA | FA_SEPHS
FA_SEPC | FA_SES
FA_SEPHC | FA_SETAC
FA_SEPHS | FA_SETAP
FA_SES | FA_SETPC
FA_SETAC | FA_SEZ
FA_SETAP | FA_SQFC
FA_SETPC | FA_SQFDF
FA_SEZ | FA_SQFDG
FA_SQFC | FA_SQFDS
FA_SQFDF | FA_SQFFD
FA_SQFDG | FA_SQFFH
FA_SQFDS | FA_SQFFM
FA_SQFFD | FA_SQFFY
FA_SQFFH | FA_SQFRA
FA_SQFFM | FA_SQFRE
FA_SQFFY | FA_SQMT
FA_SQFRA | FA_SQTA
FA_SQFRE | FA_SQTB
FA_SQMT | FA_SQTE
FA_SQTA | FA_SQTL
FA_SQTB | FA_SQTOF
FA_SQTE | FA_SQTP
FA_SQTL | FA_SQTS
FA_SQTOF | FA_SQTV
FA_SQTP | FA_SQTW
FA_SQTS | FA_SQTY
FA_SQTV | FA_SYLH
FA_SQTW | FA_WEHY
FA_SQTY
FA_SYLH
FA_WEHY

## Tables
Impact Codes | Likelihood Values | ValidRisks
A | 1 | E3
B | 2 | E4
C | 3 | E5
D | 4 | E6
E | 5 | E7
F | 6 | F3
G | 7 | F4
H | 8 | F5
F6
F7
G3
G4
G5
G6
G7
H3
H4
H5
H6
H7