## CriticalityByFcodeSystem
[8 empty] | Impacts of function loss | [7 empty] | Derived System Criticalities
System | Functional location | Function Location Description | System No | Tag Abbreviation | Utilities System YorN | Comment | - | Safety Risk | Safety Justification | Eenvironment Risk | Environment Justification | Production Risk | Production Justification | Business Risk | Business Justification | Safety Criticality | Envirnment Criticality | Production Criticality | Business Criticality
0 | R-SYSTEM-00 | GENERAL / NON SPECIFIC SYSTEM SYS 00 | 00 | SYS | N | [10 empty] | #N/A | #N/A | #N/A | #N/A
1 | R-SYSTEM-01 | RESERVED FOR SUBSEA USE | 01 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
2 | R-SYSTEM-02 | RESERVED FOR SUBSEA USE | 02 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
3 | R-SYSTEM-03 | RESERVED FOR SUBSEA USE | 3 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
4 | R-SYSTEM-04 | RESERVED FOR SUBSEA USE | 4 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
5 | R-SYSTEM-05 | CONTROL UMBILICALS AND HPU SYS 05 | 5 | SYS | N | [10 empty] | #N/A | #N/A | #N/A | #N/A
6 | R-SYSTEM-06 | RESERVED FOR SUBSEA USE | 6 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
7 | R-SYSTEM-07 | RESERVED FOR SUBSEA USE | 7 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
8 | R-SYSTEM-08 | RESERVED FOR SUBSEA USE | 8 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
9 | R-SYSTEM-09 | RESERVED FOR SUBSEA USE | 9 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
10 | R-SYSTEM-10 | RESERVED FOR SUBSEA USE | 10 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
11 | R-SYSTEM-11 | RESERVED FOR SUBSEA USE | 11 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
12 | R-SYSTEM-12 | RESERVED FOR SUBSEA USE | 12 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
13 | R-SYSTEM-13 | SUBSEA - WELLHEAD AND TEST SEPARATOR | 13 | SYS | N | [10 empty] | #N/A | #N/A | #N/A | #N/A
14 | R-SYSTEM-14 | RESERVED FOR SUBSEA USE | 14 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
15 | R-SYSTEM-15 | RESERVED FOR SUBSEA USE | 15 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
16 | R-SYSTEM-16 | RESERVED FOR SUBSEA USE | 16 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
17 | R-SYSTEM-17 | RESERVED FOR SUBSEA USE | 17 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
18 | R-SYSTEM-18 | RESERVED FOR SUBSEA USE | 18 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
19 | R-SYSTEM-19 | RESERVED FOR SUBSEA USE | 19 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
20 | R-SYSTEM-20 | PROCESS SEPARATION SYS 20 | 20 | SYS | N |  |  | H7 | No safety impact if system primary function lost - safe shutdown | H7 | No environment impact on primary function loss - system safe shut down | G7 | Production loss of 1 day @ $200k/d | G7 | Local management issue on | C | C | B | B
21 | R-SYSTEM-21 | PROCESS CONDENSATE HANDLING SYS 21 | 21 | SYS | N |  |  | H7 | No safety impact if system primary function lost - safe shutdown | H7 | No environment impact on primary function loss - system safe shut down | G7 | Production loss of 1 day @ $200k/d | G7 | Local management issue on | C | C | B | B
22 | R-SYSTEM-22 | PROCESS RECEPTION SYS 22 | 22 | SYS | N |  |  | H7 | No safety impact if system primary function lost - safe shutdown | H7 | No environment impact on primary function loss - system safe shut down | G7 | Production loss of 1 day @ $200k/d | G7 | Local management issue on | C | C | B | B
23 | R-SYSTEM-23 | PROCESS COMPRESSION MAIN | 23 | SYS | N |  |  | H7 | No safety impact if system primary function lost - safe shutdown | H7 | No environment impact on primary function loss - system safe shut down | G7 | Production loss of 1 day @ $200k/d | G7 | Local management issue on | C | C | B | B
24 | R-SYSTEM-24 | FLASH GAS COMPRESSION SYS 24 | 24 | SYS | N |  |  | H7 | No safety impact if system primary function lost - safe shutdown | H7 | No environment impact on primary function loss - system safe shut down | G7 | Production loss of 1 day @ $200k/d | G7 | Local management issue on | C | C | B | B
25 | R-SYSTEM-25 | GAS TREATMENT SYS 25 | 25 | SYS | N |  |  | H7 | No safety impact if system primary function lost - safe shutdown | H7 | No environment impact on primary function loss - system safe shut down | G7 | Production loss of 1 day @ $200k/d | G7 | Local management issue on | C | C | B | B
26 | R-SYSTEM-26 | RESERVED FOR ONSHORE USE | 26 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
27 | R-SYSTEM-27 | GAS EXPORT SYS 27 | 27 | SYS | N |  |  | H7 | No safety impact if system primary function lost - safe shutdown | H7 | No environment impact on primary function loss - system safe shut down | G7 | Production loss of 1 day @ $200k/d | G7 | Local management issue on | C | C | B | B
28 | R-SYSTEM-28 | RICH MEG SYS 28 | 28 | SYS | N |  |  | H7 | No safety impact if system primary function lost - safe shutdown | H7 | No environment impact on primary function loss - system safe shut down | G7 | Production loss of 1 day @ $200k/d | G7 | Local management issue on | C | C | B | B
29 | R-SYSTEM-29 | LEAN MEG SYS 29 | 29 | SYS | N |  |  | H7 | No safety impact if system primary function lost - safe shutdown | H7 | No environment impact on primary function loss - system safe shut down | G7 | Production loss of 1 day @ $200k/d | G7 | Local management issue on | C | C | B | B
30 | R-SYSTEM-30 | MEG REGENERATION SYS 30 | 30 | SYS | N |  |  | H7 | No safety impact if system primary function lost - safe shutdown | H7 | No environment impact on primary function loss - system safe shut down | G7 | Production loss of 1 day @ $200k/d | G7 | Local management issue on | C | C | B | B
31 | R-SYSTEM-31 | RESERVED FOR ONSHORE USE | 31 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
32 | R-SYSTEM-32 | RESERVED FOR ONSHORE USE | 32 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
33 | R-SYSTEM-33 | RESERVED FOR ONSHORE USE | 33 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
34 | R-SYSTEM-34 | RESERVED FOR ONSHORE USE | 34 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
35 | R-SYSTEM-35 | RESERVED FOR ONSHORE USE | 35 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
36 | R-SYSTEM-36 | RESERVED FOR ONSHORE USE | 36 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
37 | R-SYSTEM-37 | RESERVED FOR ONSHORE USE | 37 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
38 | R-SYSTEM-38 | RESERVED FOR ONSHORE USE | 38 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
39 | R-SYSTEM-39 | RESERVED FOR ONSHORE USE | 39 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
40 | R-SYSTEM-40 | LP FUEL GAS SYS 40 | 40 | SYS | N |  |  | H7 | No safety impact if system primary function lost - safe shutdown | H7 | No environment impact on primary function loss - system safe shut down | G7 | Production loss of 1 day @ $200k/d | G7 | Local management issue on | C | C | B | B
41 | R-SYSTEM-41 | PROCESS - HP WET FLARE | 41 | SYS | N |  |  | E5 | High safety impact if system primary function lost | H5 | No environment impact on primary function loss - system safe shut down | G7 | Production loss of 1 day @ $200k/d | G7 | Local management issue on | A | C | B | B
42 | R-SYSTEM-42 | PROCESS - HP FLARE | 42 | SYS | N |  |  | E5 | High safety impact if system primary function lost | H5 | No environment impact on primary function loss - system safe shut down | G7 | Production loss of 1 day @ $200k/d | G7 | Local management issue on | A | C | B | B
43 | R-SYSTEM-43 | PROCESS - VENT AND BLOW DOWN | 43 | SYS | N |  |  | E5 | High safety impact if system primary function lost | H5 | No environment impact on primary function loss - system safe shut down | G7 | Production loss of 1 day @ $200k/d | G7 | Local management issue on | A | C | B | B
44 | R-SYSTEM-44 | PROCESS - LP FLARE | 44 | SYS | N |  |  | E5 | High safety impact if system primary function lost | H5 | No environment impact on primary function loss - system safe shut down | G7 | Production loss of 1 day @ $200k/d | G7 | Local management issue on | A | C | B | B
45 | R-SYSTEM-45 | UTILITIES - FUEL GAS | 45 | SYS | N |  |  | H7 | No safety impact if system primary function lost - safe shutdown | H7 | No environment impact on primary function loss - system safe shut down | G7 | Production loss of 1 day @ $200k/d | G7 | Local management issue on | C | C | B | B
46 | R-SYSTEM-46 | UTILITIES - FUEL GAS HP | 46 | SYS | N |  |  | H7 | No safety impact if system primary function lost - safe shutdown | H7 | No environment impact on primary function loss - system safe shut down | G7 | Production loss of 1 day @ $200k/d | G7 | Local management issue on | C | C | B | B
47 | R-SYSTEM-47 | CHEMICALS - METHANOL INJECTION | 47 | SYS | N |  |  | H7 | No safety impact if system primary function lost - safe shutdown | H7 | No environment impact on primary function loss - system safe shut down | E5 | continuing loss of flowline / well | F5 | Senior management short term attention | C | C | A | B
48 | R-SYSTEM-48 | CHEMICALS - CORROSION INHIBITOR INJECTION | 48 | SYS | N |  |  | H7 | No safety impact if system primary function lost - safe shutdown | H7 | No environment impact on primary function loss - system safe shut down | E4 | continuing loss of flowline / well | F5 | Senior management short term attention | C | C | B | B
49 | R-SYSTEM-49 | CHEMICALS - KINETIC INHIBITOR INJECTION | 49 | SYS | N |  |  | H7 | No safety impact if system primary function lost - safe shutdown | H7 | No environment impact on primary function loss - system safe shut down | E4 | continuing loss of flowline / well | F5 | Senior management short term attention | C | C | B | B
50 | R-SYSTEM-50 | CHEMICALS - REVERSE EMULSION BREAKER | 50 | SYS | N |  |  | H7 | No safety impact if system primary function lost - safe shutdown | H7 | No environment impact on primary function loss - system safe shut down | E4 | continuing loss of flowline / well | F5 | Senior management short term attention | C | C | B | B
51 | R-SYSTEM-51 | CHEMICAL INJECTION SYS 51 | 51 | SYS | N |  |  | H7 | No safety impact if system primary function lost - safe shutdown | H7 | No environment impact on primary function loss - system safe shut down | E4 | continuing loss of flowline / well | F5 | Senior management short term attention | C | C | B | B
52 | R-SYSTEM-52 | MEG CHEMICAL INJECTION SYS 52 | 52 | SYS | N |  |  | H7 | No safety impact if system primary function lost - safe shutdown | H7 | No environment impact on primary function loss - system safe shut down | E4 | Gas export limited due to inability to meet spec | F5 | Senior management short term attention | C | C | B | B
53 | R-SYSTEM-53 | POTABLE WATER SYS 53 | 53 | SYS | Y |  |  | H7 | No safety impact if system primary function lost - safe shutdown | H7 | No environment impact on primary function loss - system safe shut down | H7 | No direct impact on export or temporary supplies substitute | H7 | Local management issue on | C | C | C | C
54 | R-SYSTEM-54 | UTILITY WATER SYS 54 | 54 | SYS | Y |  |  | H7 | No safety impact if system primary function lost - safe shutdown | H7 | No environment impact on primary function loss - system safe shut down | H7 | No direct impact on export or temporary supplies substitute | H7 | Local management issue on | C | C | C | C
55 | R-SYSTEM-55 | CHEMICALS - MISCELLANEOUS | 55 | SYS | N |  |  | H7 | No safety impact if system primary function lost - safe shutdown | H7 | No environment impact on primary function loss - system safe shut down | G7 | Long term production losses due to reduced plant efficiency | H7 | Local management issue on | C | C | B | C
56 | R-SYSTEM-56 | DRAINS - HAZARDOUS OPEN SYS 56 | 56 | SYS | N |  |  | F5 | Loss of safe disposal route for hazardous liquids. Impact based on leaks affecting personnel, not escalating to fire or explosion | H7 | Highly localised to plant and limited liquid release |  |  |  |  | B | C | #N/A | #N/A
57 | R-SYSTEM-57 | CLOSED DRAINS SYS 57 | 57 | SYS | N | [10 empty] | #N/A | #N/A | #N/A | #N/A
58 | R-SYSTEM-58 | NON-HAZARDOUS OPEN DRAINS SYS 58 | 58 | SYS | Y | [10 empty] | #N/A | #N/A | #N/A | #N/A
59 | R-SYSTEM-59 | SANITARY WATER SYS 59 | 59 | SYS | Y | [10 empty] | #N/A | #N/A | #N/A | #N/A
60 | R-SYSTEM-60 | HOT OIL SYS 60 | 60 | SYS | N | [10 empty] | #N/A | #N/A | #N/A | #N/A
61 | R-SYSTEM-61 | OXYGEN SCAVENGER SYS 61 | 61 | SYS | N | [10 empty] | #N/A | #N/A | #N/A | #N/A
62 | R-SYSTEM-62 | DIESEL SYS 62 | 62 | SYS | N | [10 empty] | #N/A | #N/A | #N/A | #N/A
63 | R-SYSTEM-63 | INSTRUMENT AIR SYS 63 | 63 | SYS | Y | [10 empty] | #N/A | #N/A | #N/A | #N/A
64 | R-SYSTEM-64 | INERT GAS SYS 64 | 64 | SYS | Y | [10 empty] | #N/A | #N/A | #N/A | #N/A
65 | R-SYSTEM-65 | PLANT/UTILITY AIR SYS 65 | 65 | SYS | Y | [10 empty] | #N/A | #N/A | #N/A | #N/A
66 | R-SYSTEM-66 | THERMAL OXIDIZER SYS 66 | 66 | SYS | N | [10 empty] | #N/A | #N/A | #N/A | #N/A
67 | R-SYSTEM-67 | PRODUCED WATER SYS 67 | 67 | SYS | N | [10 empty] | #N/A | #N/A | #N/A | #N/A
68 | R-SYSTEM-68 | RESERVED FOR ONSHORE USE | 68 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
69 | R-SYSTEM-69 | RESERVED FOR ONSHORE USE | 69 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
70 | R-SYSTEM-70 | RESERVED FOR ONSHORE USE | 70 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
71 | R-SYSTEM-71 | RESERVED FOR ONSHORE USE | 71 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
72 | R-SYSTEM-72 | RESERVED FOR ONSHORE USE | 72 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
73 | R-SYSTEM-73 | RESERVED FOR ONSHORE USE | 73 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
74 | R-SYSTEM-74 | RESERVED FOR ONSHORE USE | 74 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
75 | R-SYSTEM-75 | RESERVED FOR ONSHORE USE | 75 | SYS | N | System Not in Use | [9 empty] | #N/A | #N/A | #N/A | #N/A
76 | R-SYSTEM-76 | ICSS - PROCESS AUTOMATION SYSTEM | 76 | SYS | N | [10 empty] | #N/A | #N/A | #N/A | #N/A
77 | R-SYSTEM-77 | ICSS - SAFETY INSTRUMENTED SYSTEM ESD | 77 | SYS | N | [10 empty] | #N/A | #N/A | #N/A | #N/A
78 | R-SYSTEM-78 | FIRE AND GAS DETECTION | 78 | SYS | N | [10 empty] | #N/A | #N/A | #N/A | #N/A
79 | R-SYSTEM-79 | SAFETY - FIRE FIGHTING | 79 | SYS | N | [10 empty] | #N/A | #N/A | #N/A | #N/A
80 | R-SYSTEM-80 | NORMAL POWER | 80 | SYS | N | [10 empty] | #N/A | #N/A | #N/A | #N/A
81 | R-SYSTEM-81 | FIRE WATER SYS 81 | 81 | SYS | N | [10 empty] | #N/A | #N/A | #N/A | #N/A
82 | R-SYSTEM-82 | UTILITIES - SEWAGE SYSTEM | 82 | SYS | Y | [10 empty] | #N/A | #N/A | #N/A | #N/A
83 | R-SYSTEM-83 | TELECOMS (GENERAL) | 83 | SYS | N | [10 empty] | #N/A | #N/A | #N/A | #N/A
84 | R-SYSTEM-84 | ESSENTIAL POWER | 84 | SYS | N | [10 empty] | #N/A | #N/A | #N/A | #N/A
85 | R-SYSTEM-85 | ESSENTIAL LIGTING AND SMALL POWER | 85 | SYS | N | [10 empty] | #N/A | #N/A | #N/A | #N/A
86 | R-SYSTEM-86 | TRACE HEATING | 86 | SYS | N | [10 empty] | #N/A | #N/A | #N/A | #N/A
87 | R-SYSTEM-87 | EMERGENCY POWER | 87 | SYS | N | [10 empty] | #N/A | #N/A | #N/A | #N/A
88 | R-SYSTEM-88 | UPS POWER | 88 | SYS | N | [10 empty] | #N/A | #N/A | #N/A | #N/A
89 | R-SYSTEM-89 | NORMAL LIGHTING AND SMALL POWER | 89 | SYS | N | [10 empty] | #N/A | #N/A | #N/A | #N/A
90 | R-SYSTEM-90 | EARTHING AND LIGHTING PROTECTION | 90 | SYS | N | [10 empty] | #N/A | #N/A | #N/A | #N/A
91 | R-SYSTEM-91 | POWER - MAIN GENERATION SYS 91 | 91 | SYS | N | [10 empty] | #N/A | #N/A | #N/A | #N/A
92 | R-SYSTEM-92 | CATHODIC PROTECTION | 92 | SYS | N | [10 empty] | #N/A | #N/A | #N/A | #N/A
93 | R-SYSTEM-93 | POWER MANAGEMENT SYSTEM | 93 | SYS | N | [10 empty] | #N/A | #N/A | #N/A | #N/A
94 | R-SYSTEM-94 | UTILITIES - HVAC | 94 | SYS | Y | [10 empty] | #N/A | #N/A | #N/A | #N/A
95 | R-SYSTEM-95 | ACCESS CONTROL | 95 | SYS | N | [10 empty] | #N/A | #N/A | #N/A | #N/A
96 | R-SYSTEM-96 | CCTV - SECURITY | 96 | SYS | N | [10 empty] | #N/A | #N/A | #N/A | #N/A
97 | R-SYSTEM-97 | LAN - VOIP | 97 | SYS | N | [10 empty] | #N/A | #N/A | #N/A | #N/A
98 | R-SYSTEM-98 | PAGA | 98 | SYS | N | [10 empty] | #N/A | #N/A | #N/A | #N/A
99 | R-SYSTEM-99 | RADIO SYSTEMS (INCLUDING SAT COM) | 99 | SYS | N | [10 empty] | #N/A | #N/A | #N/A | #N/A

## FailureCodeSystemCoverage
Count of Functional location | Column Labels
Row Labels | (blank) | 00 | 04 | 05 | 13 | 20 | 21 | 22 | 23 | 24 | 25 | 27 | 28 | 29 | 30 | 38 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 75 | 76 | 77 | 78 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | N/A | Grand Total
(blank) |  | 21: 2; 27: 1; 98: 4 |  | 7
FA_CFBC |  | 78: 2 | 4 | 6
FA_CFSGA |  | 95: 37 |  | 37
FA_CFSGW |  | 81: 3 | 2 | 5
FA_CFSSE | [68 empty] | 104 | 104
FA_CFSSF | [68 empty] | 18 | 19 | bar: 67
FA_CFSST |  | 04: 1; 57: 14 | 902 | 917
FA_EECF | 1 | 42: 11; 85: 188; 89: 198 |  | 398
FA_EECH |  | 20: 8; 24: 6; 25: 1; 27: 2; 29: 3; 30: 8; 42: 1; 43: 1; 44: 1; 45: 3; 46: 3; 52: 18; 60: 1; 64: 1; 67: 1; 80: 4; 81: 3; 87: 5; 91: 53 |  | 123
FA_EECMD |  | 81: 3; 87: 4 |  | 7
FA_EECMI |  | 05: 6; 21: 25; 22: 2; 24: 45; 25: 21; 27: 20; 28: 23; 29: 13; 30: 68; 42: 2; 43: 2; 45: 3; 46: 8; 47: 14; 51: 30; 52: 53; 53: 6; 56: 30; 57: 9; 58: 8; 59: 4; 60: 37; 61: 3; 62: 2; 63: 5; 64: 1; 65: 36; 66: 4; 67: 25; 80: 14; 81: 14; 82: 6; 87: 34; 91: 65 | 7 | 645
FA_EECMS |  | 44: 1; 87: 8 |  | 9
FA_EECO |  | 66: 2; 80: 15 | 4 | 21
FA_EECT |  | 98: 2 |  | 2
FA_EEPBA |  | 80: 121; 85: 36; 87: 47; 88: 526; 89: 60; 91: 78 |  | 868
FA_EEPBV |  | 80: 44; 87: 3 | 1 | 48
FA_EEPCS |  | 20: 2; 21: 4; 27: 1; 29: 2; 30: 1; 56: 1; 92: 103 |  | 114
FA_EEPNE |  | 90: 94 | 24 | 118
FA_EEPNN |  | 80: 2; 82: 2; 91: 4 |  | 8
FA_EEPS | 17 | 20: 4; 21: 14; 24: 12; 25: 2; 27: 2; 28: 15; 29: 15; 30: 77; 42: 1; 44: 1; 45: 3; 46: 3; 47: 14; 51: 8; 52: 39; 56: 10; 57: 10; 59: 6; 60: 22; 65: 25; 66: 7; 67: 23; 87: 1 | 16 | 347
FA_EEPU |  | 88: 22; 91: 7 |  | 29
FA_EETA |  | 80: 4; 87: 2 |  | 6
FA_EETB |  | 80: 4; 81: 6; 84: 2; 87: 1; 88: 20; 91: 6 |  | 39
FA_EETC |  | 27: 9; 80: 8; 81: 2; 84: 3; 87: 4; 88: 22; 91: 9 |  | 57
FA_EETD |  | 80: 8; 87: 2; 90: 60 |  | 70
FA_EETFW |  | 20: 1; 80: 16; 87: 4 |  | 21
FA_EETGA |  | 84: 2; 87: 4; 91: 4 |  | 10
FA_EETI |  | 80: 2; 81: 3; 84: 2; 87: 4; 88: 12; 91: 2 |  | 25
FA_EETM |  | 80: 739; 87: 171 |  | 910
FA_EETO |  | 50: 4; 81: 1 |  | 5
FA_EETP | 3 | [68 empty] | 3
FA_EETQ |  | 24: 21; 25: 12; 27: 2; 30: 24; 45: 2; 60: 3; 80: 2 |  | 66
FA_EETR |  | 92: 15 |  | 15
FA_EETW |  | 66: 1; 78: 5; 80: 12; 85: 19; 86: 2; 87: 9; 88: 22; 89: 44; 90: 1; 91: 14; 92: 15; 94: 2; 95: 21 | 4 | 171
FA_EETY |  | 76: 16; 77: 6; 78: 6 |  | 28
FA_INAM |  | 21: 12; 27: 4; 46: 1 |  | 17
FA_INAP |  | 21: 2; 27: 2; 46: 1; 52: 4; 60: 1 |  | 10
FA_INDC |  | 20: 3; 22: 2; 45: 2; 56: 1; 66: 3; 81: 2 |  | 13
FA_INDFD |  | 87: 14; 91: 8 |  | 22
FA_INDFS |  | 20: 6; 21: 11; 24: 24; 25: 54; 27: 34; 45: 9; 46: 3; 62: 2; 63: 15; 64: 1; 65: 50; 66: 4; 78: 10; 87: 7; 91: 32 |  | 262
FA_INDI | 27 | 20: 116; 21: 99; 22: 10; 24: 127; 25: 166; 27: 100; 28: 119; 29: 36; 30: 131; 40: 1; 41: 3; 42: 22; 43: 18; 44: 9; 45: 22; 46: 42; 47: 27; 51: 4; 52: 32; 53: 12; 54: 2; 56: 37; 57: 37; 58: 7; 59: 3; 60: 115; 62: 40; 63: 25; 64: 34; 65: 17; 66: 13; 67: 34; 78: 2; 81: 105; 82: 5; 87: 15; 91: 59 |  | 1673
FA_INDMS |  | 00: 1; 20: 86; 21: 63; 22: 18; 24: 218; 25: 188; 27: 55; 28: 25; 29: 9; 30: 156; 42: 27; 43: 11; 44: 29; 45: 28; 46: 42; 51: 4; 52: 35; 53: 1; 56: 1; 57: 7; 58: 3; 59: 5; 60: 192; 63: 5; 64: 5; 65: 122; 66: 37; 67: 19; 81: 3; 84: 2; 87: 72; 91: 390 |  | 1859
FA_INDMT | 19 | 20: 266; 21: 156; 22: 57; 24: 339; 25: 350; 27: 148; 28: 173; 29: 80; 30: 397; 40: 18; 41: 1; 42: 54; 43: 17; 44: 36; 45: 64; 46: 111; 47: 62; 51: 40; 52: 116; 53: 6; 54: 2; 56: 24; 57: 39; 58: 12; 59: 24; 60: 181; 62: 2; 63: 26; 64: 27; 65: 85; 66: 49; 67: 71; 80: 2; 81: 51; 82: 1; 87: 34; 91: 233 |  | 3373
FA_INDP | [69 empty] | 1 | bar: 83
FA_INDS | 6 | 20: 32; 21: 84; 22: 7; 24: 88; 25: 256; 27: 79; 28: 19; 29: 8; 30: 91; 40: 3; 42: 16; 43: 19; 44: 15; 45: 31; 46: 27; 47: 4; 51: 3; 52: 11; 53: 2; 56: 12; 57: 21; 58: 2; 59: 2; 60: 170; 62: 26; 63: 62; 64: 15; 65: 17; 66: 30; 67: 29; 77: 24; 78: 185; 80: 8; 81: 118; 82: 1; 86: 1; 87: 60; 90: 5; 91: 268; 94: 2 | 4 | 1863
FA_INDT |  | 65: 33 |  | 33
FA_INSC | 1 | 87: 3; 91: 4; 93: 5 |  | 13
FA_INSD |  | 80: 6 | 3 | 9
FA_INSJ |  | 20: 26; 21: 42; 22: 34; 23: 7; 24: 9; 25: 43; 28: 34; 29: 38; 30: 81; 42: 14; 44: 2; 46: 6; 47: 15; 50: 4; 55: 1; 56: 2; 57: 3; 58: 1; 60: 33; 63: 1; 64: 1; 65: 18; 66: 12; 67: 29; 78: 171; 80: 2; 81: 6; 82: 1; 91: 3; 92: 43; 96: 56 | 128 | 866
FA_INSL | 3 | 05: 4; 20: 4; 25: 7; 27: 2; 42: 5; 43: 1; 44: 1; 46: 5; 52: 2; 60: 23; 63: 2; 64: 2; 65: 15; 66: 2; 75: 1; 76: 48; 77: 2; 78: 44; 80: 3; 81: 6; 84: 3; 87: 4; 88: 8; 90: 1; 91: 9; 96: 4 | 7 | 218
FA_INSS |  | 83: 1; 93: 3; 95: 2; 96: 2; 98: 1; 99: 1 | 2 | 12
FA_INST |  | 83: 3 |  | 3
FA_INSY |  | 22: 1; 76: 5; 77: 13 |  | 19
FA_PEA | 2 | 20: 12; 21: 6; 24: 10; 25: 1; 27: 30; 28: 3; 29: 2; 44: 3; 45: 8; 46: 12; 47: 8; 60: 4; 63: 2; 64: 2; 65: 12; 81: 18; 87: 3; 91: 14 |  | 152
FA_PEC | [69 empty] | 1 | bar: 98
FA_PEG | 49 | 05: 24; 20: 2618; 21: 1849; 22: 374; 24: 577; 25: 2784; 27: 379; 28: 2705; 29: 899; 30: 2036; 40: 447; 41: 175; 42: 1041; 43: 29; 44: 554; 45: 167; 46: 809; 47: 581; 48: 1; 51: 193; 52: 904; 53: 488; 54: 946; 56: 588; 57: 1293; 58: 588; 60: 1720; 61: 28; 62: 52; 63: 1298; 64: 1263; 65: 1019; 66: 358; 67: 2346; 81: 1743; 82: 61; 86: 6; 87: 72; 91: 186 | 58 | 33308
FA_PEL | [69 empty] | 1 | bar: 22
FA_PEM |  | 63: 130; 91: 4 |  | 134
FA_PEO |  | 20: 32; 21: 24; 22: 5; 24: 88; 25: 57; 27: 39; 28: 24; 29: 15; 30: 61; 41: 1; 42: 8; 43: 3; 44: 12; 45: 10; 46: 27; 47: 7; 52: 12; 53: 2; 56: 9; 57: 7; 58: 10; 60: 34; 64: 8; 66: 24; 67: 17; 81: 16; 82: 2; 91: 12 |  | 566
FA_PESC | 13 | 20: 92; 21: 45; 22: 18; 24: 64; 25: 70; 27: 48; 28: 21; 29: 10; 30: 51; 40: 6; 42: 4; 45: 17; 46: 30; 47: 14; 51: 8; 52: 34; 54: 1; 56: 4; 57: 3; 59: 2; 60: 9; 62: 1; 63: 19; 64: 16; 65: 12; 66: 4; 67: 12; 81: 40; 87: 7; 91: 22 |  | 697
FA_PESR | 6 | 20: 10; 21: 6; 30: 3; 81: 21; 91: 12 |  | 58
FA_PESV |  | 21: 3; 27: 1; 28: 5; 29: 3; 30: 1; 52: 4; 60: 1; 64: 1; 67: 5 |  | 24
FA_PET |  | 20: 57; 21: 36; 22: 3; 24: 97; 25: 106; 27: 50; 28: 24; 29: 3; 30: 98; 42: 2; 43: 5; 44: 3; 45: 16; 46: 20; 52: 17; 54: 1; 57: 7; 59: 2; 60: 42; 63: 6; 64: 5; 65: 31; 66: 6; 67: 5 |  | 642
FA_PEVB | 78 | 05: 66; 20: 1055; 21: 989; 22: 95; 24: 298; 25: 1301; 27: 755; 28: 1478; 29: 547; 30: 2182; 40: 192; 41: 57; 42: 238; 43: 117; 44: 98; 45: 279; 46: 525; 47: 534; 48: 5; 51: 309; 52: 930; 53: 133; 54: 180; 56: 92; 57: 307; 58: 91; 59: 2; 60: 295; 61: 17; 62: 74; 63: 594; 64: 543; 65: 324; 66: 113; 67: 679; 81: 297; 82: 12; 87: 54; 91: 158 | 9 | 16102
FA_PEVC | 24 | 05: 9; 20: 69; 21: 76; 22: 3; 24: 106; 25: 32; 27: 47; 28: 159; 29: 54; 30: 155; 40: 13; 41: 11; 42: 25; 43: 3; 44: 23; 45: 10; 46: 54; 47: 59; 48: 1; 51: 40; 52: 114; 53: 17; 54: 105; 56: 15; 57: 35; 58: 6; 60: 41; 61: 2; 62: 5; 63: 47; 64: 142; 65: 118; 66: 21; 67: 67; 81: 23; 82: 2; 87: 9; 91: 80 |  | 1822
FA_PEVD |  | 81: 3 |  | 3
FA_PEVG |  | 20: 273; 21: 402; 22: 21; 24: 832; 25: 496; 27: 30; 28: 42; 29: 23; 30: 364; 40: 24; 41: 105; 42: 289; 43: 13; 44: 193; 45: 63; 46: 53; 47: 6; 52: 9; 53: 45; 54: 82; 56: 69; 57: 80; 58: 56; 60: 767; 62: 6; 63: 29; 64: 30; 65: 61; 66: 164; 67: 10; 81: 279; 82: 2; 87: 5; 91: 29 |  | 4952
FA_PEVL |  | 20: 504; 21: 49; 22: 111; 24: 72; 25: 133; 27: 41; 28: 358; 29: 31; 30: 112; 40: 11; 42: 12; 43: 7; 44: 13; 45: 19; 46: 44; 47: 24; 48: 1; 51: 10; 52: 14; 56: 1; 57: 19; 58: 4; 60: 46; 63: 6; 64: 7; 65: 3; 66: 34; 67: 47; 81: 7 |  | 1740
FA_PEVM | 9 | 21: 1; 52: 4; 81: 5 |  | 19
FA_PEVN | 69 | 20: 22; 21: 22; 22: 1; 25: 15; 27: 38; 28: 17; 30: 12; 43: 5; 45: 4; 46: 17; 47: 6; 51: 1; 52: 3; 57: 12; 60: 2; 64: 8 |  | 254
FA_PEVX |  | 21: 2; 42: 1; 87: 3 |  | 6
FA_PEVY |  | 25: 1; 27: 1; 63: 22; 64: 6; 65: 5; 66: 4; 81: 26 |  | 65
FA_REBC |  | 25: 3; 43: 2; 60: 6; 82: 2 |  | 13
FA_REC |  | 30: 4 |  | 4
FA_REDH |  | 81: 6 |  | 6
FA_REDP |  | 21: 3; 25: 3; 27: 10; 45: 4; 80: 4; 87: 2 |  | 26
FA_REEL |  | 81: 4; 87: 1 |  | 5
FA_REFA |  | 21: 9; 25: 3; 45: 3; 87: 17 |  | 32
FA_REFC |  | 24: 31; 25: 14; 27: 4; 30: 26; 46: 8; 60: 8; 65: 25; 66: 2; 67: 3; 80: 2; 87: 11; 91: 28 |  | 162
FA_REI |  | 42: 2; 51: 14; 52: 10; 56: 4; 82: 2 |  | 32
FA_REMC |  | 27: 2; 63: 2; 64: 1; 87: 1 |  | 6
FA_REMR |  | 24: 6 |  | 6
FA_REMT |  | 65: 10; 87: 1 |  | 11
FA_RENG |  | 27: 2; 46: 6; 80: 4; 91: 4 |  | 16
FA_REPC |  | 05: 6; 21: 10; 24: 12; 27: 4; 28: 24; 29: 16; 30: 32; 42: 5; 47: 19; 51: 30; 52: 59; 53: 6; 56: 28; 57: 12; 58: 8; 60: 17; 61: 4; 62: 2; 65: 5; 67: 22; 80: 4; 81: 17; 82: 4; 87: 6; 91: 13 | 2 | 367
FA_REPD |  | 20: 3; 22: 4; 25: 4; 27: 3; 29: 1; 30: 1; 60: 9; 66: 2; 81: 6; 87: 6 |  | 39
FA_RER |  | 56: 3; 67: 1 |  | 4
FA_RETG |  | 65: 5 |  | 5
FA_RETP |  | 65: 5 |  | 5
FA_REUC | [69 empty] | 1 | bar: 67
FA_SEA |  | 63: 6 |  | 6
FA_SEC |  | 65: 6 |  | 6
FA_SEE |  | 28: 3 |  | 3
FA_SEFB |  | 20: 5; 21: 32; 22: 1; 24: 17; 25: 6; 27: 9; 28: 25; 29: 11; 30: 45; 40: 4; 41: 4; 42: 4; 43: 4; 45: 4; 46: 6; 47: 9; 51: 9; 52: 38; 53: 4; 57: 3; 60: 11; 62: 2; 65: 3; 67: 11; 81: 28; 91: 28 |  | 323
FA_SEFE |  | 05: 6; 20: 5; 21: 2; 24: 13; 25: 9; 27: 5; 29: 5; 30: 8; 45: 3; 46: 6; 47: 12; 51: 2; 60: 1; 62: 2; 63: 21; 64: 8; 65: 35; 67: 2; 81: 23; 87: 27; 91: 34 |  | 229
FA_SEFS |  | 27: 4; 46: 2; 64: 21; 91: 12 |  | 39
FA_SEHF |  | 21: 6; 24: 18; 25: 11; 27: 2; 30: 19; 45: 1; 46: 4; 60: 3; 63: 5; 65: 30; 67: 1; 80: 4; 87: 4; 91: 4 |  | 112
FA_SEHS |  | 21: 6; 28: 11; 30: 20; 52: 3; 60: 8 |  | 48
FA_SEHT |  | 20: 20; 21: 6; 25: 7; 27: 2; 30: 4; 46: 3; 57: 3; 60: 1; 81: 6; 91: 4 |  | 56
FA_SEL | 2 | 22: 1; 24: 2; 27: 2; 28: 1; 41: 1; 43: 1; 46: 1; 56: 9; 58: 6; 62: 2; 67: 2; 81: 2; 87: 5; 91: 16 |  | 53
FA_SEM |  | 42: 1; 43: 2; 44: 1 | 1 | 5
FA_SENF |  | 25: 2; 60: 2 |  | 4
FA_SEPA | 6 | 20: 9; 21: 6; 22: 9; 25: 24; 27: 3; 28: 10; 29: 9; 30: 28; 52: 4; 60: 50; 66: 16; 81: 18 |  | 192
FA_SEPC |  | 20: 10; 21: 1; 25: 6; 27: 7; 28: 12; 30: 4; 42: 1; 45: 1; 46: 3; 47: 2; 57: 6; 60: 1; 64: 4; 87: 5 |  | 63
FA_SEPHC |  | 21: 2 |  | 2
FA_SEPHS |  | 20: 13; 21: 11; 22: 3; 24: 9; 25: 18; 27: 8; 28: 6; 29: 7; 30: 10; 40: 1; 42: 1; 43: 4; 44: 1; 45: 2; 46: 1; 47: 2; 52: 2; 53: 4; 57: 7; 60: 26; 63: 8; 64: 25; 65: 10; 66: 4; 67: 6; 87: 3; 91: 16 | 1 | 209
FA_SES |  | 24: 16; 29: 10; 47: 32; 51: 16; 52: 58 |  | 132
FA_SETAC |  | 05: 2; 21: 2; 24: 10; 28: 5; 29: 4; 30: 7; 42: 1; 47: 1; 51: 7; 52: 10; 53: 1; 56: 5; 60: 1; 61: 1; 62: 3; 63: 2; 67: 4; 81: 11; 87: 4; 91: 1 |  | 82
FA_SETAP |  | 28: 3; 47: 1; 56: 9; 57: 3; 58: 7; 59: 1; 60: 1; 65: 5; 67: 3; 82: 4 | 12 | 49
FA_SETPC |  | 57: 1; 81: 5; 87: 5 |  | 11
FA_SEZ |  | 42: 1; 63: 2; 64: 1; 65: 30; 66: 1; 87: 1; 91: 28 |  | 64
FA_SQFC |  | 81: 21 |  | 21
FA_SQFDF |  | 78: 467; 87: 4; 91: 12 | 2 | 485
FA_SQFDG |  | 78: 727; 87: 5; 91: 24 | 2 | 758
FA_SQFDS |  | 78: 145 |  | 145
FA_SQFFD |  | 20: 2; 21: 5; 27: 1; 45: 1; 81: 22; 91: 12 |  | 43
FA_SQFFH |  | 81: 3 |  | 3
FA_SQFFM |  | 81: 23 |  | 23
FA_SQFFY |  | 81: 118 |  | 118
FA_SQFRA |  | 60: 1; 78: 209; 81: 29; 82: 1; 91: 8 |  | 248
FA_SQFRE |  | 53: 36 |  | 36
FA_SQMC | [68 empty] | 1 | 1
FA_SQMT |  | 24: 2 |  | 2
FA_SQTA |  | 25: 36; 42: 1; 78: 25; 81: 17; 87: 5 | 3 | 87
FA_SQTB |  | 52: 1; 78: 18; 81: 45; 91: 8; 98: 94 | 6 | 172
FA_SQTE |  | 83: 28; 97: 2; 99: 1 | 4 | 35
FA_SQTH |  | 83: 20; 96: 75 |  | 95
FA_SQTL |  | 98: 455 | 32 | 487
FA_SQTN |  | 99: 3 |  | 3
FA_SQTOF |  | 99: 4 | 2 | 6
FA_SQTP |  | 83: 2; 97: 2; 98: 12 | 92 | 108
FA_SQTS |  | 83: 10; 97: 53; 98: 2; 99: 2 | 55 | 122
FA_SQTV |  | 76: 18; 83: 1; 96: 148 |  | 167
FA_SQTW |  | 97: 22 | 17 | 39
FA_SQTY |  | 78: 4 |  | 4
FA_SYLH | 245 |  |  | 7 | 1 | 13 | 8 | 11 | 1 | 10 | 17 | 16 | 6 | 6 | 16 |  | 4 | 2 | 8 | 4 | 8 | 3 | 26 | 7 | 2 | 1 | 1 | 5 | 7 | 4 | 4 | 1 | 4 | 5 | 4 | 2 | 25 | 3 | 5 | 7 | 7 | 11 | 9 | 18 |  | 1 | 1 | 1 | 2 | 28 | 3 | 1 | 2 | 1 | 2 | 7 | 1 | 1 | 1 | 23 | 1 | 1 | 3 | [5 empty] | 3 | 627
FA_WECO |  | 24: 2; 27: 8; 46: 1; 65: 1; 91: 1 |  | 13
FA_WEHY |  | 30: 4 |  | 4
LOOP |  | 20: 354; 21: 291; 22: 53; 24: 227; 25: 581; 27: 214; 28: 274; 29: 121; 30: 632; 40: 23; 41: 4; 42: 102; 43: 40; 44: 67; 45: 112; 46: 142; 47: 129; 48: 1; 51: 59; 52: 215; 53: 49; 54: 5; 56: 99; 57: 89; 58: 40; 59: 45; 60: 355; 62: 14; 63: 135; 64: 122; 65: 69; 66: 58; 67: 181; 78: 929; 81: 94; 82: 10; 91: 20 | 2 | 5957
SOFT | 21 |  |  |  |  | 546 | 566 | 110 |  | 1474 | 1192 | 305 | 591 | 269 | 1876 | 3 | 60 | 4 | 161 | 44 | 101 | 214 | 227 | 232 | 2 |  |  | 133 | 568 | 126 | 4 |  | 222 | 199 | 90 | 136 | 697 |  | 24 | 139 | 119 | 302 | 210 | 419 |  | 42 | 49 | 2025 | 8 | 450 | 21 |  | 18 |  | 249 | 720 |  |  |  | 1292 | [8 empty] | 5 | 16265
Grand Total | 601 | 1 | 1 | 130 | 1 | 6278 | 4990 | 955 | 8 | 4882 | 8032 | 2531 | 6215 | 2250 | 8845 | 3 | 807 | 368 | 2061 | 352 | 1172 | 1108 | 2279 | 1821 | 13 | 1 | 9 | 925 | 3330 | 942 | 1332 | 2 | 1279 | 2231 | 943 | 234 | 4962 | 58 | 264 | 2621 | 2426 | 2555 | 1194 | 4094 | 1 | 130 | 95 | 4975 | 1044 | 3780 | 142 | 67 | 34 | 244 | 260 | 1505 | 633 | 303 | 162 | 3353 | 177 | 9 | 7 | 60 | 285 | 79 | 571 | 11 | 1539 | 104572

## FailureCodes
Failure codes list in ASSET-C |  |  |  | Failure Codes found in ASSET-C
FailureCode | Description | Number found in ASSET-C WND | Count of Disciplines for code | STATUS | (All)
FA_CFBC | CONTROL ROOM | 4
FA_CFBE | ELECTRICAL SUBSTATION | #REF! |  | Object type2 | FAILURE CODE PLUS | Failure Code and Description | Count of Functional location
FA_CFBI | INSTRUMENT HOUSE | #REF! |  | FA_CFBC | CONTROL ROOM | FA_CFBC - CONTROL ROOM | 6
FA_CFBL | LIVING ACCOMMODATION | #REF! |  | FA_CFBC Total |  |  | 6
FA_CFBO | OFFICE BUILDING | #REF! |  | FA_CFSGA | (blank) | FA_CFSGA - ACCESS CONTROL GATE | 37
FA_CFDL | LAGOON | #REF! |  | FA_CFSGA Total |  |  | 37
FA_CFDO | OUTFALL | #REF! |  | FA_CFSGW | WALL OR FENCE | FA_CFSGW - WALL OR FENCE | 5
FA_CFSGA | ACCESS CONTROL GATE | #REF! |  | FA_CFSGW Total |  |  | 5
FA_CFSGB | BRIDGE | #REF! |  | FA_CFSSE | EQUIPMENT SUPPORT STRUCTURE | FA_CFSSE - EQUIPMENT SUPPORT STRUCTURE | 104
FA_CFSGC | CONTAINMENT | #REF! |  | FA_CFSSE Total |  |  | 104
FA_CFSGP | PARKING LOT | #REF! |  | FA_CFSSF | STRUCTURAL FOUNDATION | FA_CFSSF - STRUCTURAL FOUNDATION | 19
FA_CFSGR | ROAD | #REF! |  | FA_CFSSF Total |  |  | 19
FA_CFSGS | STORAGE YARD | #REF! |  | FA_CFSST | STRUCTURAL BASE | FA_CFSST - STRUCTURAL BASE | 917
FA_CFSGT | WASTE STORAGE | #REF! |  | FA_CFSST Total |  |  | 917
FA_CFSGW | WALL OR FENCE | 5 |  | FA_EECF | LIGHT FITTING | FA_EECF - LIGHT FITTING | 397
FA_CFSPD | FIRE DOOR | #REF! |  | FA_EECF | LIGHT FITTING | (blank) | 1
FA_CFSPW | FIRE / BLAST WALL | #REF! |  | FA_EECF Total |  |  | 398
FA_CFSSA | ANCHOR | #REF! |  | FA_EECH | AC INDUCTION ELECTRIC MOTOR | FA_EECMI - AC INDUCTION ELECTRIC MOTOR | 2
FA_CFSSD | DERRICK OR FRAME | #REF! |  | FA_EECH | ELECTRIC HEATER | FA_EECH - ELECTRIC HEATER | 58
FA_CFSSE | EQUIPMENT SUPPORT STRUCTURE | 104 |  | FA_EECH | ELECTRIC HEATER | SOFT - SOFT TAG | 43
FA_CFSSF | STRUCTURAL FOUNDATION | 19 |  | FA_EECH | (blank) | SOFT - SOFT TAG | 20
FA_CFSSI | PILE | #REF! |  | FA_EECH Total |  |  | 123
FA_CFSSP | PEDESTAL | #REF! |  | FA_EECMD | DC ELECTRIC MOTOR | FA_EECMD - DC ELECTRIC MOTOR | 6
FA_CFSSS | STABILISATION OR GUIDANCE EQUIPMENT | #REF! |  | FA_EECMD | (blank) | FA_EECMD - DC ELECTRIC MOTOR | 1
FA_CFSST | STRUCTURAL BASE | 907 |  | FA_EECMD Total |  |  | 7
FA_EECF | LIGHT FITTING | 398 |  | FA_EECMI | AC INDUCTION ELECTRIC MOTOR | FA_EECMI - AC INDUCTION ELECTRIC MOTOR | 637
FA_EECH | ELECTRIC HEATER | 109 |  | FA_EECMI | AC INDUCTION ELECTRIC MOTOR | (blank) | 2
FA_EECMD | DC ELECTRIC MOTOR | 7 |  | FA_EECMI | MOV VALVE - MOV | FA_PEVB - BALL VALVE | 6
FA_EECMI | AC INDUCTION ELECTRIC MOTOR | 466 |  | FA_EECMI Total |  |  | 645
FA_EECMS | AC SYNCHRONOUS ELECTRIC MOTOR | 1 |  | FA_EECMS | AC SYNCHRONOUS ELECTRIC MOTOR | FA_EECMS - AC SYNCHRONOUS ELECTRIC MOTOR | 9
FA_EECO | ELECTRIC SOCKET OUTLET | 21 |  | FA_EECMS Total |  |  | 9
FA_EECT | TRACE HEATING CIRCUIT | 2 |  | FA_EECO | ELECTRIC SOCKET OUTLET | FA_EECO - ELECTRIC SOCKET OUTLET | 20
FA_EEHC | AIR CONDITIONING UNIT | #REF! |  | FA_EECO | START / STOP SWITCH | FA_EEPS - START / STOP SWITCH | 1
FA_EEHH | AIR HANDLING UNIT | #REF! |  | FA_EECO Total |  |  | 21
FA_EEHV | CONSTANT VOLUME UNIT | #REF! |  | FA_EECT | TRACE HEATING CIRCUIT | FA_EECT - TRACE HEATING CIRCUIT | 2
FA_EEPA | SURGE ARRESTOR | #REF! |  | FA_EECT Total |  |  | 2
FA_EEPBA | AIR CIRCUIT BREAKER | 868 |  | FA_EEPBA | AIR CIRCUIT BREAKER | FA_EEPBA - AIR CIRCUIT BREAKER | 868
FA_EEPBG | GAS CIRCUIT BREAKER | #REF! |  | FA_EEPBA Total |  |  | 868
FA_EEPBL | LIQUID CIRCUIT BREAKER | #REF! |  | FA_EEPBV | VACUUM CIRCUIT BREAKER | FA_EEPBV - VACUUM CIRCUIT BREAKER | 48
FA_EEPBV | VACUUM CIRCUIT BREAKER | 48 |  | FA_EEPBV Total |  |  | 48
FA_EEPCI | IMPRESSED CURRENT CATHODE | #REF! |  | FA_EEPCS | SACRIFICIAL ANODE | FA_EEPCS - SACRIFICIAL ANODE | 114
FA_EEPCS | SACRIFICIAL ANODE | 109 |  | FA_EEPCS Total |  |  | 114
FA_EEPE | ELECTRICAL DISCONNECT SWITCH | #REF! |  | FA_EEPNE | EARTHING BAR | FA_EEPNE - EARTHING BAR | 118
FA_EEPNE | EARTHING BAR | 118 |  | FA_EEPNE Total |  |  | 118
FA_EEPNN | NEUTRAL GROUND RESISTOR | 8 |  | FA_EEPNN | NEUTRAL GROUND RESISTOR | FA_EEPNN - NEUTRAL GROUND RESISTOR | 8
FA_EEPP | PROTECTIVE RELAY | #REF! |  | FA_EEPNN Total |  |  | 8
FA_EEPS | START / STOP SWITCH | 221 |  | FA_EEPS | START / STOP SWITCH | FA_EEPS - START / STOP SWITCH | 328
FA_EEPU | UNINTERRUPTIBLE POWER SUPPLY | 29 |  | FA_EEPS | START / STOP SWITCH | (blank) | 19
FA_EETA | REACTOR / INDUCTOR | 6 |  | FA_EEPS Total |  |  | 347
FA_EETB | BATTERY | 39 |  | FA_EEPU | UNINTERRUPTIBLE POWER SUPPLY | FA_EEPU - UNINTERRUPTIBLE POWER SUPPLY | 29
FA_EETC | BATTERY CHARGER | 57 |  | FA_EEPU Total |  |  | 29
FA_EETD | BUS DUCT / BUS BAR | 70 |  | FA_EETA | REACTOR / INDUCTOR | (blank) | 6
FA_EETFD | DRY TRANSFORMER | #REF! |  | FA_EETA Total |  |  | 6
FA_EETFE | ENCAPSULATED TRANSFORMER | #REF! |  | FA_EETB | BATTERY | FA_EETB - BATTERY | 36
FA_EETFW | WET TRANSFORMER | 20 |  | FA_EETB | UNINTERRUPTIBLE POWER SUPPLY | FA_EEPU - UNINTERRUPTIBLE POWER SUPPLY | 2
FA_EETGA | AC ELECTRIC GENERATOR | 10 |  | FA_EETB | (blank) | FA_EETB - BATTERY | 1
FA_EETGD | DC ELECTRIC GENERATOR | #REF! |  | FA_EETB Total |  |  | 39
FA_EETH | ELECTRICAL SLIP RING | #REF! |  | FA_EETC | BATTERY CHARGER | FA_EETC - BATTERY CHARGER | 57
FA_EETI | ELECTRIC ISOLATOR | 25 |  | FA_EETC Total |  |  | 57
FA_EETL | SOLAR PANEL | #REF! |  | FA_EETD | BUS DUCT / BUS BAR | FA_EETD - BUS DUCT / BUS BAR | 70
FA_EETM | MOTOR CONTROL CENTER | 910 |  | FA_EETD Total |  |  | 70
FA_EETO | POWER / CONTROL MODULE | 5 |  | FA_EETFW | WET TRANSFORMER | FA_EETFW - WET TRANSFORMER | 21
FA_EETP | ELECTRICAL PANEL | 3 |  | FA_EETFW Total |  |  | 21
FA_EETQ | VARIABLE FREQUENCY DRIVE | 64 |  | FA_EETGA | AC ELECTRIC GENERATOR | FA_EETGA - AC ELECTRIC GENERATOR | 10
FA_EETR | POWER RECTIFIER | 15 |  | FA_EETGA Total |  |  | 10
FA_EETS | ELECTRICAL TRANSFER SWITCH | #REF! |  | FA_EETI | ELECTRIC ISOLATOR | FA_EETI - ELECTRIC ISOLATOR | 25
FA_EETT | ELECTRICAL CAPACITOR | #REF! |  | FA_EETI Total |  |  | 25
FA_EETV | POWER INVERTER | #REF! |  | FA_EETM | MOTOR CONTROL CENTER | FA_EETM - MOTOR CONTROL CENTER | 731
FA_EETW | SWITCHGEAR | 170 |  | FA_EETM | MOTOR CONTROL CENTER | FA_EETO - POWER / CONTROL MODULE | 179
FA_EETY | POWER SUPPLY | 28 |  | FA_EETM Total |  |  | 910
FA_INAA | GAS ANALYSER | #REF! |  | FA_EETO | (blank) | FA_EETO - POWER / CONTROL MODULE | 5
FA_INAC | GAS CHROMATOGRAPH | #REF! |  | FA_EETO Total |  |  | 5
FA_INAF | FLOW COMPUTER | #REF! |  | FA_EETP | ELECTRICAL PANEL | (blank) | 3
FA_INAL | LIQUID CHROMATOGRAPH | #REF! |  | FA_EETP Total |  |  | 3
FA_INAM | FLOW METER | 17 |  | FA_EETQ | VARIABLE FREQUENCY DRIVE | FA_EETQ - VARIABLE FREQUENCY DRIVE | 66
FA_INAP | SAMPLER | 10 |  | FA_EETQ Total |  |  | 66
FA_INAS | LIQUID ANALYSER | #REF! |  | FA_EETR | POWER RECTIFIER | FA_EETR - POWER RECTIFIER | 15
FA_INDC | LOCAL CONTROLLER | 9 |  | FA_EETR Total |  |  | 15
FA_INDFA | ACTUATOR | #REF! |  | FA_EETW | SWITCHGEAR | FA_EETW - SWITCHGEAR | 152
FA_INDFD | DAMPER | 20 |  | FA_EETW | (blank) | FA_EETW - SWITCHGEAR | 19
FA_INDFS | SOLENOID VALVE | 230 |  | FA_EETW Total |  |  | 171
FA_INDI | INDICATOR | 1479 |  | FA_EETY | ELECTRIC CABLE | FA_EETY - POWER SUPPLY | 28
FA_INDMS | SENSING ELEMENT | 1691 |  | FA_EETY Total |  |  | 28
FA_INDMT | TRANSMITTER | 2715 |  | FA_INAM | FLOW METER | FA_INAM - FLOW METER | 17
FA_INDP | PRINTER / RECORDER | #REF! |  | FA_INAM Total |  |  | 17
FA_INDS | INSTRUMENT SWITCH | 1553 |  | FA_INAP | (blank) | FA_INAP - SAMPLER | 10
FA_INDT | TRANSDUCER | 33 |  | FA_INAP Total |  |  | 10
FA_INSC | PLC PANEL | 13 |  | FA_INDC | LOCAL CONTROLLER | FA_INDC - LOCAL CONTROLLER | 13
FA_INSD | DISTRIBUTED CONTROL PANEL | 9 |  | FA_INDC Total |  |  | 13
FA_INSJ | JUNCTION BOX | 866 |  | FA_INDFD | DAMPER | FA_INDFD - DAMPER | 22
FA_INSL | LOCAL CONTROL PANEL | 218 |  | FA_INDFD Total |  |  | 22
FA_INSM | METEOROLOGICAL SYSTEM PANEL | #REF! |  | FA_INDFS | SOLENOID VALVE | FA_INDFS - SOLENOID VALVE | 262
FA_INSP | CONDITION MONITORING SYSTEM PANEL | #REF! |  | FA_INDFS Total |  |  | 262
FA_INSS | OPERATOR STATION | 8 |  | FA_INDI | (blank) | FA_INDI - INDICATOR | 1640
FA_INST | TERMINATION RACK | 3 |  | FA_INDI | (blank) | (blank) | 33
FA_INSY | SAFETY INSTRUMENT SYSTEM PANEL | 19 |  | FA_INDI Total |  |  | 1673
FA_PEA | SELF-ACTUATING VALVE | 133 |  | FA_INDMS | BRIDGE | FA_CFSGB - BRIDGE | 1
FA_PEB | BUOYANCY DEVICE | #REF! |  | FA_INDMS | SENSING ELEMENT | FA_INDMS - SENSING ELEMENT | 1805
FA_PEC | DUCT | #REF! |  | FA_INDMS | SENSING ELEMENT | (blank) | 6
FA_PED | DIVERTER | #REF! |  | FA_INDMS | TRANSMITTER - TEMPERATURE (RESISTIVE TEMPERATURE DEVICE TYPE) | FA_INDMT - TRANSMITTER | 8
FA_PEE | EXPANSION DEVICE | #REF! |  | FA_INDMS | (blank) | FA_INDMS - SENSING ELEMENT | 39
FA_PEG | PIPING | 12600 |  | FA_INDMS Total |  |  | 1859
FA_PEH | BUNKERING HOSE | #REF! |  | FA_INDMT | THERMOWELL | FA_PET - THERMOWELL | 1
FA_PEI | BUCKLE INITIATOR | #REF! |  | FA_INDMT | TRANSMITTER | FA_INDMT - TRANSMITTER | 1363
FA_PEL | PIG LAUNCHER / RECEIVER | 1 |  | FA_INDMT | Transmitter - Flow (Coriolis type) | FA_INDMT - TRANSMITTER | 22
FA_PEM | MANIFOLD | 134 |  | FA_INDMT | Transmitter - Flow (Orifice Plate type) | FA_INDMT - TRANSMITTER | 5
FA_PEN | METER PROVER | #REF! |  | FA_INDMT | Transmitter - Flow (Turbine type) | FA_INDMT - TRANSMITTER | 1
FA_PEO | RESTRICTIVE ORIFICE | 482 |  | FA_INDMT | Transmitter - Flow (Ultrasonic type) | FA_INDMT - TRANSMITTER | 10
FA_PEP | BLOWOUT PREVENTER | #REF! |  | FA_INDMT | Transmitter - Flow (Vortex type) | FA_INDMT - TRANSMITTER | 36
FA_PEQ | TURRET EQUIPMENT | #REF! |  | FA_INDMT | Transmitter - Level (Displacer type) | FA_INDMT - TRANSMITTER | 6
FA_PER | RISER | #REF! |  | FA_INDMT | Transmitter - Level (Float type) | FA_INDMT - TRANSMITTER | 1
FA_PESC | CONVENTIONAL PRESSURE SAFETY VALVE | 550 |  | FA_INDMT | Transmitter - Level (Guided Wave Radar type) | FA_INDMT - TRANSMITTER | 149
FA_PESP | PILOT OPERATED PRESSURE SAFETY VALVE | #REF! |  | FA_INDMT | Transmitter - Level (Nucleonic type) | FA_INDMT - TRANSMITTER | 10
FA_PESR | RUPTURE DISC | 49 |  | FA_INDMT | TRANSMITTER - PRESSURE (DIFFERENTIAL PRESSURE TYPE) | FA_INDMT - TRANSMITTER | 181
FA_PESV | VACUUM RELIEF PRESSURE SAFETY VALVE | 15 |  | FA_INDMT | TRANSMITTER - TEMPERATURE (RESISTIVE TEMPERATURE DEVICE TYPE) | FA_INDMT - TRANSMITTER | 593
FA_PET | THERMOWELL | 548 |  | FA_INDMT | VIB VIBRATION TRANSMITTER | FA_INDMT - TRANSMITTER | 204
FA_PEU | UMBILICAL | #REF! |  | FA_INDMT | (blank) | FA_INDMT - TRANSMITTER | 772
FA_PEVB | BALL VALVE | 9510 |  | FA_INDMT | (blank) | (blank) | 19
FA_PEVC | CHECK VALVE | 1564 |  | FA_INDMT Total |  |  | 3373
FA_PEVD | DIAPHRAGM VALVE | 3 |  | FA_INDP | (blank) | FA_INDP - PRINTER / RECORDER | 1
FA_PEVG | GATE VALVE | 2589 |  | FA_INDP Total |  |  | 1
FA_PEVH | SHEAR VALVE | #REF! |  | FA_INDS | INSTRUMENT SWITCH | FA_INDS - INSTRUMENT SWITCH | 1251
FA_PEVL | GLOBE VALVE | 969 |  | FA_INDS | INSTRUMENT SWITCH (HAND OPERATED) | FA_INDS - INSTRUMENT SWITCH | 606
FA_PEVM | MULTIPLE ORIFICE VALVE | 9 |  | FA_INDS | INSTRUMENT SWITCH (HAND OPERATED) | (blank) | 6
FA_PEVN | NEEDLE VALVE | 79 |  | FA_INDS Total |  |  | 1863
FA_PEVS | SUBSURFACE SAFETY VALVE | #REF! |  | FA_INDT | TRANSDUCER | FA_INDT - TRANSDUCER | 33
FA_PEVX | DIVERTER VALVE | 4 |  | FA_INDT Total |  |  | 33
FA_PEVY | BUTTERFLY VALVE | 65 |  | FA_INSC | PLC PANEL | FA_INSC - PLC PANEL | 12
FA_PEW | SWIVEL | #REF! |  | FA_INSC | Progammable Logic Controller | (blank) | 1
FA_PEX | X-MAS TREE / WELLHEAD | #REF! |  | FA_INSC Total |  |  | 13
FA_PEZ | TUBING HANGER | #REF! |  | FA_INSD | DISTRIBUTED CONTROL PANEL | FA_INSD - DISTRIBUTED CONTROL PANEL | 6
FA_REBC | BLOWER, CENTRIFUGAL | 4 |  | FA_INSD | EMERGENCY LIGHTING EMERGENCY LIGHTING PANEL- HIGH | FA_EETP - ELECTRICAL PANEL | 1
FA_REBR | ROTARY LOBE BLOWER | #REF! |  | FA_INSD | INSTRUMENT SWITCH | FA_INDS - INSTRUMENT SWITCH | 1
FA_REC | CENTRIFUGE | 4 |  | FA_INSD | (blank) | SOFT - SOFT TAG | 1
FA_REDH | HYDRAULIC MOTOR | 6 |  | FA_INSD Total |  |  | 9
FA_REDP | PNEUMATIC MOTOR | 26 |  | FA_INSJ | JUNCTION BOX | FA_INSJ - JUNCTION BOX | 866
FA_REDT | TOP DRIVE | #REF! |  | FA_INSJ Total |  |  | 866
FA_REEG | GAS FUEL COMBUSTION ENGINE | #REF! |  | FA_INSL | LOCAL CONTROL PANEL | FA_INSL - LOCAL CONTROL | 1
FA_REEL | LIQUID FUEL COMBUSTION ENGINE | 4 |  | FA_INSL | LOCAL CONTROL PANEL | FA_INSL - LOCAL CONTROL PANEL | 90
FA_REFA | AXIAL FAN | 24 |  | FA_INSL | LOCAL CONTROL PANEL | FA_SQFC - EQUIPMENT CABINET | 124
FA_REFC | CENTRIFUGAL FAN | 131 |  | FA_INSL | LOCAL CONTROL PANEL | (blank) | 3
FA_REI | MIXER | #REF! |  | FA_INSL Total |  |  | 218
FA_REMA | AXIAL COMPRESSOR | #REF! |  | FA_INSS | OPERATOR STATION | FA_INSS - OPERATOR STATION | 12
FA_REMC | CENTRIFUGAL COMPRESSOR | 3 |  | FA_INSS Total |  |  | 12
FA_REMR | RECIPROCATING COMPRESSOR | 6 |  | FA_INST | (blank) | FA_INST - TERMINATION RACK | 3
FA_REMT | ROTARY COMPRESSOR | 11 |  | FA_INST Total |  |  | 3
FA_RENG | GAS TURBINE | 10 |  | FA_INSY | Master Fire Panel Master Firel Panel | FA_INSY - SAFETY INSTRUMENT SYSTEM PANEL | 2
FA_RENS | STEAM TURBINE | #REF! |  | FA_INSY | Master Fire Panel Master Firel Panel | FA_SQFC - EQUIPMENT CABINET | 17
FA_REPB | BEAM PUMP | #REF! |  | FA_INSY Total |  |  | 19
FA_REPC | CENTRIFUGAL PUMP | 275 |  | FA_PEA | PRESSURE REGULATOR | (blank) | 11
FA_REPD | POSITIVE DISPLACEMENT PUMP | 39 |  | FA_PEA | SELF-ACTUATING VALVE | FA_PEA - SELF-ACTUATING VALVE | 139
FA_REPG | PROGRESSIVE CAVITY PUMP | #REF! |  | FA_PEA | (blank) | (blank) | 2
FA_REPR | RECIPROCATING PUMP | #REF! |  | FA_PEA Total |  |  | 152
FA_REPV | CONTROLLED VOLUME PUMP | #REF! |  | FA_PEC | DUCT | FA_PEC - DUCT | 1
FA_RER | RAKE / SCRAPER | 2 |  | FA_PEC Total |  |  | 1
FA_RES | SOOTBLOWER | #REF! |  | FA_PEG | PIPING | FA_PEG - PIPING | 33130
FA_RETC | CLUTCH | #REF! |  | FA_PEG | (blank) | FA_PEG - PIPING | 129
FA_RETG | GEARBOX | 5 |  | FA_PEG | (blank) | (blank) | 49
FA_RETH | HYDRAULIC / TORQUE CONVERTER | #REF! |  | FA_PEG Total |  |  | 33308
FA_RETP | COUPLING | 5 |  | FA_PEL | PIG LAUNCHER / RECEIVER | FA_PEL - PIG LAUNCHER / RECEIVER | 1
FA_RETV | CONTINOUSLY VARIABLE TRANSMISSION | #REF! |  | FA_PEL Total |  |  | 1
FA_REUC | CHEMICAL INJECTION SYSTEM | 1 |  | FA_PEM | MANIFOLD | FA_PEM - MANIFOLD | 111
FA_REUH | HYDRAULIC SYSTEM | #REF! |  | FA_PEM | (blank) | FA_PEM - MANIFOLD | 23
FA_REXA | AXIAL TURBO EXPANDER | #REF! |  | FA_PEM Total |  |  | 134
FA_REXC | CENTRIFUGAL TURBO EXPANDER | #REF! |  | FA_PEO | RESTRICTIVE ORIFICE | FA_PEO - RESTRICTIVE ORIFICE | 566
FA_REZ | ROTARY DRUM FILTER | #REF! |  | FA_PEO Total |  |  | 566
FA_SEA | AIR DRYER | #REF! |  | FA_PESC | CONVENTIONAL PRESSURE SAFETY VALVE | FA_PESC - CONVENTIONAL PRESSURE SAFETY VALVE | 684
FA_SEBF | FIRETUBE BOILER | #REF! |  | FA_PESC | Reg - High Serv Pressure Safety Valve - Reg - High Service | (blank) | 12
FA_SEBH | WASTE HEAT BOILER | #REF! |  | FA_PESC | Reg - Low Serv Pressure Safety Valve - Reg - Low Service | (blank) | 1
FA_SEBW | WATERTUBE BOILER | #REF! |  | FA_PESC Total |  |  | 697
FA_SEC | CYCLONE | 6 |  | FA_PESR | RUPTURE DISC | FA_PESR - RUPTURE DISC | 52
FA_SED | DRAIN POT | #REF! |  | FA_PESR | RUPTURE DISC | (blank) | 6
FA_SEE | EJECTOR / EDUCTOR | 3 |  | FA_PESR Total |  |  | 58
FA_SEFB | BASKET STRAINER FILTER | 310 |  | FA_PESV | VACUUM RELIEF PRESSURE SAFETY VALVE | FA_PESV - VACUUM RELIEF PRESSURE SAFETY VALVE | 24
FA_SEFC | COALESCER FILTER | #REF! |  | FA_PESV Total |  |  | 24
FA_SEFE | ELEMENT FILTER | 194 |  | FA_PET | THERMOWELL | FA_PET - THERMOWELL | 642
FA_SEFM | MEDIA FILTER | #REF! |  | FA_PET Total |  |  | 642
FA_SEFP | ELECTROSTATIC PRECIPITATOR FILTER | #REF! |  | FA_PEVB | BALL VALVE | FA_PEVB - BALL VALVE | 15037
FA_SEFR | REVERSE OSMOSIS FILTER | #REF! |  | FA_PEVB | BALL VALVE | (blank) | 76
FA_SEFS | SCREEN FILTER | 18 |  | FA_PEVB | BDV VALVE - EMERGENCY SHUTDOWN | FA_PEVB - BALL VALVE | 52
FA_SEHC | CALORIFIER HEAT EXCHANGER | #REF! |  | FA_PEVB | CONTROL VALVE CONTROL - GENERAL | FA_PEVB - BALL VALVE | 901
FA_SEHF | FINNED COIL HEAT EXCHANGER | 70 |  | FA_PEVB | CONTROL VALVE CONTROL - GENERAL | LOOP - LOOP TAG | 5
FA_SEHP | PLATE & FRAME HEAT EXCHANGER | #REF! |  | FA_PEVB | GATE VALVE | FA_PEVG - GATE VALVE | 1
FA_SEHR | RECUPERATOR HEAT EXCHANGER | #REF! |  | FA_PEVB | MOV VALVE - MOV | FA_PEVB - BALL VALVE | 27
FA_SEHS | SPIRAL HEAT EXCHANGER | 48 |  | FA_PEVB | MOV VALVE - MOV | (blank) | 2
FA_SEHT | SHELL & TUBE HEAT EXCHANGER | 51 |  | FA_PEVB | SDV VALVE - EMERGENCY SHUTDOWN | FA_PEVB - BALL VALVE | 1
FA_SEI | BIN / HOPPER | #REF! |  | FA_PEVB Total |  |  | 16102
FA_SEL | FLAME ARRESTOR | 53 |  | FA_PEVC | CHECK VALVE | FA_PEVC - CHECK VALVE | 1798
FA_SEM | FLARE | 5 |  | FA_PEVC | CHECK VALVE | (blank) | 24
FA_SENF | FIRED HEATER FURNACE | 4 |  | FA_PEVC Total |  |  | 1822
FA_SENI | INCINERATOR FURNACE | #REF! |  | FA_PEVD | DIAPHRAM VALVE | FA_PEVD - DIAPHRAGM VALVE | 3
FA_SENT | THERMAL OXIDIZER FURNACE | #REF! |  | FA_PEVD Total |  |  | 3
FA_SEPA | ACCUMULATOR | 192 |  | FA_PEVG | BALL VALVE | FA_PEVB - BALL VALVE | 8
FA_SEPC | CYLINDER | 59 |  | FA_PEVG | BALL VALVE | FA_PEVG - GATE VALVE | 1
FA_SEPHC | CONDENSER VESSEL | 2 |  | FA_PEVG | CONTROL VALVE CONTROL - GENERAL | FA_PEVG - GATE VALVE | 6
FA_SEPHS | SEPARATOR VESSEL | 190 |  | FA_PEVG | GATE VALVE | FA_PEVG - GATE VALVE | 4934
FA_SEPHV | VAPORISER VESSEL | #REF! |  | FA_PEVG | MOV VALVE - MOV | FA_PEVG - GATE VALVE | 3
FA_SEPRL | FLUIDISED BED REACTOR | #REF! |  | FA_PEVG Total |  |  | 4952
FA_SEPRR | REGENERATOR REACTOR | #REF! |  | FA_PEVL | GLOBE VALVE | FA_PEVB - BALL VALVE | 19
FA_SEPRX | FIXED BED REACTOR | #REF! |  | FA_PEVL | GLOBE VALVE | FA_PEVG - GATE VALVE | 2
FA_SEPVA | ABSORBER COLUMN | #REF! |  | FA_PEVL | GLOBE VALVE | FA_PEVG - GLOBE VALVE | 1
FA_SEPVC | CONTACTOR COLUMN | #REF! |  | FA_PEVL | GLOBE VALVE | FA_PEVL - GLOBE VALVE | 1718
FA_SEPVS | SCRUBBER COLUMN | #REF! |  | FA_PEVL Total |  |  | 1740
FA_SEPVT | STRIPPER COLUMN | #REF! |  | FA_PEVM | MULTIPLE ORIFICE VALVE | FA_PEVM - MULTIPLE ORIFICE VALVE | 10
FA_SER | STATIC MIXER | #REF! |  | FA_PEVM | MULTIPLE ORIFICE VALVE | (blank) | 9
FA_SES | PULSATION DAMPENER | 72 |  | FA_PEVM Total |  |  | 19
FA_SETAC | CLOSED ROOF ATMOSPHERIC TANK | 60 |  | FA_PEVN | BUTTERFLY VALVE | FA_PEVY - NEEDLE VALVE | 12
FA_SETAF | FLOATING ROOF ATMOSPHERIC TANK | #REF! |  | FA_PEVN | NEEDLE VALVE | FA_PEVN - NEEDLE VALVE | 173
FA_SETAO | OPEN ROOF ATMOSPHERIC TANK | #REF! |  | FA_PEVN | NEEDLE VALVE | (blank) | 69
FA_SETAP | PIT / SUMP | 40 |  | FA_PEVN Total |  |  | 254
FA_SETAR | RESERVOIR | #REF! |  | FA_PEVX | DIVERTER VALVE | FA_PEVX - DIVERTER VALVE | 4
FA_SETPC | CYLINDRICAL PRESSURISED TANK | 11 |  | FA_PEVX | (blank) | FA_PEVX - DIVERTER VALVE | 2
FA_SETPS | SPHERICAL PRESSURISED TANK | #REF! |  | FA_PEVX Total |  |  | 6
FA_SEV | LOUVRE | #REF! |  | FA_PEVY | BUTTERFLY VALVE | FA_PEVY - BUTTERFLY VALVE | 65
FA_SEY | HYDRAULIC HATCH | #REF! |  | FA_PEVY Total |  |  | 65
FA_SEZ | SILENCER / MUFFLER | 64 |  | FA_REBC | CENTRIFUGAL BLOWER | FA_REBC - BLOWER, CENTRIFUGAL | 13
FA_SQFC | EQUIPMENT CABINET | 21 |  | FA_REBC Total |  |  | 13
FA_SQFDD | DUST DETECTOR | #REF! |  | FA_REC | CENTRIFUGE | FA_REC - CENTRIFUGE | 4
FA_SQFDF | FLAME DETECTOR | 420 |  | FA_REC Total |  |  | 4
FA_SQFDG | FIXED GAS DETECTOR | 739 |  | FA_REDH | HYDRAULIC MOTOR | FA_REDH - HYDRAULIC MOTOR | 6
FA_SQFDH | PERSONAL H2S MONITOR | #REF! |  | FA_REDH Total |  |  | 6
FA_SQFDM | MOTION DETECTOR | #REF! |  | FA_REDP | PNEUMATIC MOTOR | FA_REDP - PNEUMATIC MOTOR | 26
FA_SQFDP | PORTABLE GAS MONITOR | #REF! |  | FA_REDP Total |  |  | 26
FA_SQFDR | PERSONAL RADIATION MONITOR | #REF! |  | FA_REEL | STANDBY ENGINE LIQUID FUEL COMBUSTION ENGINE - STANDBY | FA_REEL - LIQUID FUEL COMBUSTION ENGINE | 5
FA_SQFDS | SMOKE DETECTOR | 140 |  | FA_REEL Total |  |  | 5
FA_SQFFD | FIREWATER DELUGE SYSTEM | 26 |  | FA_REFA | AXIAL FAN | FA_REFA - AXIAL FAN | 32
FA_SQFFE | FIRE EXTINGUISHER | #REF! |  | FA_REFA Total |  |  | 32
FA_SQFFF | FIRE FIGHTING FOAM SYSTEM | #REF! |  | FA_REFC | CENTRIFUGAL FAN | FA_REFC - CENTRIFUGAL FAN | 162
FA_SQFFH | FIRE HOSE | 3 |  | FA_REFC Total |  |  | 162
FA_SQFFM | FIRE WATER/FOAM MONITOR | 23 |  | FA_REI | MIXER | FA_REI - MIXER | 32
FA_SQFFS | FIRE EXTINGUISHING SYSTEM | #REF! |  | FA_REI Total |  |  | 32
FA_SQFFT | FIRE TRUCK | #REF! |  | FA_REMC | CENTRIFUGAL COMPRESSOR | FA_REMC - CENTRIFUGAL COMPRESSOR | 6
FA_SQFFY | FIRE HYDRANT | 118 |  | FA_REMC Total |  |  | 6
FA_SQFRA | EMERGENCY ALARM DEVICE | 244 |  | FA_REMR | RECIPROCATING COMPRESSOR | FA_REMR - RECIPROCATING COMPRESSOR | 6
FA_SQFRB | BREATHING AIR BOTTLE | #REF! |  | FA_REMR Total |  |  | 6
FA_SQFRC | DESCENT DEVICE | #REF! |  | FA_REMT | ROTARY COMPRESSOR | FA_REMT - ROTARY COMPRESSOR | 11
FA_SQFRD | AUTOMATED EXTERNAL DEFIBRILLATOR | #REF! |  | FA_REMT Total |  |  | 11
FA_SQFRE | SAFETY SHOWER OR EYE BATH | 20 |  | FA_RENG | GAS TURBINE | FA_RENG - GAS TURBINE | 14
FA_SQFRJ | LIFEJACKET | #REF! |  | FA_RENG | SOLAR GAS TURBINE | FA_RENG - GAS TURBINE | 2
FA_SQFRK | PERSONNEL BASKET | #REF! |  | FA_RENG Total |  |  | 16
FA_SQFRL | LIFEBOAT AND DAVIT | #REF! |  | FA_REPC | CENTRIFUGAL PUMP | FA_REPC - CENTRIFUGAL PUMP | 349
FA_SQFRP | SELF-CONTAINED BREATHING APPARATUS | #REF! |  | FA_REPC | FIREWATER CENTRIFUGAL PUMP - FIREWATER | FA_REPC - CENTRIFUGAL PUMP | 14
FA_SQFRR | LIFERAFT | #REF! |  | FA_REPC | POSITIVE DISPLACEMENT PUMP | FA_REPD - POSITIVE DISPLACEMENT PUMP | 4
FA_SQFRS | BREATHING AIR SYSTEM | #REF! |  | FA_REPC Total |  |  | 367
FA_SQFRT | RESCUE BOAT | #REF! |  | FA_REPD | POSITIVE DISPLACEMENT PUMP | FA_REPD - POSITIVE DISPLACEMENT PUMP | 39
FA_SQFRV | SURVIVAL SUIT | #REF! |  | FA_REPD Total |  |  | 39
FA_SQFRY | LIFEBUOY | #REF! |  | FA_RER | (blank) | (blank) | 4
FA_SQL | LABORATORY EQUIPMENT | #REF! |  | FA_RER Total |  |  | 4
FA_SQMC | PORTABLE COMPRESSOR | #REF! |  | FA_RETG | BREATHING AIR SYSTEM | FA_SQFRS - BREATHING AIR SYSTEM | 5
FA_SQMD | TESTING DEVICE | #REF! |  | FA_RETG Total |  |  | 5
FA_SQMG | PORTABLE GENERATOR | #REF! |  | FA_RETP | (blank) | FA_RETP - COUPLING | 5
FA_SQML | PORTABLE LIGHT PLANT | #REF! |  | FA_RETP Total |  |  | 5
FA_SQMT | MAINTENANCE TOOL | 2 |  | FA_REUC | CHEMICAL INJECTION SYSTEM | FA_REUC - CHEMICAL INJECTION SYSTEM | 1
FA_SQMW | WELDING MACHINE | #REF! |  | FA_REUC Total |  |  | 1
FA_SQNB | SIGNAL BUOY | #REF! |  | FA_SEA | AIR DRYER | FA_SEA - AIR DRYER | 6
FA_SQNL | NAVIGATION LIGHT | #REF! |  | FA_SEA Total |  |  | 6
FA_SQNP | POSITIONING EQUIPMENT | #REF! |  | FA_SEC | HYDROCYCLONE | FA_SEC - CYCLONE | 6
FA_SQR | OIL SPILL RESPONSE EQUIPMENT | #REF! |  | FA_SEC Total |  |  | 6
FA_SQTA | PUBLIC ADDRESS AND ALARM SYSTEM | 60 |  | FA_SEE | EJECTOR / EDUCTOR | FA_SEE - EJECTOR / EDUCTOR | 3
FA_SQTB | NON DIRECTIONAL BEACON | 169 |  | FA_SEE Total |  |  | 3
FA_SQTC | COMPASS | #REF! |  | FA_SEFB | BASKET STRAINER FILTER | FA_SEFB - BASKET STRAINER FILTER | 323
FA_SQTD | RADAR | #REF! |  | FA_SEFB Total |  |  | 323
FA_SQTE | TELECOMMUNICATION CABINET | 33 |  | FA_SEFE | ELEMENT FILTER | FA_SEFE - ELEMENT FILTER | 229
FA_SQTF | FACSIMILE MACHINE | #REF! |  | FA_SEFE Total |  |  | 229
FA_SQTH | PATCH PANEL | 95 |  | FA_SEFS | COALESCER FILTER | FA_SEFC - COALESCER FILTER | 12
FA_SQTI | INTERCOM SYSTEM | #REF! |  | FA_SEFS | SCREEN FILTER | FA_SEFS - SCREEN FILTER | 27
FA_SQTL | LOUDSPEAKER | 487 |  | FA_SEFS Total |  |  | 39
FA_SQTM | AMPLIFIER | #REF! |  | FA_SEHF | FINNED COIL HEAT EXCHANGER | FA_SEHF - FINNED COIL HEAT EXCHANGER | 112
FA_SQTN | ANTENNA | 3 |  | FA_SEHF Total |  |  | 112
FA_SQTOF | FIXED RADIO | 6 |  | FA_SEHS | SPIRAL HEAT EXCHANGER | FA_SEHS - SPIRAL HEAT EXCHANGER | 48
FA_SQTOP | PAGER | #REF! |  | FA_SEHS Total |  |  | 48
FA_SQTOR | PORTABLE RADIO | #REF! |  | FA_SEHT | ELECTRIC HEATER | FA_EECH - ELECTRIC HEATER | 14
FA_SQTP | COMPUTER PERIPHERAL | 104 |  | FA_SEHT | SHELL & TUBE HEAT EXCHANGER | FA_SEHT - SHELL & TUBE HEAT EXCHANGER | 6
FA_SQTR | PROXIMITY READER | #REF! |  | FA_SEHT | SHELL & TUBE HEAT EXCHANGER | FA_SEHT - SHELLTUBE HEAT EXCHANGER | 35
FA_SQTS | TELEPHONE OR MULTIMEDIA EQUIPMENT | 101 |  | FA_SEHT | (blank) | FA_SEHT - SHELLTUBE HEAT EXCHANGER | 1
FA_SQTT | SATELLITE EQUIPMENT | #REF! |  | FA_SEHT Total |  |  | 56
FA_SQTV | CCTV CAMERA UNIT | 167 |  | FA_SEL | LOSS CONTROL - FLAME ARRESTOR | FA_SEL - FLAME ARRESTOR | 51
FA_SQTW | WIRELESS COMMUNICATION OR CONTROL EQUIPMENT | 17 |  | FA_SEL | LOSS CONTROL - FLAME ARRESTOR | (blank) | 2
FA_SQTX | MULTIPLEXER | #REF! |  | FA_SEL Total |  |  | 53
FA_SQTY | RECEIVER / TRANSMITTER | 4 |  | FA_SEM | FLARE | FA_SEM - FLARE | 5
FA_SQUC | CLEANING EQUIPMENT | #REF! |  | FA_SEM Total |  |  | 5
FA_SQUE | EXERCISE EQUIPMENT | #REF! |  | FA_SENF | FIRED HEATER FURNACE | FA_SENF - FIRED HEATER FURNACE | 4
FA_SQUG | GALLEY EQUIPMENT | #REF! |  | FA_SENF Total |  |  | 4
FA_SRFRN | VENTILATOR | #REF! |  | FA_SEPA | ACCUMULATOR | FA_SEPA - ACCUMULATOR | 186
FA_SYLH | SYSTEM LEVEL HIERARCHY | 316 |  | FA_SEPA | ACCUMULATOR | (blank) | 6
FA_WECM | MOBILE CRANE | #REF! |  | FA_SEPA Total |  |  | 192
FA_WECO | OVERHEAD CRANE | 11 |  | FA_SEPC | CYLINDER | FA_SEPC - CYLINDER | 45
FA_WECP | PEDESTAL CRANE | #REF! |  | FA_SEPC | (blank) | FA_SEPC - CYLINDER | 18
FA_WECT | TOWER CRANE | #REF! |  | FA_SEPC Total |  |  | 63
FA_WED | LOADING ARM | #REF! |  | FA_SEPHC | CONDENSER | FA_SEPHC - CONDENSER VESSEL | 2
FA_WEHC | CUTTING DRILL | #REF! |  | FA_SEPHC Total |  |  | 2
FA_WEHR | CRUSHER / SHREDDER | #REF! |  | FA_SEPHS | SEPARATOR VESSEL | FA_SEPHS - SEPARATOR VESSEL | 209
FA_WEHS | SHAKER | #REF! |  | FA_SEPHS Total |  |  | 209
FA_WEHY | CONVEYOR | 2 |  | FA_SES | PULSATION DAMPENER | FA_SES - PULSATION DAMPENER | 132
FA_WELB | CHAIN BLOCK | #REF! |  | FA_SES Total |  |  | 132
FA_WELC | CABLE OR CHAIN | #REF! |  | FA_SETAC | CONE ROOF ATMOSPHERIC TANK | FA_SETAC - CLOSED ROOF ATMOSPHERIC TANK | 82
FA_WELD | DAVIT | #REF! |  | FA_SETAC Total |  |  | 82
FA_WELE | ELEVATOR | #REF! |  | FA_SETAP | PIT / SUMP | FA_SETAP - PIT / SUMP | 49
FA_WELF | FORKLIFT | #REF! |  | FA_SETAP Total |  |  | 49
FA_WELG | SLING | #REF! |  | FA_SETPC | CYLINDRICAL PRESSURE TANK | FA_SETPC - CYLINDRICAL PRESSURISED TANK | 10
FA_WELH | HOIST | #REF! |  | FA_SETPC | CYLINDRICAL PRESSURE TANK | (blank) | 1
FA_WELJ | JACK | #REF! |  | FA_SETPC Total |  |  | 11
FA_WELM | MAN LIFT / BASKET / CHERRY PICKER | #REF! |  | FA_SEZ | SILENCER / MUFFLER | FA_SEZ - SILENCER / MUFFLER | 63
FA_WELN | CONTAINER | #REF! |  | FA_SEZ | (blank) | FA_SEZ - SILENCER / MUFFLER | 1
FA_WELP | SPREADER FRAME / BAR | #REF! |  | FA_SEZ Total |  |  | 64
FA_WELS | SHEAVE OR PULLEY | #REF! |  | FA_SQFC | (blank) | FA_SQFC - EQUIPMENT CABINET | 21
FA_WELT | MONORAIL / TROLLEY | #REF! |  | FA_SQFC Total |  |  | 21
FA_WELW | WINCH | #REF! |  | FA_SQFDF | CONTROL ROOM | FA_CFBC - CONTROL ROOM | 12
FA_WESR | REMOTE OPERATED VEHICLE (ROV) | #REF! |  | FA_SQFDF | FLAME DETECTORS (UR / IR / CCTV TYPES) | FA_SQFDF - FLAME DETECTOR | 451
FA_WEST | RUNNING TOOL | #REF! |  | FA_SQFDF | HEAT DETECTOR | FA_SQFDF - FLAME DETECTOR | 14
FA_WETRA | AUTOMOBILE | #REF! |  | FA_SQFDF | OFFICE BUILDING | FA_CFBO - OFFICE BUILDING | 2
FA_WETRC | ROAD COMPACTOR | #REF! |  | FA_SQFDF | OIL MIST DETECTOR (INFRARED) | FA_SQFDF - FLAME DETECTOR | 6
FA_WETRL | LAWNMOWER | #REF! |  | FA_SQFDF Total |  |  | 485
FA_WETRO | TRACTOR | #REF! |  | FA_SQFDG | FIXED GAS DETECTOR (ELECTROCHEMICAL H2S) | FA_SQFDG - FIXED GAS DETECTOR | 30
FA_WETRR | TRAILER | #REF! |  | FA_SQFDG | FIXED GAS DETECTOR (POINT INFRARED) | FA_SQFDG - FIXED GAS DETECTOR | 649
FA_WETRS | ROAD SCRAPER | #REF! |  | FA_SQFDG | NO DEVICE FIRE AND GAS DETECTOR - HYDROCARBON | FA_SQFDG - FIXED GAS DETECTOR | 18
FA_WETRT | TRUCK | #REF! |  | FA_SQFDG | (blank) | FA_SQFDG - FIXED GAS DETECTOR | 61
FA_WETRW | ROAD SWEEPER | #REF! |  | FA_SQFDG Total |  |  | 758
FA_WETWB | BARGE | #REF! |  | FA_SQFDS | SMOKE DETECTOR (HIGH SENSITIVITY) | FA_SQFDS - SMOKE DETECTOR | 45
FA_WETWF | MARINE FENDER | #REF! |  | FA_SQFDS | SMOKE DETECTOR (IONISATION) | FA_SQFDS - SMOKE DETECTOR | 12
FA_WETWT | MARINE THRUSTER | #REF! |  | FA_SQFDS | SMOKE DETECTOR (OPTICAL) | FA_SQFDS - SMOKE DETECTOR | 88
FA_WETWV | MARINE VESSEL | #REF! |  | FA_SQFDS Total |  |  | 145
|  |  |  | FA_SQFFD | FIREWATER DELUGE SYSTEM | FA_SQFFD - FIREWATER DELUGE SYSTEM | 43
|  |  |  | FA_SQFFD Total |  |  | 43
|  |  |  | FA_SQFFH | FIRE HOSE | FA_SQFFH - FIRE HOSE | 3
|  |  |  | FA_SQFFH Total |  |  | 3
|  |  |  | FA_SQFFM | FIRE WATER/FOAM MONITOR | FA_SQFFM - FIRE WATER/FOAM MONITOR | 23
|  |  |  | FA_SQFFM Total |  |  | 23
|  |  |  | FA_SQFFY | FIRE HYDRANT | FA_SQFFY - FIRE HYDRANT | 118
|  |  |  | FA_SQFFY Total |  |  | 118
|  |  |  | FA_SQFRA | MANUALLY ACTIVATED CALL POINTS | FA_SQFRA - EMERGENCY ALARM DEVICE | 248
|  |  |  | FA_SQFRA Total |  |  | 248
|  |  |  | FA_SQFRE | SAFETY SHOWER OR EYE BATH | FA_SQFRE - SAFETY SHOWER OR EYE BATH | 36
|  |  |  | FA_SQFRE Total |  |  | 36
|  |  |  | FA_SQMC | PORTABLE COMPRESSOR | FA_SQMC - PORTABLE COMPRESSOR | 1
|  |  |  | FA_SQMC Total |  |  | 1
|  |  |  | FA_SQMT | (blank) | (blank) | 2
|  |  |  | FA_SQMT Total |  |  | 2
|  |  |  | FA_SQTA | (blank) | FA_SQTA - PUBLIC ADDRESS AND ALARM SYSTEM | 87
|  |  |  | FA_SQTA Total |  |  | 87
|  |  |  | FA_SQTB | NON DIRECTIONAL BEACON | FA_SQTB - NON DIRECTIONAL BEACON | 172
|  |  |  | FA_SQTB Total |  |  | 172
|  |  |  | FA_SQTE | TELECOMMUNICATION CABINET | FA_SQTE - TELECOMMUNICATION CABINET | 35
|  |  |  | FA_SQTE Total |  |  | 35
|  |  |  | FA_SQTH | PATCH PANEL | FA_SQTH - PATCH PANEL | 59
|  |  |  | FA_SQTH | (blank) | FA_SQTH - PATCH PANEL | 36
|  |  |  | FA_SQTH Total |  |  | 95
|  |  |  | FA_SQTL | LOUDSPEAKER | FA_SQTL - LOUDSPEAKER | 487
|  |  |  | FA_SQTL Total |  |  | 487
|  |  |  | FA_SQTN | TELECOMMS - ANTENNA | FA_SQTN - ANTENNA | 2
|  |  |  | FA_SQTN | TELECOMMS - ANTENNA | (blank) | 1
|  |  |  | FA_SQTN Total |  |  | 3
|  |  |  | FA_SQTOF | MF HF RADIO MF HF - FIXED RADIO | FA_SQTOF - FIXED RADIO | 6
|  |  |  | FA_SQTOF Total |  |  | 6
|  |  |  | FA_SQTP | (blank) | (blank) | 108
|  |  |  | FA_SQTP Total |  |  | 108
|  |  |  | FA_SQTS | TELEPHONE SYSTEMS EQUIPMENT | FA_SQTS - TELEPHONE OR MULTIMEDIA EQUIPMENT | 101
|  |  |  | FA_SQTS | TELEPHONE SYSTEMS EQUIPMENT | (blank) | 21
|  |  |  | FA_SQTS Total |  |  | 122
|  |  |  | FA_SQTV | CCTV CAMERA UNIT | FA_SQTV - CCTV CAMERA UNIT | 167
|  |  |  | FA_SQTV Total |  |  | 167
|  |  |  | FA_SQTW | THERMOWELL | FA_PET - THERMOWELL | 22
|  |  |  | FA_SQTW | WIRELESS ACCESS / GATEWAY | FA_SQTW - WIRELESS COMMUNICATION OR CONTROL EQUIPMENT | 17
|  |  |  | FA_SQTW Total |  |  | 39
|  |  |  | FA_SQTY | RECEIVER / TRANSMITTER | FA_SQTY - RECEIVER / TRANSMITTER | 4
|  |  |  | FA_SQTY Total |  |  | 4
|  |  |  | FA_SYLH | (blank) | FA_EECMS - AC SYNCHRONOUS ELECTRIC MOTOR | 1
|  |  |  | FA_SYLH | (blank) | FA_SYLH - SYSTEM LEVEL HIERARCHY | 381
|  |  |  | FA_SYLH | (blank) | (blank) | 245
|  |  |  | FA_SYLH Total |  |  | 627
|  |  |  | FA_WECO | OVERHEAD CRANE | FA_WECO - OVERHEAD CRANE | 13
|  |  |  | FA_WECO Total |  |  | 13
|  |  |  | FA_WEHY | (blank) | FA_WEHY - CONVEYOR | 4
|  |  |  | FA_WEHY Total |  |  | 4
|  |  |  | LOOP | WET TRANSFORMER | LOOP - LOOP TAG | 8
|  |  |  | LOOP | (blank) | LOOP - LOOP TAG | 5949
|  |  |  | LOOP Total |  |  | 5957
|  |  |  | SOFT | CONE ROOF ATMOSPHERIC TANK | FA_SETAC - CLOSED ROOF ATMOSPHERIC TANK | 1
|  |  |  | SOFT | ELECTRIC HEATER | FA_EECH - ELECTRIC HEATER | 14
|  |  |  | SOFT | GLOBE VALVE | FA_PEVL - GLOBE VALVE | 1
|  |  |  | SOFT | START / STOP SWITCH | FA_EEPS - START / STOP SWITCH | 1
|  |  |  | SOFT | TRANSMITTER | FA_INDMT - TRANSMITTER | 112
|  |  |  | SOFT | (blank) | FA_SQTA - PUBLIC ADDRESS AND ALARM SYSTEM | 40
|  |  |  | SOFT | (blank) | LOOP - LOOP TAG | 3
|  |  |  | SOFT | (blank) | SOFT - SOFT TAG | 16072
|  |  |  | SOFT | (blank) | (blank) | 21
|  |  |  | SOFT Total |  |  | 16265
|  |  |  | (blank) | (blank) | (blank) | 7
|  |  |  | (blank) Total |  |  | 7
|  |  |  | Grand Total |  |  | 104572

## Sheet10
Data returned for Distinct Count of Discipline, FA_EECH (First 1000 rows).
AssetRegisterTbl[Functional location] | AssetRegisterTbl[Function Location Description] | AssetRegisterTbl[Object type2] | AssetRegisterTbl[STATUS] | AssetRegisterTbl[UMCL PLUS] | AssetRegisterTbl[ISO CODE] | AssetRegisterTbl[SIL Input] | AssetRegisterTbl[SIL Output] | AssetRegisterTbl[SIS Tag Abbreviation] | AssetRegisterTbl[Discipline] | AssetRegisterTbl[SYSTEMID]
E-EEH-8731 | JW HEATER | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 87
E-EEH-8732 | JW HEATER | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 87
E-PM-3005B-EEH01 | SPACE HEATERS | FA_EECH | VALID |  |  | N | N |  | ELEC | 30
E-PM-3005A-EEH01 | SPACE HEATERS | FA_EECH | VALID |  |  | N | N |  | ELEC | 30
E-H-4602B | FUEL GAS HEATER | FA_EECH | VALID | 1450 | HBEH | N | N |  | MECH | 46
E-H-4602A | FUEL GAS HEATER | FA_EECH | VALID | 1450 | HBEH | N | N |  | MECH | 46
R-H-4521 | LP FUEL GAS HEATER | FA_EECH | VALID | 1450 | HBEH | N | N |  | MECH | 45
R-H-4522 | HP FUEL GAS HEATER | FA_EECH | VALID | 1450 | HBEH | N | N |  | MECH | 45
E-H-4601 | AUXILIARY GAS HEATER | FA_EECH | VALID | 1450 | HBEH | N | N |  | MECH | 46
E-H-4401 | LP FLARE KO DRUM HEATER | FA_EECH | VALID | 1450 | HBEH | N | N |  | MECH | 44
E-H-4201 | HP FLARE KO DRUM HEATER | FA_EECH | VALID | 1450 | HBEH | N | N |  | MECH | 42
R-H-2521 | REGENERATION GAS HEATER | FA_EECH | VALID | 1450 | HBEH | N | N |  | MECH | 25
E-GE-8731-EEH01 | ANTI CONDENSATION HEATER | FA_EECH | VALID |  |  | N | N |  | ELEC | 87
E-H-5212 | CHEMICAL CLEANING HEATER | FA_EECH | VALID | 1450 | HBEH | N | N |  | MECH | 52
E-H-9141B | E-G-9141 - LUBE OIL HEATER | FA_EECH |  | 1450 | HBEH | N | N |  | MECH | 91
E-H-9141A | E-G-9141 - LUBE OIL HEATER | FA_EECH |  | 1450 | HBEH | N | N |  | MECH | 91
E-H-9131B | E-G-9131 - LUBE OIL HEATER | FA_EECH |  | 1450 | HBEH | N | N |  | MECH | 91
E-H-9131A | E-G-9131 - LUBE OIL HEATER | FA_EECH |  | 1450 | HBEH | N | N |  | MECH | 91
E-H-9121B | E-G-9121 - LUBE OIL HEATER | FA_EECH |  | 1450 | HBEH | N | N |  | MECH | 91
E-H-9121A | E-G-9121 - LUBE OIL HEATER | FA_EECH |  | 1450 | HBEH | N | N |  | MECH | 91
E-H-9111B | E-G-9111 - LUBE OIL HEATER | FA_EECH |  | 1450 | HBEH | N | N |  | MECH | 91
E-H-9111A | E-G-9111 - LUBE OIL HEATER | FA_EECH |  | 1450 | HBEH | N | N |  | MECH | 91
E-H-5203 | MEG CHEMICAL CLEANING HEATER | FA_EECH | VALID | 1450 | HBEH | N | N |  | MECH | 52
R-H-8022 | GAS TURBINE B LUBE OIL HEATER | FA_EECH |  | 1450 | HBEH | N | N |  | MECH | 80
R-H-8021 | GAS TURBINE A LUBE OIL HEATER | FA_EECH |  | 1450 | HBEH | N | N |  | MECH | 80
E-H-3005 | MEG CENTRIFUGE LUBE OIL HEATER | FA_EECH | VALID | 1450 | HBEH | N | N |  | MECH | 30
E-H-3004 | MEG CENTRIFUGE LUBE OIL HEATER | FA_EECH | VALID | 1450 | HBEH | N | N |  | MECH | 30
R-H-2022B | NEW CONDENSATE ELECTRIC HEATER | FA_EECH | VALID | 1450 | HBEH | N | N |  | MECH | 20
R-H-2022A | NEW CONDENSATE ELECTRIC HEATER | FA_EECH | VALID | 1450 | HBEH | N | N |  | MECH | 20
E-CEM-3003-EEH01 | SPACE HEATER FOR MAIN DRIVE MOTOR | FA_EECH |  | 63774 | EMAC | N | N |  | ELEC | 30
E-CEM-3002-EEH01 | SPACE HEATER FOR MAIN DRIVE MOTOR | FA_EECH |  | 63774 | EMAC | N | N |  | ELEC | 30
E-CDM-3003-EEH01 | SPACE HEATER FOR BACK DRIVE MOTOR | FA_EECH |  | 1450 | HBEH | N | N |  | ELEC | 30
E-CDM-3002-EEH01 | SPACE HEATER FOR BACK DRIVE MOTOR | FA_EECH |  | 1450 | HBEH | N | N |  | ELEC | 30
E-EEH-5203B | SODIUM CARBONATE STORAGE TANK HEATER | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 52
E-EEH-5203A | SODIUM CARBONATE STORAGE TANK HEATER | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 52
R-H-2001B | SLUG CATCHER BOTTOMS ELECTRIC HEATER | FA_EECH | VALID | 1450 | HBEH | N | N |  | MECH | 20
R-H-2001A | SLUG CATCHER BOTTOMS ELECTRIC HEATER | FA_EECH | VALID | 1450 | HBEH | N | N |  | MECH | 20
E-EH-5203B | SODIUM CARBONATE STORAGE TANK HEATER B | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 52
E-EH-5203A | SODIUM CARBONATE STORAGE TANK HEATER A | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 52
R-H-2721B | ONSHORE GAS COMPRESSOR LUBE OIL HEATER | FA_EECH |  | 1450 | HBEH | N | N |  | MECH | 27
R-H-2721A | ONSHORE GAS COMPRESSOR LUBE OIL HEATER | FA_EECH |  | 1450 | HBEH | N | N |  | MECH | 27
E-EEH-5205 | SODIUM CARBONATE OFF-LOADING TANK HEATER | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 52
E-EEH-5204 | SODIUM HYDROXIDE OFF-LOADING TANK HEATER | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 52
E-EEH-5202B | SODIUM CARBONATE OFF-LOADING TANK HEATER | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 52
E-EEH-5202A | SODIUM CARBONATE OFF-LOADING TANK HEATER | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 52
E-EEH-5201B | SODIUM HYDROXIDE OFF-LOADING TANK HEATER | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 52
E-EEH-5201A | SODIUM HYDROXIDE OFF-LOADING TANK HEATER | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 52
E-EEH-8701 | COOLING SYSTEM JW HEATER EM GEN E-GE-8711 | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 87
R-GSH-8022 | TURBINE B GENERATOR SPACE HEATER (G-8022) | FA_EECH |  | 1450 | HBEH | N | N |  | ELEC | 80
R-GSH-8021 | TURBINE A GENERATOR SPACE HEATER (G-8021) | FA_EECH |  | 1450 | HBEH | N | N |  | ELEC | 80
E-EEH-8131 | 3KW JACKET WATER HEATER FIRE PUMP E-P-8131 | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 81
E-EEH-8121 | 3KW JACKET WATER HEATER FIRE PUMP E-P-8121 | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 81
E-EEH-8111 | 3KW JACKET WATER HEATER FIRE PUMP E-P-8111 | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 81
E-H-6401 | NITROGEN GENERATION PACKAGE ELECTRICAL HEATER | FA_EECH | VALID | 1450 | HBEH | N | N |  | MECH | 64
E-EEH-9142E | IMMERSION HEATER: EXTINGUISHANT CABINET HEATER 5 | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 91
E-EEH-9142D | IMMERSION HEATER: EXTINGUISHANT CABINET HEATER 4 | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 91
E-EEH-9142C | IMMERSION HEATER: EXTINGUISHANT CABINET HEATER 3 | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 91
E-EEH-9142B | IMMERSION HEATER: EXTINGUISHANT CABINET HEATER 2 | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 91
E-EEH-9132E | IMMERSION HEATER: EXTINGUISHANT CABINET HEATER 5 | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 91
E-EEH-9132D | IMMERSION HEATER: EXTINGUISHANT CABINET HEATER 4 | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 91
E-EEH-9132C | IMMERSION HEATER: EXTINGUISHANT CABINET HEATER 3 | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 91
E-EEH-9132B | IMMERSION HEATER: EXTINGUISHANT CABINET HEATER 2 | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 91
E-EEH-9122E | IMMERSION HEATER: EXTINGUISHANT CABINET HEATER 5 | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 91
E-EEH-9122D | IMMERSION HEATER: EXTINGUISHANT CABINET HEATER 4 | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 91
E-EEH-9122C | IMMERSION HEATER: EXTINGUISHANT CABINET HEATER 3 | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 91
E-EEH-9122B | IMMERSION HEATER: EXTINGUISHANT CABINET HEATER 2 | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 91
E-EEH-9112E | IMMERSION HEATER: EXTINGUISHANT CABINET HEATER 5 | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 91
E-EEH-9112D | IMMERSION HEATER: EXTINGUISHANT CABINET HEATER 4 | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 91
E-EEH-9112C | IMMERSION HEATER: EXTINGUISHANT CABINET HEATER 3 | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 91
E-EEH-9112B | IMMERSION HEATER: EXTINGUISHANT CABINET HEATER 2 | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 91
E-GE-8711-EEH01 | GENERATOR SYSTEM ANTI CONDENSATION HEATER EM GEN E-GE-8711 | FA_EECH | VALID |  |  | N | N |  | ELEC | 87
E-EEH-9141B | IMMERSION HEATER IN LUBE OIL TANK IN SGT-200 SINGLE SHAFT E-X-9141 LUBE OIL SYSTEM | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 91
E-EEH-9141A | IMMERSION HEATER IN LUBE OIL TANK IN SGT-200 SINGLE SHAFT E-X-9141 LUBE OIL SYSTEM | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 91
E-EEH-9131B | IMMERSION HEATER IN LUBE OIL TANK IN SGT-200 SINGLE SHAFT E-X-9131 LUBE OIL SYSTEM | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 91
E-EEH-9131A | IMMERSION HEATER IN LUBE OIL TANK IN SGT-200 SINGLE SHAFT E-X-9131 LUBE OIL SYSTEM | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 91
E-EEH-9121B | IMMERSION HEATER IN LUBE OIL TANK IN SGT-200 SINGLE SHAFT E-X-9121 LUBE OIL SYSTEM | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 91
E-EEH-9121A | IMMERSION HEATER IN LUBE OIL TANK IN SGT-200 SINGLE SHAFT E-X-9121 LUBE OIL SYSTEM | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 91
E-EEH-9111B | IMMERSION HEATER IN LUBE OIL TANK IN SGT-200 SINGLE SHAFT E-X-9111 LUBE OIL SYSTEM | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 91
E-EEH-9111A | IMMERSION HEATER IN LUBE OIL TANK IN SGT-200 SINGLE SHAFT E-X-9111 LUBE OIL SYSTEM | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 91
E-H-2421 | FRAME OIL HEATER IN LP FLASH GAS COMPRESSOR PACKAGE TRAIN 2-LUBE OIL SYSTEM E-X-2421 | FA_EECH | VALID | 1450 | HBEH | N | N |  | MECH | 24
E-H-2411 | FRAME OIL HEATER IN LP FLASH GAS COMPRESSOR PACKAGE TRAIN 1-LUBE OIL SYSTEM E-X-2411 | FA_EECH | VALID | 1450 | HBEH | N | N |  | MECH | 24
E-EEH-9101 | IMMERSION HEATER ON WATER WASH TANK IN SGT-200 SINGLE SHAFT E-X-9111 WATER WASH MODULE | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 91
E-H-2423 | COOLING WATER TANK HEATER IN LP FLASH GAS COMPRESSOR PACKAGE TRAIN 2-COOLANT CONSOLE E-X-2421 | FA_EECH | VALID | 1450 | HBEH | N | N |  | MECH | 24
E-H-2413 | COOLING WATER TANK HEATER IN LP FLASH GAS COMPRESSOR PACKAGE TRAIN 1-COOLANT CONSOLE E-X-2411 | FA_EECH | VALID | 1450 | HBEH | N | N |  | MECH | 24
E-H-2422 | LUBRICATION OIL HEATER IN LP FLASH GAS COMPRESSOR PACKAGE TRAIN 2-CYLINDER LUBRICATOR E-X-2421 | FA_EECH | VALID | 1450 | HBEH | N | N |  | MECH | 24
E-H-2412 | LUBRICATION OIL HEATER IN LP FLASH GAS COMPRESSOR PACKAGE TRAIN 1-CYLINDER LUBRICATOR E-X-2411 | FA_EECH | VALID | 1450 | HBEH | N | N |  | MECH | 24
E-PM-2904C-EEH01 | ELECTRICAL SPACE HEATER IN LEAN MEG STORAGE TANKS AND EXPORT PUMPS ABOVE GROUND CABLE ROUTING LAYOUT | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 29
E-PM-2904B-EEH01 | ELECTRICAL SPACE HEATER IN LEAN MEG STORAGE TANKS AND EXPORT PUMPS ABOVE GROUND CABLE ROUTING LAYOUT | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 29
E-PM-2904A-EEH01 | ELECTRICAL SPACE HEATER IN LEAN MEG STORAGE TANKS AND EXPORT PUMPS ABOVE GROUND CABLE ROUTING LAYOUT | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 29
E-EEH-9145 | HEATER-ANTI CONDENSATION HEATER GENERATOR EXCITER IN SGT-200 SINGLE SHAFT E-X-9141 DRIVEN UNIT PACKAGE | FA_EECH | VALID |  |  | N | N |  | ELEC | 91
E-EEH-9135 | HEATER-ANTI CONDENSATION HEATER GENERATOR EXCITER IN SGT-200 SINGLE SHAFT E-X-9131 DRIVEN UNIT PACKAGE | FA_EECH | VALID |  |  | N | N |  | ELEC | 91
E-EEH-9125 | HEATER-ANTI CONDENSATION HEATER GENERATOR EXCITER IN SGT-200 SINGLE SHAFT E-X-9121 DRIVEN UNIT PACKAGE | FA_EECH | VALID |  |  | N | N |  | ELEC | 91
E-EEH-9115 | HEATER-ANTI CONDENSATION HEATER GENERATOR EXCITER IN SGT-200 SINGLE SHAFT E-X-9111 DRIVEN UNIT PACKAGE | FA_EECH | VALID |  |  | N | N |  | ELEC | 91
E-EEH-9144 | HEATER-ANTI CONDENSATION HEATER GENERATOR WINDINGS IN SGT-200 SINGLE SHAFT E-X-9141 DRIVEN UNIT PACKAGE | FA_EECH | VALID |  |  | N | N |  | ELEC | 91
E-EEH-9143 | HEATER-ANTI CONDENSATION HEATER GENERATOR WINDINGS IN SGT-200 SINGLE SHAFT E-X-9141 DRIVEN UNIT PACKAGE | FA_EECH | VALID |  |  | N | N |  | ELEC | 91
E-EEH-9134 | HEATER-ANTI CONDENSATION HEATER GENERATOR WINDINGS IN SGT-200 SINGLE SHAFT E-X-9131 DRIVEN UNIT PACKAGE | FA_EECH | VALID |  |  | N | N |  | ELEC | 91
E-EEH-9133 | HEATER-ANTI CONDENSATION HEATER GENERATOR WINDINGS IN SGT-200 SINGLE SHAFT E-X-9131 DRIVEN UNIT PACKAGE | FA_EECH | VALID |  |  | N | N |  | ELEC | 91
E-EEH-9124 | HEATER-ANTI CONDENSATION HEATER GENERATOR WINDINGS IN SGT-200 SINGLE SHAFT E-X-9121 DRIVEN UNIT PACKAGE | FA_EECH | VALID |  |  | N | N |  | ELEC | 91
E-EEH-9123 | HEATER-ANTI CONDENSATION HEATER GENERATOR WINDINGS IN SGT-200 SINGLE SHAFT E-X-9121 DRIVEN UNIT PACKAGE | FA_EECH | VALID |  |  | N | N |  | ELEC | 91
E-EEH-9114 | HEATER-ANTI CONDENSATION HEATER GENERATOR WINDINGS IN SGT-200 SINGLE SHAFT E-X-9111 DRIVEN UNIT PACKAGE | FA_EECH | VALID |  |  | N | N |  | ELEC | 91
E-EEH-9113 | HEATER-ANTI CONDENSATION HEATER GENERATOR WINDINGS IN SGT-200 SINGLE SHAFT E-X-9111 DRIVEN UNIT PACKAGE | FA_EECH | VALID |  |  | N | N |  | ELEC | 91
E-EEH-9146 | HEATER-ANTI CONDENSATION HEATER GENERATOR TERMINAL BOX IN SGT-200 SINGLE SHAFT E-X-9141 DRIVEN UNIT PACKAGE | FA_EECH | VALID |  |  | N | N |  | ELEC | 91
E-EEH-9136 | HEATER-ANTI CONDENSATION HEATER GENERATOR TERMINAL BOX IN SGT-200 SINGLE SHAFT E-X-9131 DRIVEN UNIT PACKAGE | FA_EECH | VALID |  |  | N | N |  | ELEC | 91
E-EEH-9126 | HEATER-ANTI CONDENSATION HEATER GENERATOR TERMINAL BOX IN SGT-200 SINGLE SHAFT E-X-9121 DRIVEN UNIT PACKAGE | FA_EECH | VALID |  |  | N | N |  | ELEC | 91
E-EEH-9116 | HEATER-ANTI CONDENSATION HEATER GENERATOR TERMINAL BOX IN SGT-200 SINGLE SHAFT E-X-9111 DRIVEN UNIT PACKAGE | FA_EECH | VALID |  |  | N | N |  | ELEC | 91
E-EEH-9142A | IMMERSION HEATER FOR EXTINGUISHANT CABINET HEATER 1 IN SGT-200 SINGLE SHAFT E-X-9141 EXTINGUISHANT BOTTLE RACK SYSTEM | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 91
E-EEH-9132A | IMMERSION HEATER FOR EXTINGUISHANT CABINET HEATER 1 IN SGT-200 SINGLE SHAFT E-X-9131 EXTINGUISHANT BOTTLE RACK SYSTEM | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 91
E-EEH-9122A | IMMERSION HEATER FOR EXTINGUISHANT CABINET HEATER 1 IN SGT-200 SINGLE SHAFT E-X-9121 EXTINGUISHANT BOTTLE RACK SYSTEM | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 91
E-EEH-9112A | IMMERSION HEATER FOR EXTINGUISHANT CABINET HEATER 1 IN SGT-200 SINGLE SHAFT E-X-9111 EXTINGUISHANT BOTTLE RACK SYSTEM | FA_EECH | VALID | 1450 | HBEH | N | N |  | ELEC | 91

## SystemDiscCountsbyFCode
STATUS | (Multiple Items)
Row Labels | Distinct Count of Discipline | Distinct Count of SYSTEMID
(blank) | 2 | 2
FA_CFBC | 1 | 1
FA_CFSGW | 1 | 2
FA_CFSSE | 1 | 1
FA_CFSSF | 1 | 2
FA_CFSST | 1 | 3
FA_EECF | 1 | 4
FA_EECH | 2 | 16
FA_EECMD | 3 | 2
FA_EECMI | 4 | 29
FA_EECMS | 1 | 1
FA_EECO | 1 | 3
FA_EECT | 1 | 1
FA_EEPBA | 1 | 6
FA_EEPBV | 1 | 3
FA_EEPCS | 2 | 6
FA_EEPNE | 2 | 2
FA_EEPNN | 1 | 3
FA_EEPS | 3 | 22
FA_EEPU | 1 | 2
FA_EETA | 1 | 2
FA_EETB | 2 | 6
FA_EETC | 1 | 7
FA_EETD | 1 | 3
FA_EETFW | 1 | 2
FA_EETGA | 1 | 3
FA_EETI | 1 | 6
FA_EETM | 1 | 2
FA_EETO | 2 | 2
FA_EETP | 1 | 1
FA_EETQ | 1 | 7
FA_EETR | 1 | 1
FA_EETW | 2 | 14
FA_EETY | 1 | 3
FA_INAM | 1 | 3
FA_INAP | 1 | 5
FA_INDC | 1 | 4
FA_INDFD | 1 | 2
FA_INDFS | 1 | 14
FA_INDI | 3 | 37
FA_INDMS | 2 | 31
FA_INDMT | 2 | 37
FA_INDS | 3 | 42
FA_INDT | 1 | 1
FA_INSC | 2 | 4
FA_INSD | 1 | 2
FA_INSJ | 5 | 32
FA_INSL | 6 | 28
FA_INSS | 2 | 4
FA_INST | 1 | 1
FA_INSY | 1 | 3
FA_PEA | 3 | 19
FA_PEG | 3 | 41
FA_PEL | 1 | 1
FA_PEM | 1 | 2
FA_PEO | 1 | 28
FA_PESC | 2 | 29
FA_PESR | 1 | 5
FA_PESV | 1 | 6
FA_PET | 2 | 23
FA_PEVB | 3 | 40
FA_PEVC | 3 | 39
FA_PEVD | 1 | 1
FA_PEVG | 3 | 33
FA_PEVL | 3 | 28
FA_PEVM | 1 | 2
FA_PEVN | 3 | 11
FA_PEVX | 1 | 2
FA_PEVY | 2 | 7
FA_REBC | 1 | 2
FA_REC | 1 | 1
FA_REDH | 1 | 1
FA_REDP | 1 | 6
FA_REEL | 1 | 2
FA_REFA | 1 | 4
FA_REFC | 1 | 11
FA_REMC | 1 | 2
FA_REMR | 1 | 1
FA_REMT | 1 | 2
FA_RENG | 1 | 3
FA_REPC | 2 | 24
FA_REPD | 3 | 10
FA_RER | 1 | 2
FA_RETG | 1 | 1
FA_RETP | 1 | 1
FA_REUC | 1 | 1
FA_SEC | 1 | 1
FA_SEE | 1 | 1
FA_SEFB | 3 | 26
FA_SEFE | 3 | 21
FA_SEFS | 2 | 3
FA_SEHF | 1 | 12
FA_SEHS | 1 | 5
FA_SEHT | 1 | 9
FA_SEL | 2 | 15
FA_SEM | 1 | 4
FA_SENF | 1 | 2
FA_SEPA | 1 | 13
FA_SEPC | 1 | 13
FA_SEPHC | 1 | 1
FA_SEPHS | 2 | 27
FA_SES | 2 | 4
FA_SETAC | 1 | 15
FA_SETAP | 3 | 9
FA_SETPC | 2 | 3
FA_SEZ | 2 | 7
FA_SQFC | 1 | 1
FA_SQFDF | 2 | 4
FA_SQFDG | 2 | 4
FA_SQFDS | 1 | 1
FA_SQFFD | 3 | 6
FA_SQFFH | 1 | 1
FA_SQFFM | 1 | 1
FA_SQFFY | 1 | 1
FA_SQFRA | 3 | 5
FA_SQFRE | 1 | 1
FA_SQMT | 1 | 1
FA_SQTA | 3 | 5
FA_SQTB | 4 | 5
FA_SQTE | 2 | 3
FA_SQTH | 1 | 2
FA_SQTL | 2 | 2
FA_SQTN | 1 | 1
FA_SQTOF | 2 | 2
FA_SQTP | 1 | 2
FA_SQTS | 2 | 5
FA_SQTV | 2 | 3
FA_SQTW | 1 | 1
FA_SQTY | 1 | 1
FA_SYLH | 4 | 42
FA_WECO | 1 | 3
FA_WEHY | 1 | 1
SOFT | 1 | 5
Grand Total | 12 | 66

## FCodesBySystemDiscipline
STATUS | (Multiple Items)
Count of Functional location | Column Labels
Row Labels | (blank) | ELEC | F&G | HVAC | INST | MECH | N/A | PIPING | SAFETY | STRUCTURE | TBC | TELE | Grand Total
(blank) |  |  |  |  | 1 | [5 empty] | 4 |  | 5
27 |  |  |  |  | 1 | [7 empty] | 1
98 | [10 empty] | 4 |  | 4
FA_CFBC | [9 empty] | 4 |  |  | 4
N/A | [9 empty] | 4 |  |  | 4
FA_CFSGW | [9 empty] | 5 |  |  | 5
81 | [9 empty] | 3 |  |  | 3
N/A | [9 empty] | 2 |  |  | 2
FA_CFSSE | [9 empty] | 104 |  |  | 104
N/A | [9 empty] | 104 |  |  | 104
FA_CFSSF | [9 empty] | 19 |  |  | 19
67 | [9 empty] | 1 |  |  | 1
N/A | [9 empty] | 18 |  |  | 18
FA_CFSST | [9 empty] | 907 |  |  | 907
04 | [9 empty] | 1 |  |  | 1
57 | [9 empty] | 14 |  |  | 14
N/A | [9 empty] | 892 |  |  | 892
FA_EECF |  | 398 | [10 empty] | 398
(blank) |  | 1 | [10 empty] | 1
42 |  | 11 | [10 empty] | 11
85 |  | 188 | [10 empty] | 188
89 |  | 198 | [10 empty] | 198
FA_EECH |  | 74 |  |  |  | 35 | [6 empty] | 109
20 | [5 empty] | 4 | [6 empty] | 4
24 | [5 empty] | 6 | [6 empty] | 6
25 | [5 empty] | 1 | [6 empty] | 1
27 | [5 empty] | 2 | [6 empty] | 2
29 |  | 3 | [10 empty] | 3
30 |  | 6 |  |  |  | 2 | [6 empty] | 8
42 | [5 empty] | 1 | [6 empty] | 1
44 | [5 empty] | 1 | [6 empty] | 1
45 | [5 empty] | 2 | [6 empty] | 2
46 | [5 empty] | 3 | [6 empty] | 3
52 |  | 10 |  |  |  | 2 | [6 empty] | 12
64 | [5 empty] | 1 | [6 empty] | 1
80 |  | 2 |  |  |  | 2 | [6 empty] | 4
81 |  | 3 | [10 empty] | 3
87 |  | 5 | [10 empty] | 5
91 |  | 45 |  |  |  | 8 | [6 empty] | 53
FA_EECMD |  | 5 |  |  |  | 1 |  |  |  |  | 1 |  | 7
81 |  | 3 | [10 empty] | 3
87 |  | 2 |  |  |  | 1 |  |  |  |  | 1 |  | 4
FA_EECMI |  | 432 |  |  | 12 | 20 |  |  |  |  | 2 |  | 466
05 |  | 5 | [10 empty] | 5
21 |  | 25 | [10 empty] | 25
22 |  | 2 | [10 empty] | 2
24 |  | 39 | [10 empty] | 39
25 |  | 18 |  |  |  | 1 | [6 empty] | 19
27 |  | 9 |  |  |  | 8 | [6 empty] | 17
28 |  | 21 | [10 empty] | 21
29 |  | 13 | [10 empty] | 13
30 |  | 62 | [10 empty] | 62
43 | [5 empty] | 2 | [6 empty] | 2
45 |  | 3 | [10 empty] | 3
47 |  | 10 | [10 empty] | 10
51 |  | 8 | [10 empty] | 8
52 |  | 34 | [10 empty] | 34
53 |  | 4 | [10 empty] | 4
56 |  | 17 | [10 empty] | 17
57 |  | 9 | [10 empty] | 9
58 |  | 2 | [10 empty] | 2
60 |  | 25 | [10 empty] | 25
62 |  | 2 | [10 empty] | 2
65 |  | 20 | [10 empty] | 20
66 |  | 4 | [10 empty] | 4
67 |  | 17 | [10 empty] | 17
80 |  | 10 |  |  |  | 4 | [6 empty] | 14
81 |  | 8 | [10 empty] | 8
82 |  | 4 | [10 empty] | 4
87 |  | 17 |  |  | 12 | 1 | [6 empty] | 30
91 |  | 41 |  |  |  | 4 | [6 empty] | 45
N/A |  | 3 | [8 empty] | 2 |  | 5
FA_EECMS | [5 empty] | 1 | [6 empty] | 1
44 | [5 empty] | 1 | [6 empty] | 1
FA_EECO |  | 21 | [10 empty] | 21
66 |  | 2 | [10 empty] | 2
80 |  | 15 | [10 empty] | 15
N/A |  | 4 | [10 empty] | 4
FA_EECT |  | 2 | [10 empty] | 2
98 |  | 2 | [10 empty] | 2
FA_EEPBA |  | 868 | [10 empty] | 868
80 |  | 121 | [10 empty] | 121
85 |  | 36 | [10 empty] | 36
87 |  | 47 | [10 empty] | 47
88 |  | 526 | [10 empty] | 526
89 |  | 60 | [10 empty] | 60
91 |  | 78 | [10 empty] | 78
FA_EEPBV |  | 48 | [10 empty] | 48
80 |  | 44 | [10 empty] | 44
87 |  | 3 | [10 empty] | 3
N/A |  | 1 | [10 empty] | 1
FA_EEPCS |  | 103 |  |  | 6 | [7 empty] | 109
20 |  |  |  |  | 1 | [7 empty] | 1
21 |  |  |  |  | 1 | [7 empty] | 1
27 |  |  |  |  | 1 | [7 empty] | 1
29 |  |  |  |  | 2 | [7 empty] | 2
56 |  |  |  |  | 1 | [7 empty] | 1
92 |  | 103 | [10 empty] | 103
FA_EEPNE |  | 100 | [8 empty] | 18 |  | 118
90 |  | 94 | [10 empty] | 94
N/A |  | 6 | [8 empty] | 18 |  | 24
FA_EEPNN |  | 8 | [10 empty] | 8
80 |  | 2 | [10 empty] | 2
82 |  | 2 | [10 empty] | 2
91 |  | 4 | [10 empty] | 4
FA_EEPS |  | 152 |  |  | 66 | [5 empty] | 3 |  | 221
(blank) |  |  |  |  | 17 | [7 empty] | 17
20 |  | 4 | [10 empty] | 4
21 |  | 6 |  |  | 6 | [7 empty] | 12
27 |  |  |  |  | 2 | [7 empty] | 2
28 |  | 3 |  |  | 6 | [7 empty] | 9
29 |  | 6 | [10 empty] | 6
30 |  | 11 |  |  | 27 | [7 empty] | 38
42 |  | 1 | [10 empty] | 1
44 |  | 1 | [10 empty] | 1
45 |  | 2 | [10 empty] | 2
46 |  | 1 | [10 empty] | 1
47 |  | 9 |  |  | 4 | [7 empty] | 13
51 |  | 8 | [10 empty] | 8
52 |  | 15 |  |  | 2 | [5 empty] | 3 |  | 20
56 |  | 10 | [10 empty] | 10
57 |  | 4 | [10 empty] | 4
60 |  | 13 | [10 empty] | 13
65 |  | 25 | [10 empty] | 25
66 |  | 7 | [10 empty] | 7
67 |  | 9 |  |  | 2 | [7 empty] | 11
87 |  | 1 | [10 empty] | 1
N/A |  | 16 | [10 empty] | 16
FA_EEPU |  | 29 | [10 empty] | 29
88 |  | 22 | [10 empty] | 22
91 |  | 7 | [10 empty] | 7
FA_EETA |  | 6 | [10 empty] | 6
80 |  | 4 | [10 empty] | 4
87 |  | 2 | [10 empty] | 2
FA_EETB |  | 38 | [8 empty] | 1 |  | 39
80 |  | 4 | [10 empty] | 4
81 |  | 6 | [10 empty] | 6
84 |  | 2 | [10 empty] | 2
87 | [10 empty] | 1 |  | 1
88 |  | 20 | [10 empty] | 20
91 |  | 6 | [10 empty] | 6
FA_EETC |  | 57 | [10 empty] | 57
27 |  | 9 | [10 empty] | 9
80 |  | 8 | [10 empty] | 8
81 |  | 2 | [10 empty] | 2
84 |  | 3 | [10 empty] | 3
87 |  | 4 | [10 empty] | 4
88 |  | 22 | [10 empty] | 22
91 |  | 9 | [10 empty] | 9
FA_EETD |  | 70 | [10 empty] | 70
80 |  | 8 | [10 empty] | 8
87 |  | 2 | [10 empty] | 2
90 |  | 60 | [10 empty] | 60
FA_EETFW |  | 20 | [10 empty] | 20
80 |  | 16 | [10 empty] | 16
87 |  | 4 | [10 empty] | 4
FA_EETGA | [5 empty] | 10 | [6 empty] | 10
84 | [5 empty] | 2 | [6 empty] | 2
87 | [5 empty] | 4 | [6 empty] | 4
91 | [5 empty] | 4 | [6 empty] | 4
FA_EETI |  | 25 | [10 empty] | 25
80 |  | 2 | [10 empty] | 2
81 |  | 3 | [10 empty] | 3
84 |  | 2 | [10 empty] | 2
87 |  | 4 | [10 empty] | 4
88 |  | 12 | [10 empty] | 12
91 |  | 2 | [10 empty] | 2
FA_EETM |  | 910 | [10 empty] | 910
80 |  | 739 | [10 empty] | 739
87 |  | 171 | [10 empty] | 171
FA_EETO |  | 4 | 1 | [9 empty] | 5
50 |  | 4 | [10 empty] | 4
81 |  |  | 1 | [9 empty] | 1
FA_EETP |  |  |  |  | 3 | [7 empty] | 3
(blank) |  |  |  |  | 3 | [7 empty] | 3
FA_EETQ |  | 64 | [10 empty] | 64
24 |  | 21 | [10 empty] | 21
25 |  | 12 | [10 empty] | 12
27 |  | 2 | [10 empty] | 2
30 |  | 23 | [10 empty] | 23
45 |  | 1 | [10 empty] | 1
60 |  | 3 | [10 empty] | 3
80 |  | 2 | [10 empty] | 2
FA_EETR |  | 15 | [10 empty] | 15
92 |  | 15 | [10 empty] | 15
FA_EETW |  | 165 | 5 | [9 empty] | 170
66 |  | 1 | [10 empty] | 1
78 |  |  | 5 | [9 empty] | 5
80 |  | 11 | [10 empty] | 11
85 |  | 19 | [10 empty] | 19
86 |  | 2 | [10 empty] | 2
87 |  | 9 | [10 empty] | 9
88 |  | 22 | [10 empty] | 22
89 |  | 44 | [10 empty] | 44
90 |  | 1 | [10 empty] | 1
91 |  | 14 | [10 empty] | 14
92 |  | 15 | [10 empty] | 15
94 |  | 2 | [10 empty] | 2
95 |  | 21 | [10 empty] | 21
N/A |  | 4 | [10 empty] | 4
FA_EETY |  | 28 | [10 empty] | 28
76 |  | 16 | [10 empty] | 16
77 |  | 6 | [10 empty] | 6
78 |  | 6 | [10 empty] | 6
FA_INAM |  |  |  |  | 17 | [7 empty] | 17
21 |  |  |  |  | 12 | [7 empty] | 12
27 |  |  |  |  | 4 | [7 empty] | 4
46 |  |  |  |  | 1 | [7 empty] | 1
FA_INAP | [10 empty] | 10 |  | 10
21 | [10 empty] | 2 |  | 2
27 | [10 empty] | 2 |  | 2
46 | [10 empty] | 1 |  | 1
52 | [10 empty] | 4 |  | 4
60 | [10 empty] | 1 |  | 1
FA_INDC |  |  |  |  | 9 | [7 empty] | 9
20 |  |  |  |  | 3 | [7 empty] | 3
22 |  |  |  |  | 2 | [7 empty] | 2
56 |  |  |  |  | 1 | [7 empty] | 1
66 |  |  |  |  | 3 | [7 empty] | 3
FA_INDFD |  |  |  | 20 | [8 empty] | 20
87 |  |  |  | 12 | [8 empty] | 12
91 |  |  |  | 8 | [8 empty] | 8
FA_INDFS |  |  |  |  | 230 | [7 empty] | 230
20 |  |  |  |  | 2 | [7 empty] | 2
21 |  |  |  |  | 9 | [7 empty] | 9
24 |  |  |  |  | 24 | [7 empty] | 24
25 |  |  |  |  | 48 | [7 empty] | 48
27 |  |  |  |  | 31 | [7 empty] | 31
45 |  |  |  |  | 4 | [7 empty] | 4
46 |  |  |  |  | 3 | [7 empty] | 3
62 |  |  |  |  | 2 | [7 empty] | 2
63 |  |  |  |  | 4 | [7 empty] | 4
65 |  |  |  |  | 50 | [7 empty] | 50
66 |  |  |  |  | 4 | [7 empty] | 4
78 |  |  |  |  | 10 | [7 empty] | 10
87 |  |  |  |  | 7 | [7 empty] | 7
91 |  |  |  |  | 32 | [7 empty] | 32
FA_INDI |  |  |  |  | 1291 |  |  | 61 |  |  | 127 |  | 1479
(blank) |  |  |  |  | 27 | [7 empty] | 27
20 |  |  |  |  | 63 | [5 empty] | 24 |  | 87
21 |  |  |  |  | 88 | [7 empty] | 88
22 |  |  |  |  | 10 | [7 empty] | 10
24 |  |  |  |  | 92 |  |  | 35 |  |  |  |  | 127
25 |  |  |  |  | 146 | [5 empty] | 6 |  | 152
27 |  |  |  |  | 91 | [5 empty] | 2 |  | 93
28 |  |  |  |  | 65 |  |  | 18 |  |  | 27 |  | 110
29 |  |  |  |  | 35 | [7 empty] | 35
30 |  |  |  |  | 123 | [7 empty] | 123
40 |  |  |  |  | 1 | [7 empty] | 1
41 |  |  |  |  | 2 | [7 empty] | 2
42 |  |  |  |  | 13 | [7 empty] | 13
43 |  |  |  |  | 15 | [5 empty] | 2 |  | 17
44 |  |  |  |  | 7 | [5 empty] | 1 |  | 8
45 |  |  |  |  | 13 | [5 empty] | 2 |  | 15
46 |  |  |  |  | 39 | [7 empty] | 39
47 |  |  |  |  | 21 | [5 empty] | 2 |  | 23
51 |  |  |  |  | 4 | [7 empty] | 4
52 |  |  |  |  | 20 |  |  | 1 |  |  | 1 |  | 22
53 |  |  |  |  | 10 | [7 empty] | 10
54 |  |  |  |  | 1 | [7 empty] | 1
56 |  |  |  |  | 21 | [7 empty] | 21
57 |  |  |  |  | 25 | [5 empty] | 8 |  | 33
58 |  |  |  |  | 3 | [7 empty] | 3
60 |  |  |  |  | 100 | [5 empty] | 3 |  | 103
62 |  |  |  |  | 6 | [5 empty] | 34 |  | 40
63 |  |  |  |  | 14 | [7 empty] | 14
64 |  |  |  |  | 18 | [5 empty] | 8 |  | 26
65 |  |  |  |  | 12 |  |  | 5 |  |  |  |  | 17
66 |  |  |  |  | 13 | [7 empty] | 13
67 |  |  |  |  | 23 |  |  | 2 |  |  |  |  | 25
78 | [10 empty] | 2 |  | 2
81 |  |  |  |  | 92 | [5 empty] | 5 |  | 97
82 |  |  |  |  | 4 | [7 empty] | 4
87 |  |  |  |  | 15 | [7 empty] | 15
91 |  |  |  |  | 59 | [7 empty] | 59
FA_INDMS |  |  |  |  | 1687 | 4 | [6 empty] | 1691
00 | [5 empty] | 1 | [6 empty] | 1
20 |  |  |  |  | 61 | [7 empty] | 61
21 |  |  |  |  | 58 | [7 empty] | 58
22 |  |  |  |  | 11 | [7 empty] | 11
24 |  |  |  |  | 206 | [7 empty] | 206
25 |  |  |  |  | 180 | [7 empty] | 180
27 |  |  |  |  | 54 | [7 empty] | 54
28 |  |  |  |  | 24 | [7 empty] | 24
29 |  |  |  |  | 9 | [7 empty] | 9
30 |  |  |  |  | 123 | [7 empty] | 123
42 |  |  |  |  | 27 | [7 empty] | 27
43 |  |  |  |  | 11 | [7 empty] | 11
44 |  |  |  |  | 26 | [7 empty] | 26
45 |  |  |  |  | 19 | [7 empty] | 19
46 |  |  |  |  | 38 | [7 empty] | 38
51 |  |  |  |  | 4 | [7 empty] | 4
52 |  |  |  |  | 18 | [7 empty] | 18
53 |  |  |  |  | 1 | [7 empty] | 1
56 |  |  |  |  | 1 | [7 empty] | 1
57 |  |  |  |  | 7 | [7 empty] | 7
58 |  |  |  |  | 1 | [7 empty] | 1
60 |  |  |  |  | 177 | [7 empty] | 177
63 |  |  |  |  | 3 | [7 empty] | 3
64 |  |  |  |  | 2 | [7 empty] | 2
65 |  |  |  |  | 116 | [7 empty] | 116
66 |  |  |  |  | 32 | [7 empty] | 32
67 |  |  |  |  | 15 | [7 empty] | 15
81 |  |  |  |  | 1 | 1 | [6 empty] | 2
84 | [5 empty] | 2 | [6 empty] | 2
87 |  |  |  |  | 72 | [7 empty] | 72
91 |  |  |  |  | 390 | [7 empty] | 390
FA_INDMT |  | 2 |  |  | 2713 | [7 empty] | 2715
(blank) |  |  |  |  | 19 | [7 empty] | 19
20 |  |  |  |  | 154 | [7 empty] | 154
21 |  |  |  |  | 123 | [7 empty] | 123
22 |  |  |  |  | 42 | [7 empty] | 42
24 |  |  |  |  | 269 | [7 empty] | 269
25 |  |  |  |  | 310 | [7 empty] | 310
27 |  |  |  |  | 138 | [7 empty] | 138
28 |  |  |  |  | 113 | [7 empty] | 113
29 |  |  |  |  | 63 | [7 empty] | 63
30 |  |  |  |  | 354 | [7 empty] | 354
40 |  |  |  |  | 9 | [7 empty] | 9
41 |  |  |  |  | 1 | [7 empty] | 1
42 |  |  |  |  | 38 | [7 empty] | 38
43 |  |  |  |  | 15 | [7 empty] | 15
44 |  |  |  |  | 29 | [7 empty] | 29
45 |  |  |  |  | 42 | [7 empty] | 42
46 |  |  |  |  | 87 | [7 empty] | 87
47 |  |  |  |  | 50 | [7 empty] | 50
51 |  |  |  |  | 29 | [7 empty] | 29
52 |  |  |  |  | 85 | [7 empty] | 85
53 |  |  |  |  | 6 | [7 empty] | 6
54 |  |  |  |  | 2 | [7 empty] | 2
56 |  |  |  |  | 18 | [7 empty] | 18
57 |  |  |  |  | 29 | [7 empty] | 29
58 |  |  |  |  | 4 | [7 empty] | 4
60 |  |  |  |  | 164 | [7 empty] | 164
62 |  |  |  |  | 2 | [7 empty] | 2
63 |  |  |  |  | 17 | [7 empty] | 17
64 |  |  |  |  | 19 | [7 empty] | 19
65 |  |  |  |  | 85 | [7 empty] | 85
66 |  |  |  |  | 44 | [7 empty] | 44
67 |  |  |  |  | 48 | [7 empty] | 48
80 |  | 2 | [10 empty] | 2
81 |  |  |  |  | 41 | [7 empty] | 41
82 |  |  |  |  | 1 | [7 empty] | 1
87 |  |  |  |  | 34 | [7 empty] | 34
91 |  |  |  |  | 229 | [7 empty] | 229
FA_INDS |  | 29 |  |  | 1485 | [5 empty] | 39 |  | 1553
(blank) |  |  |  |  | 6 | [7 empty] | 6
20 |  |  |  |  | 19 | [7 empty] | 19
21 |  | 1 |  |  | 64 | [7 empty] | 65
22 |  |  |  |  | 5 | [7 empty] | 5
24 |  |  |  |  | 82 | [7 empty] | 82
25 |  |  |  |  | 228 | [7 empty] | 228
27 |  |  |  |  | 76 | [7 empty] | 76
28 |  |  |  |  | 19 | [7 empty] | 19
29 |  |  |  |  | 8 | [7 empty] | 8
30 |  |  |  |  | 80 | [7 empty] | 80
40 |  |  |  |  | 2 | [7 empty] | 2
42 |  |  |  |  | 16 | [7 empty] | 16
43 | [10 empty] | 19 |  | 19
44 |  |  |  |  | 15 | [7 empty] | 15
45 |  |  |  |  | 31 | [7 empty] | 31
46 |  |  |  |  | 23 | [7 empty] | 23
47 |  |  |  |  | 3 | [7 empty] | 3
51 |  |  |  |  | 3 | [7 empty] | 3
52 |  |  |  |  | 9 | [7 empty] | 9
53 |  |  |  |  | 2 | [7 empty] | 2
56 |  |  |  |  | 5 | [7 empty] | 5
57 |  |  |  |  | 21 | [7 empty] | 21
58 |  |  |  |  | 2 | [7 empty] | 2
59 |  |  |  |  | 1 | [7 empty] | 1
60 |  |  |  |  | 152 | [7 empty] | 152
62 |  |  |  |  | 6 | [5 empty] | 20 |  | 26
63 |  |  |  |  | 43 | [7 empty] | 43
64 |  |  |  |  | 6 | [7 empty] | 6
65 |  |  |  |  | 17 | [7 empty] | 17
66 |  |  |  |  | 29 | [7 empty] | 29
67 |  |  |  |  | 26 | [7 empty] | 26
77 |  |  |  |  | 21 | [7 empty] | 21
78 |  |  |  |  | 30 | [7 empty] | 30
80 |  | 8 | [10 empty] | 8
81 |  |  |  |  | 118 | [7 empty] | 118
82 |  |  |  |  | 1 | [7 empty] | 1
86 |  |  |  |  | 1 | [7 empty] | 1
87 |  | 7 |  |  | 49 | [7 empty] | 56
90 |  | 5 | [10 empty] | 5
91 |  | 4 |  |  | 264 | [7 empty] | 268
94 |  |  |  |  | 2 | [7 empty] | 2
N/A |  | 4 | [10 empty] | 4
FA_INDT |  |  |  |  | 33 | [7 empty] | 33
65 |  |  |  |  | 33 | [7 empty] | 33
FA_INSC |  | 12 |  |  | 1 | [7 empty] | 13
(blank) |  |  |  |  | 1 | [7 empty] | 1
87 |  | 3 | [10 empty] | 3
91 |  | 4 | [10 empty] | 4
93 |  | 5 | [10 empty] | 5
FA_INSD |  | 9 | [10 empty] | 9
80 |  | 6 | [10 empty] | 6
N/A |  | 3 | [10 empty] | 3
FA_INSJ |  | 63 | 549 |  | 167 | [5 empty] | 28 | 59 | 866
20 |  |  | 18 |  | 8 | [7 empty] | 26
21 |  |  | 32 |  | 10 | [7 empty] | 42
22 |  |  | 22 |  | 12 | [7 empty] | 34
23 |  |  | 7 | [9 empty] | 7
24 |  |  | 9 | [9 empty] | 9
25 |  |  | 31 |  | 12 | [7 empty] | 43
28 |  |  | 28 |  | 6 | [7 empty] | 34
29 |  |  | 27 |  | 11 | [7 empty] | 38
30 |  |  | 50 |  | 31 | [7 empty] | 81
42 |  | 3 | 9 |  | 2 | [7 empty] | 14
44 |  |  | 2 | [9 empty] | 2
46 |  |  | 3 |  | 3 | [7 empty] | 6
47 |  |  | 10 |  | 5 | [7 empty] | 15
50 |  |  | 4 | [9 empty] | 4
55 |  |  | 1 | [9 empty] | 1
56 |  |  | 2 | [9 empty] | 2
57 |  |  | 2 |  | 1 | [7 empty] | 3
58 |  |  | 1 | [9 empty] | 1
60 |  |  | 23 |  | 10 | [7 empty] | 33
63 |  |  |  |  | 1 | [7 empty] | 1
64 |  |  | 1 | [9 empty] | 1
65 |  |  | 5 |  | 13 | [7 empty] | 18
66 |  |  | 11 |  | 1 | [7 empty] | 12
67 |  |  | 18 |  | 11 | [7 empty] | 29
78 |  |  | 171 | [9 empty] | 171
80 |  |  |  |  | 2 | [7 empty] | 2
81 |  |  | 5 |  | 1 | [7 empty] | 6
82 |  |  | 1 | [9 empty] | 1
91 |  |  | 3 | [9 empty] | 3
92 |  | 43 | [10 empty] | 43
96 | [11 empty] | 56 | 56
N/A |  | 17 | 53 |  | 27 | [5 empty] | 28 | 3 | 128
FA_INSL |  | 44 |  |  | 162 | 1 |  |  | 1 |  | 6 | 4 | 218
(blank) |  | 2 |  |  | 1 | [7 empty] | 3
05 |  |  |  |  | 4 | [7 empty] | 4
20 |  | 4 | [10 empty] | 4
25 |  | 6 |  |  | 1 | [7 empty] | 7
27 |  | 2 | [10 empty] | 2
42 |  | 3 |  |  | 2 | [7 empty] | 5
43 |  | 1 | [10 empty] | 1
44 |  | 1 | [10 empty] | 1
46 |  | 3 |  |  |  | 1 |  |  |  |  | 1 |  | 5
52 |  | 2 | [10 empty] | 2
60 |  | 1 |  |  | 22 | [7 empty] | 23
63 |  |  |  |  | 2 | [7 empty] | 2
64 |  | 1 |  |  | 1 | [7 empty] | 2
65 |  | 5 |  |  | 10 | [7 empty] | 15
66 |  |  |  |  | 2 | [7 empty] | 2
75 |  |  |  |  | 1 | [7 empty] | 1
76 |  |  |  |  | 48 | [7 empty] | 48
77 |  |  |  |  | 2 | [7 empty] | 2
78 |  |  |  |  | 44 | [7 empty] | 44
80 |  | 3 | [10 empty] | 3
81 |  |  |  |  | 5 |  |  |  | 1 |  |  |  | 6
84 |  | 3 | [10 empty] | 3
87 |  |  |  |  | 4 | [7 empty] | 4
88 |  |  |  |  | 8 | [7 empty] | 8
90 |  |  |  |  | 1 | [7 empty] | 1
91 |  | 5 |  |  | 4 | [7 empty] | 9
96 | [11 empty] | 4 | 4
N/A |  | 2 | [8 empty] | 5 |  | 7
FA_INSS | [10 empty] | 3 | 5 | 8
93 | [11 empty] | 3 | 3
96 | [11 empty] | 2 | 2
98 | [10 empty] | 1 |  | 1
N/A | [10 empty] | 2 |  | 2
FA_INST | [11 empty] | 3 | 3
83 | [11 empty] | 3 | 3
FA_INSY |  |  |  |  | 19 | [7 empty] | 19
22 |  |  |  |  | 1 | [7 empty] | 1
76 |  |  |  |  | 5 | [7 empty] | 5
77 |  |  |  |  | 13 | [7 empty] | 13
FA_PEA |  |  |  |  | 119 | 3 |  |  |  |  | 11 |  | 133
(blank) |  |  |  |  | 2 | [7 empty] | 2
20 |  |  |  |  | 5 | [7 empty] | 5
21 |  |  |  |  | 5 | [7 empty] | 5
24 |  |  |  |  | 10 | [7 empty] | 10
25 |  |  |  |  | 1 | [7 empty] | 1
27 |  |  |  |  | 29 | [7 empty] | 29
28 |  |  |  |  | 2 | [7 empty] | 2
29 |  |  |  |  | 2 | [7 empty] | 2
44 |  |  |  |  | 1 | [7 empty] | 1
45 |  |  |  |  | 5 | [7 empty] | 5
46 |  |  |  |  | 12 | [7 empty] | 12
47 |  |  |  |  | 7 | [7 empty] | 7
60 |  |  |  |  | 2 | [7 empty] | 2
63 |  |  |  |  | 2 | [7 empty] | 2
64 |  |  |  |  | 2 | [7 empty] | 2
65 |  |  |  |  | 12 | [7 empty] | 12
81 |  |  |  |  | 4 | 3 |  |  |  |  | 10 |  | 17
87 |  |  |  |  | 2 | [5 empty] | 1 |  | 3
91 |  |  |  |  | 14 | [7 empty] | 14
FA_PEG | [5 empty] | 115 |  | 12361 |  |  | 124 |  | 12600
(blank) | [7 empty] | 17 |  |  |  |  | 17
05 | [5 empty] | 1 |  | 23 |  |  |  |  | 24
20 | [5 empty] | 5 |  | 704 |  |  | 23 |  | 732
21 | [7 empty] | 466 |  |  | 7 |  | 473
22 | [5 empty] | 7 |  | 124 |  |  |  |  | 131
24 | [7 empty] | 495 |  |  |  |  | 495
25 | [5 empty] | 4 |  | 623 |  |  | 15 |  | 642
27 | [7 empty] | 181 |  |  | 2 |  | 183
28 | [5 empty] | 5 |  | 905 |  |  | 28 |  | 938
29 | [5 empty] | 8 |  | 301 |  |  |  |  | 309
30 | [5 empty] | 9 |  | 1231 |  |  |  |  | 1240
40 | [7 empty] | 101 |  |  |  |  | 101
41 | [7 empty] | 92 |  |  |  |  | 92
42 | [5 empty] | 1 |  | 409 |  |  | 5 |  | 415
43 | [7 empty] | 27 |  |  |  |  | 27
44 | [5 empty] | 4 |  | 239 |  |  |  |  | 243
45 | [7 empty] | 100 |  |  | 2 |  | 102
46 | [7 empty] | 218 |  |  |  |  | 218
47 | [5 empty] | 3 |  | 182 |  |  | 4 |  | 189
48 | [7 empty] | 1 |  |  |  |  | 1
51 | [7 empty] | 135 |  |  |  |  | 135
52 | [7 empty] | 662 |  |  |  |  | 662
53 | [7 empty] | 176 |  |  |  |  | 176
54 | [5 empty] | 7 |  | 385 |  |  |  |  | 392
56 | [7 empty] | 403 |  |  |  |  | 403
57 | [5 empty] | 1 |  | 458 |  |  | 14 |  | 473
58 | [7 empty] | 470 |  |  |  |  | 470
60 | [7 empty] | 458 |  |  | 2 |  | 460
61 | [7 empty] | 24 |  |  |  |  | 24
62 | [7 empty] | 19 |  |  |  |  | 19
63 | [7 empty] | 446 |  |  |  |  | 446
64 | [5 empty] | 6 |  | 462 |  |  |  |  | 468
65 | [5 empty] | 7 |  | 396 |  |  |  |  | 403
66 | [7 empty] | 139 |  |  |  |  | 139
67 | [7 empty] | 604 |  |  | 3 |  | 607
81 | [5 empty] | 3 |  | 487 |  |  |  |  | 490
82 | [7 empty] | 32 |  |  |  |  | 32
86 | [7 empty] | 6 |  |  |  |  | 6
87 | [5 empty] | 2 |  | 29 |  |  | 19 |  | 50
91 | [5 empty] | 4 |  | 114 |  |  |  |  | 118
N/A | [5 empty] | 38 |  | 17 |  |  |  |  | 55
FA_PEL | [5 empty] | 1 | [6 empty] | 1
22 | [5 empty] | 1 | [6 empty] | 1
FA_PEM | [5 empty] | 134 | [6 empty] | 134
63 | [5 empty] | 130 | [6 empty] | 130
91 | [5 empty] | 4 | [6 empty] | 4
FA_PEO |  |  |  |  | 482 | [7 empty] | 482
20 |  |  |  |  | 26 | [7 empty] | 26
21 |  |  |  |  | 23 | [7 empty] | 23
22 |  |  |  |  | 5 | [7 empty] | 5
24 |  |  |  |  | 87 | [7 empty] | 87
25 |  |  |  |  | 51 | [7 empty] | 51
27 |  |  |  |  | 32 | [7 empty] | 32
28 |  |  |  |  | 24 | [7 empty] | 24
29 |  |  |  |  | 15 | [7 empty] | 15
30 |  |  |  |  | 54 | [7 empty] | 54
41 |  |  |  |  | 1 | [7 empty] | 1
42 |  |  |  |  | 1 | [7 empty] | 1
43 |  |  |  |  | 3 | [7 empty] | 3
44 |  |  |  |  | 3 | [7 empty] | 3
45 |  |  |  |  | 7 | [7 empty] | 7
46 |  |  |  |  | 23 | [7 empty] | 23
47 |  |  |  |  | 4 | [7 empty] | 4
52 |  |  |  |  | 5 | [7 empty] | 5
53 |  |  |  |  | 2 | [7 empty] | 2
56 |  |  |  |  | 7 | [7 empty] | 7
57 |  |  |  |  | 7 | [7 empty] | 7
58 |  |  |  |  | 1 | [7 empty] | 1
60 |  |  |  |  | 31 | [7 empty] | 31
64 |  |  |  |  | 6 | [7 empty] | 6
66 |  |  |  |  | 20 | [7 empty] | 20
67 |  |  |  |  | 15 | [7 empty] | 15
81 |  |  |  |  | 15 | [7 empty] | 15
82 |  |  |  |  | 2 | [7 empty] | 2
91 |  |  |  |  | 12 | [7 empty] | 12
FA_PESC |  |  |  |  | 546 | [5 empty] | 4 |  | 550
(blank) |  |  |  |  | 13 | [7 empty] | 13
20 |  |  |  |  | 48 | [7 empty] | 48
21 |  |  |  |  | 30 | [7 empty] | 30
22 |  |  |  |  | 17 | [7 empty] | 17
24 |  |  |  |  | 58 | [7 empty] | 58
25 |  |  |  |  | 61 | [7 empty] | 61
27 |  |  |  |  | 45 | [7 empty] | 45
28 |  |  |  |  | 15 | [7 empty] | 15
29 |  |  |  |  | 10 | [7 empty] | 10
30 |  |  |  |  | 50 | [7 empty] | 50
40 |  |  |  |  | 4 | [7 empty] | 4
45 |  |  |  |  | 9 | [7 empty] | 9
46 |  |  |  |  | 27 | [7 empty] | 27
47 |  |  |  |  | 13 | [7 empty] | 13
51 |  |  |  |  | 8 | [7 empty] | 8
52 |  |  |  |  | 22 | [7 empty] | 22
54 |  |  |  |  | 1 | [7 empty] | 1
56 |  |  |  |  | 2 | [7 empty] | 2
57 |  |  |  |  | 3 | [7 empty] | 3
60 |  |  |  |  | 9 | [7 empty] | 9
62 |  |  |  |  | 1 | [7 empty] | 1
63 |  |  |  |  | 10 | [7 empty] | 10
64 |  |  |  |  | 6 | [7 empty] | 6
65 |  |  |  |  | 12 | [7 empty] | 12
66 |  |  |  |  | 4 | [7 empty] | 4
67 |  |  |  |  | 8 | [7 empty] | 8
81 |  |  |  |  | 35 | [7 empty] | 35
87 |  |  |  |  | 3 | [5 empty] | 4 |  | 7
91 |  |  |  |  | 22 | [7 empty] | 22
FA_PESR |  |  |  |  | 49 | [7 empty] | 49
(blank) |  |  |  |  | 6 | [7 empty] | 6
20 |  |  |  |  | 4 | [7 empty] | 4
21 |  |  |  |  | 6 | [7 empty] | 6
81 |  |  |  |  | 21 | [7 empty] | 21
91 |  |  |  |  | 12 | [7 empty] | 12
FA_PESV |  |  |  |  | 15 | [7 empty] | 15
21 |  |  |  |  | 2 | [7 empty] | 2
28 |  |  |  |  | 5 | [7 empty] | 5
29 |  |  |  |  | 3 | [7 empty] | 3
52 |  |  |  |  | 2 | [7 empty] | 2
64 |  |  |  |  | 1 | [7 empty] | 1
67 |  |  |  |  | 2 | [7 empty] | 2
FA_PET |  |  |  |  | 547 | [5 empty] | 1 |  | 548
20 |  |  |  |  | 37 | [7 empty] | 37
21 |  |  |  |  | 31 | [7 empty] | 31
22 |  |  |  |  | 2 | [7 empty] | 2
24 |  |  |  |  | 88 | [7 empty] | 88
25 |  |  |  |  | 98 | [7 empty] | 98
27 |  |  |  |  | 46 | [7 empty] | 46
28 |  |  |  |  | 24 | [7 empty] | 24
29 |  |  |  |  | 3 | [7 empty] | 3
30 |  |  |  |  | 83 | [7 empty] | 83
42 |  |  |  |  | 2 | [7 empty] | 2
43 |  |  |  |  | 4 | [7 empty] | 4
44 |  |  |  |  | 2 | [7 empty] | 2
45 |  |  |  |  | 13 | [7 empty] | 13
46 |  |  |  |  | 19 | [7 empty] | 19
52 |  |  |  |  | 8 | [7 empty] | 8
54 |  |  |  |  | 1 | [7 empty] | 1
57 |  |  |  |  | 7 | [7 empty] | 7
60 |  |  |  |  | 36 | [5 empty] | 1 |  | 37
63 |  |  |  |  | 1 | [7 empty] | 1
64 |  |  |  |  | 2 | [7 empty] | 2
65 |  |  |  |  | 31 | [7 empty] | 31
66 |  |  |  |  | 6 | [7 empty] | 6
67 |  |  |  |  | 3 | [7 empty] | 3
FA_PEVB |  |  |  |  | 716 | 8557 |  |  |  |  | 237 |  | 9510
(blank) |  |  |  |  | 2 | 18 | [6 empty] | 20
05 | [5 empty] | 53 |  |  |  |  | 4 |  | 57
20 |  |  |  |  | 44 | 669 |  |  |  |  | 52 |  | 765
21 |  |  |  |  | 27 | 448 |  |  |  |  | 46 |  | 521
22 |  |  |  |  | 8 | 86 | [6 empty] | 94
24 |  |  |  |  | 1 | 157 | [6 empty] | 158
25 |  |  |  |  | 145 | 661 |  |  |  |  | 24 |  | 830
27 |  |  |  |  | 50 | 402 |  |  |  |  | 3 |  | 455
28 |  |  |  |  | 72 | 749 |  |  |  |  | 51 |  | 872
29 |  |  |  |  | 20 | 242 | [6 empty] | 262
30 |  |  |  |  | 93 | 1446 |  |  |  |  | 1 |  | 1540
40 |  |  |  |  | 5 | 99 | [6 empty] | 104
41 | [5 empty] | 37 | [6 empty] | 37
42 |  |  |  |  | 9 | 163 | [6 empty] | 172
43 |  |  |  |  | 7 | 49 | [6 empty] | 56
44 |  |  |  |  | 5 | 73 | [6 empty] | 78
45 |  |  |  |  | 12 | 102 |  |  |  |  | 5 |  | 119
46 |  |  |  |  | 19 | 242 | [6 empty] | 261
47 |  |  |  |  | 14 | 202 |  |  |  |  | 6 |  | 222
48 | [5 empty] | 4 | [6 empty] | 4
51 |  |  |  |  | 3 | 157 | [6 empty] | 160
52 |  |  |  |  | 5 | 457 | [6 empty] | 462
53 | [5 empty] | 85 | [6 empty] | 85
54 |  |  |  |  | 1 | 99 | [6 empty] | 100
56 | [5 empty] | 52 | [6 empty] | 52
57 |  |  |  |  | 15 | 120 | [6 empty] | 135
58 |  |  |  |  | 2 | 70 | [6 empty] | 72
60 |  |  |  |  | 18 | 163 | [6 empty] | 181
61 | [5 empty] | 17 | [6 empty] | 17
62 |  |  |  |  | 1 | 36 | [6 empty] | 37
63 |  |  |  |  | 4 | 215 |  |  |  |  | 4 |  | 223
64 |  |  |  |  | 8 | 287 |  |  |  |  | 8 |  | 303
65 |  |  |  |  | 11 | 185 | [6 empty] | 196
66 |  |  |  |  | 9 | 52 | [6 empty] | 61
67 |  |  |  |  | 15 | 347 | [6 empty] | 362
81 |  |  |  |  | 25 | 197 | [6 empty] | 222
82 | [5 empty] | 8 | [6 empty] | 8
87 |  |  |  |  | 7 | 21 |  |  |  |  | 24 |  | 52
91 |  |  |  |  | 59 | 87 | [6 empty] | 146
N/A | [10 empty] | 9 |  | 9
FA_PEVC | [5 empty] | 1557 |  | 1 |  |  | 6 |  | 1564
(blank) | [5 empty] | 24 | [6 empty] | 24
05 | [5 empty] | 9 | [6 empty] | 9
20 | [5 empty] | 54 | [6 empty] | 54
21 | [5 empty] | 69 | [6 empty] | 69
22 | [5 empty] | 3 | [6 empty] | 3
24 | [5 empty] | 51 | [6 empty] | 51
25 | [5 empty] | 27 | [6 empty] | 27
27 | [5 empty] | 46 | [6 empty] | 46
28 | [5 empty] | 145 | [6 empty] | 145
29 | [5 empty] | 48 | [6 empty] | 48
30 | [5 empty] | 127 |  | 1 |  |  |  |  | 128
40 | [5 empty] | 7 | [6 empty] | 7
41 | [5 empty] | 11 | [6 empty] | 11
42 | [5 empty] | 17 |  |  |  |  | 1 |  | 18
43 | [5 empty] | 3 | [6 empty] | 3
44 | [5 empty] | 23 | [6 empty] | 23
45 | [5 empty] | 10 | [6 empty] | 10
46 | [5 empty] | 51 | [6 empty] | 51
47 | [5 empty] | 51 | [6 empty] | 51
48 | [5 empty] | 1 | [6 empty] | 1
51 | [5 empty] | 22 | [6 empty] | 22
52 | [5 empty] | 102 | [6 empty] | 102
53 | [5 empty] | 16 | [6 empty] | 16
54 | [5 empty] | 98 | [6 empty] | 98
56 | [5 empty] | 15 | [6 empty] | 15
57 | [5 empty] | 35 | [6 empty] | 35
58 | [5 empty] | 6 | [6 empty] | 6
60 | [5 empty] | 35 | [6 empty] | 35
61 | [5 empty] | 2 | [6 empty] | 2
62 | [5 empty] | 5 | [6 empty] | 5
63 | [5 empty] | 35 | [6 empty] | 35
64 | [5 empty] | 117 | [6 empty] | 117
65 | [5 empty] | 111 | [6 empty] | 111
66 | [5 empty] | 21 | [6 empty] | 21
67 | [5 empty] | 54 | [6 empty] | 54
81 | [5 empty] | 20 | [6 empty] | 20
82 | [5 empty] | 2 | [6 empty] | 2
87 | [5 empty] | 4 |  |  |  |  | 5 |  | 9
91 | [5 empty] | 80 | [6 empty] | 80
FA_PEVD |  |  |  |  | 3 | [7 empty] | 3
81 |  |  |  |  | 3 | [7 empty] | 3
FA_PEVG |  |  |  |  | 151 | 2410 |  |  |  |  | 28 |  | 2589
20 |  |  |  |  | 5 | 145 |  |  |  |  | 2 |  | 152
21 |  |  |  |  | 7 | 222 | [6 empty] | 229
22 |  |  |  |  | 5 | 8 | [6 empty] | 13
24 |  |  |  |  | 17 | 366 |  |  |  |  | 9 |  | 392
25 |  |  |  |  | 3 | 246 | [6 empty] | 249
27 | [5 empty] | 23 | [6 empty] | 23
28 |  |  |  |  | 5 | 15 |  |  |  |  | 8 |  | 28
29 | [5 empty] | 9 | [6 empty] | 9
30 |  |  |  |  | 63 | 153 | [6 empty] | 216
40 | [5 empty] | 9 | [6 empty] | 9
41 | [5 empty] | 58 | [6 empty] | 58
42 | [5 empty] | 146 | [6 empty] | 146
43 | [5 empty] | 8 | [6 empty] | 8
44 | [5 empty] | 99 | [6 empty] | 99
45 | [5 empty] | 34 | [6 empty] | 34
46 | [5 empty] | 22 | [6 empty] | 22
47 | [5 empty] | 3 | [6 empty] | 3
52 | [5 empty] | 3 | [6 empty] | 3
53 | [5 empty] | 12 | [6 empty] | 12
54 | [5 empty] | 64 | [6 empty] | 64
56 | [5 empty] | 53 | [6 empty] | 53
57 | [5 empty] | 41 | [6 empty] | 41
58 | [5 empty] | 56 | [6 empty] | 56
60 |  |  |  |  | 11 | 286 | [6 empty] | 297
62 |  |  |  |  | 2 | 1 | [6 empty] | 3
64 |  |  |  |  | 4 | 4 | [6 empty] | 8
65 | [5 empty] | 53 | [6 empty] | 53
66 |  |  |  |  | 11 | 83 | [6 empty] | 94
67 | [5 empty] | 6 | [6 empty] | 6
81 |  |  |  |  | 1 | 169 |  |  |  |  | 5 |  | 175
82 | [5 empty] | 2 | [6 empty] | 2
87 |  |  |  |  | 1 | [5 empty] | 4 |  | 5
91 |  |  |  |  | 16 | 11 | [6 empty] | 27
FA_PEVL |  |  |  |  | 150 | 813 |  |  |  |  | 6 |  | 969
20 |  |  |  |  | 10 | 246 |  |  |  |  | 4 |  | 260
21 |  |  |  |  | 17 | 22 | [6 empty] | 39
22 |  |  |  |  | 4 | 51 | [6 empty] | 55
24 |  |  |  |  | 16 | 34 | [6 empty] | 50
25 |  |  |  |  | 15 | 60 | [6 empty] | 75
27 | [5 empty] | 25 |  |  |  |  | 2 |  | 27
28 |  |  |  |  | 27 | 148 | [6 empty] | 175
29 |  |  |  |  | 6 | 6 | [6 empty] | 12
30 |  |  |  |  | 1 | 67 | [6 empty] | 68
40 |  |  |  |  | 4 | 7 | [6 empty] | 11
42 | [5 empty] | 7 | [6 empty] | 7
43 | [5 empty] | 7 | [6 empty] | 7
44 | [5 empty] | 11 | [6 empty] | 11
45 | [5 empty] | 16 | [6 empty] | 16
46 |  |  |  |  | 7 | 19 | [6 empty] | 26
47 |  |  |  |  | 6 | 4 | [6 empty] | 10
48 | [5 empty] | 1 | [6 empty] | 1
51 | [5 empty] | 7 | [6 empty] | 7
52 |  |  |  |  | 3 | 5 | [6 empty] | 8
56 | [5 empty] | 1 | [6 empty] | 1
57 | [5 empty] | 13 | [6 empty] | 13
58 | [5 empty] | 3 | [6 empty] | 3
60 |  |  |  |  | 15 | 10 | [6 empty] | 25
63 | [5 empty] | 5 | [6 empty] | 5
64 | [5 empty] | 5 | [6 empty] | 5
66 |  |  |  |  | 3 | 12 | [6 empty] | 15
67 |  |  |  |  | 16 | 18 | [6 empty] | 34
81 | [5 empty] | 3 | [6 empty] | 3
FA_PEVM | [10 empty] | 9 |  | 9
52 | [10 empty] | 4 |  | 4
81 | [10 empty] | 5 |  | 5
FA_PEVN |  |  |  |  | 12 | 7 |  |  |  |  | 60 |  | 79
20 | [5 empty] | 4 |  |  |  |  | 16 |  | 20
22 | [5 empty] | 1 | [6 empty] | 1
25 | [5 empty] | 2 |  |  |  |  | 12 |  | 14
27 |  |  |  |  | 8 | [5 empty] | 2 |  | 10
28 | [10 empty] | 11 |  | 11
45 | [10 empty] | 2 |  | 2
46 |  |  |  |  | 4 | [7 empty] | 4
47 | [10 empty] | 4 |  | 4
52 | [10 empty] | 3 |  | 3
60 | [10 empty] | 2 |  | 2
64 | [10 empty] | 8 |  | 8
FA_PEVX | [10 empty] | 4 |  | 4
42 | [10 empty] | 1 |  | 1
87 | [10 empty] | 3 |  | 3
FA_PEVY |  |  |  |  | 21 | 44 | [6 empty] | 65
25 | [5 empty] | 1 | [6 empty] | 1
27 | [5 empty] | 1 | [6 empty] | 1
63 |  |  |  |  | 10 | 12 | [6 empty] | 22
64 |  |  |  |  | 2 | 4 | [6 empty] | 6
65 |  |  |  |  | 5 | [7 empty] | 5
66 |  |  |  |  | 4 | [7 empty] | 4
81 | [5 empty] | 26 | [6 empty] | 26
FA_REBC | [5 empty] | 4 | [6 empty] | 4
25 | [5 empty] | 2 | [6 empty] | 2
43 | [5 empty] | 2 | [6 empty] | 2
FA_REC | [5 empty] | 4 | [6 empty] | 4
30 | [5 empty] | 4 | [6 empty] | 4
FA_REDH | [5 empty] | 6 | [6 empty] | 6
81 | [5 empty] | 6 | [6 empty] | 6
FA_REDP | [5 empty] | 26 | [6 empty] | 26
21 | [5 empty] | 3 | [6 empty] | 3
25 | [5 empty] | 3 | [6 empty] | 3
27 | [5 empty] | 10 | [6 empty] | 10
45 | [5 empty] | 4 | [6 empty] | 4
80 | [5 empty] | 4 | [6 empty] | 4
87 | [5 empty] | 2 | [6 empty] | 2
FA_REEL | [5 empty] | 4 | [6 empty] | 4
81 | [5 empty] | 3 | [6 empty] | 3
87 | [5 empty] | 1 | [6 empty] | 1
FA_REFA | [5 empty] | 24 | [6 empty] | 24
21 | [5 empty] | 9 | [6 empty] | 9
25 | [5 empty] | 3 | [6 empty] | 3
45 | [5 empty] | 3 | [6 empty] | 3
87 | [5 empty] | 9 | [6 empty] | 9
FA_REFC | [5 empty] | 131 | [6 empty] | 131
24 | [5 empty] | 27 | [6 empty] | 27
25 | [5 empty] | 14 | [6 empty] | 14
27 | [5 empty] | 4 | [6 empty] | 4
30 | [5 empty] | 25 | [6 empty] | 25
60 | [5 empty] | 5 | [6 empty] | 5
65 | [5 empty] | 15 | [6 empty] | 15
66 | [5 empty] | 2 | [6 empty] | 2
67 | [5 empty] | 3 | [6 empty] | 3
80 | [5 empty] | 2 | [6 empty] | 2
87 | [5 empty] | 6 | [6 empty] | 6
91 | [5 empty] | 28 | [6 empty] | 28
FA_REMC | [5 empty] | 3 | [6 empty] | 3
27 | [5 empty] | 2 | [6 empty] | 2
87 | [5 empty] | 1 | [6 empty] | 1
FA_REMR | [5 empty] | 6 | [6 empty] | 6
24 | [5 empty] | 6 | [6 empty] | 6
FA_REMT | [5 empty] | 11 | [6 empty] | 11
65 | [5 empty] | 10 | [6 empty] | 10
87 | [5 empty] | 1 | [6 empty] | 1
FA_RENG | [5 empty] | 10 | [6 empty] | 10
27 | [5 empty] | 2 | [6 empty] | 2
80 | [5 empty] | 4 | [6 empty] | 4
91 | [5 empty] | 4 | [6 empty] | 4
FA_REPC | [5 empty] | 271 |  |  |  |  | 4 |  | 275
05 | [5 empty] | 6 | [6 empty] | 6
21 | [5 empty] | 10 | [6 empty] | 10
24 | [5 empty] | 12 | [6 empty] | 12
27 | [5 empty] | 4 | [6 empty] | 4
28 | [5 empty] | 22 | [6 empty] | 22
29 | [5 empty] | 16 | [6 empty] | 16
30 | [5 empty] | 30 | [6 empty] | 30
47 | [5 empty] | 14 | [6 empty] | 14
51 | [5 empty] | 12 | [6 empty] | 12
52 | [5 empty] | 36 | [6 empty] | 36
53 | [5 empty] | 4 | [6 empty] | 4
56 | [5 empty] | 16 | [6 empty] | 16
57 | [5 empty] | 12 | [6 empty] | 12
58 | [5 empty] | 2 | [6 empty] | 2
60 | [5 empty] | 14 | [6 empty] | 14
62 | [5 empty] | 2 | [6 empty] | 2
65 | [5 empty] | 5 | [6 empty] | 5
67 | [5 empty] | 14 | [6 empty] | 14
80 | [5 empty] | 4 | [6 empty] | 4
81 | [5 empty] | 15 | [6 empty] | 15
82 | [5 empty] | 4 | [6 empty] | 4
87 | [5 empty] | 2 |  |  |  |  | 4 |  | 6
91 | [5 empty] | 13 | [6 empty] | 13
N/A | [5 empty] | 2 | [6 empty] | 2
FA_REPD |  | 1 |  |  |  | 32 |  |  |  |  | 6 |  | 39
20 | [5 empty] | 3 | [6 empty] | 3
22 |  | 1 |  |  |  | 3 | [6 empty] | 4
25 | [5 empty] | 4 | [6 empty] | 4
27 | [5 empty] | 3 | [6 empty] | 3
29 | [5 empty] | 1 | [6 empty] | 1
30 | [5 empty] | 1 | [6 empty] | 1
60 | [5 empty] | 9 | [6 empty] | 9
66 | [5 empty] | 2 | [6 empty] | 2
81 | [5 empty] | 6 | [6 empty] | 6
87 | [10 empty] | 6 |  | 6
FA_RER | [5 empty] | 2 | [6 empty] | 2
56 | [5 empty] | 1 | [6 empty] | 1
67 | [5 empty] | 1 | [6 empty] | 1
FA_RETG | [5 empty] | 5 | [6 empty] | 5
65 | [5 empty] | 5 | [6 empty] | 5
FA_RETP | [5 empty] | 5 | [6 empty] | 5
65 | [5 empty] | 5 | [6 empty] | 5
FA_REUC | [10 empty] | 1 |  | 1
67 | [10 empty] | 1 |  | 1
FA_SEC |  |  |  | 6 | [8 empty] | 6
65 |  |  |  | 6 | [8 empty] | 6
FA_SEE | [5 empty] | 3 | [6 empty] | 3
28 | [5 empty] | 3 | [6 empty] | 3
FA_SEFB | [5 empty] | 2 |  | 302 |  |  | 6 |  | 310
20 | [7 empty] | 5 |  |  |  |  | 5
21 | [7 empty] | 25 |  |  |  |  | 25
22 | [7 empty] | 1 |  |  |  |  | 1
24 | [7 empty] | 11 |  |  |  |  | 11
25 | [7 empty] | 6 |  |  |  |  | 6
27 | [7 empty] | 5 |  |  | 4 |  | 9
28 | [7 empty] | 25 |  |  |  |  | 25
29 | [7 empty] | 11 |  |  |  |  | 11
30 | [7 empty] | 45 |  |  |  |  | 45
40 | [7 empty] | 4 |  |  |  |  | 4
41 | [7 empty] | 4 |  |  |  |  | 4
42 | [7 empty] | 4 |  |  |  |  | 4
43 | [7 empty] | 4 |  |  |  |  | 4
45 | [7 empty] | 4 |  |  |  |  | 4
46 | [5 empty] | 2 |  | 2 |  |  | 2 |  | 6
47 | [7 empty] | 9 |  |  |  |  | 9
51 | [7 empty] | 9 |  |  |  |  | 9
52 | [7 empty] | 38 |  |  |  |  | 38
53 | [7 empty] | 4 |  |  |  |  | 4
57 | [7 empty] | 3 |  |  |  |  | 3
60 | [7 empty] | 11 |  |  |  |  | 11
62 | [7 empty] | 2 |  |  |  |  | 2
65 | [7 empty] | 3 |  |  |  |  | 3
67 | [7 empty] | 11 |  |  |  |  | 11
81 | [7 empty] | 28 |  |  |  |  | 28
91 | [7 empty] | 28 |  |  |  |  | 28
FA_SEFE | [5 empty] | 158 |  | 5 |  |  | 31 |  | 194
05 | [5 empty] | 6 | [6 empty] | 6
20 | [5 empty] | 2 | [6 empty] | 2
21 | [5 empty] | 2 | [6 empty] | 2
24 | [5 empty] | 9 | [6 empty] | 9
25 | [5 empty] | 9 | [6 empty] | 9
27 | [5 empty] | 1 |  |  |  |  | 4 |  | 5
29 | [5 empty] | 5 | [6 empty] | 5
30 | [5 empty] | 8 | [6 empty] | 8
45 | [5 empty] | 2 | [6 empty] | 2
46 | [5 empty] | 4 |  |  |  |  | 2 |  | 6
47 | [5 empty] | 10 | [6 empty] | 10
51 | [5 empty] | 2 | [6 empty] | 2
60 | [5 empty] | 1 | [6 empty] | 1
62 | [5 empty] | 2 | [6 empty] | 2
63 | [5 empty] | 4 | [6 empty] | 4
64 | [5 empty] | 2 | [6 empty] | 2
65 | [5 empty] | 35 | [6 empty] | 35
67 | [5 empty] | 2 | [6 empty] | 2
81 | [5 empty] | 18 |  | 5 |  |  |  |  | 23
87 | [10 empty] | 25 |  | 25
91 | [5 empty] | 34 | [6 empty] | 34
FA_SEFS | [5 empty] | 12 |  |  |  |  | 6 |  | 18
27 | [10 empty] | 4 |  | 4
46 | [10 empty] | 2 |  | 2
91 | [5 empty] | 12 | [6 empty] | 12
FA_SEHF | [5 empty] | 70 | [6 empty] | 70
21 | [5 empty] | 2 | [6 empty] | 2
24 | [5 empty] | 9 | [6 empty] | 9
25 | [5 empty] | 3 | [6 empty] | 3
27 | [5 empty] | 2 | [6 empty] | 2
30 | [5 empty] | 9 | [6 empty] | 9
45 | [5 empty] | 1 | [6 empty] | 1
60 | [5 empty] | 1 | [6 empty] | 1
65 | [5 empty] | 30 | [6 empty] | 30
67 | [5 empty] | 1 | [6 empty] | 1
80 | [5 empty] | 4 | [6 empty] | 4
87 | [5 empty] | 4 | [6 empty] | 4
91 | [5 empty] | 4 | [6 empty] | 4
FA_SEHS | [5 empty] | 48 | [6 empty] | 48
21 | [5 empty] | 6 | [6 empty] | 6
28 | [5 empty] | 11 | [6 empty] | 11
30 | [5 empty] | 20 | [6 empty] | 20
52 | [5 empty] | 3 | [6 empty] | 3
60 | [5 empty] | 8 | [6 empty] | 8
FA_SEHT | [5 empty] | 51 | [6 empty] | 51
20 | [5 empty] | 18 | [6 empty] | 18
21 | [5 empty] | 6 | [6 empty] | 6
25 | [5 empty] | 5 | [6 empty] | 5
27 | [5 empty] | 2 | [6 empty] | 2
30 | [5 empty] | 4 | [6 empty] | 4
46 | [5 empty] | 3 | [6 empty] | 3
57 | [5 empty] | 3 | [6 empty] | 3
81 | [5 empty] | 6 | [6 empty] | 6
91 | [5 empty] | 4 | [6 empty] | 4
FA_SEL | [5 empty] | 2 |  | 51 |  |  |  |  | 53
(blank) | [5 empty] | 2 | [6 empty] | 2
22 | [7 empty] | 1 |  |  |  |  | 1
24 | [7 empty] | 2 |  |  |  |  | 2
27 | [7 empty] | 2 |  |  |  |  | 2
28 | [7 empty] | 1 |  |  |  |  | 1
41 | [7 empty] | 1 |  |  |  |  | 1
43 | [7 empty] | 1 |  |  |  |  | 1
46 | [7 empty] | 1 |  |  |  |  | 1
56 | [7 empty] | 9 |  |  |  |  | 9
58 | [7 empty] | 6 |  |  |  |  | 6
62 | [7 empty] | 2 |  |  |  |  | 2
67 | [7 empty] | 2 |  |  |  |  | 2
81 | [7 empty] | 2 |  |  |  |  | 2
87 | [7 empty] | 5 |  |  |  |  | 5
91 | [7 empty] | 16 |  |  |  |  | 16
FA_SEM | [5 empty] | 5 | [6 empty] | 5
42 | [5 empty] | 1 | [6 empty] | 1
43 | [5 empty] | 2 | [6 empty] | 2
44 | [5 empty] | 1 | [6 empty] | 1
N/A | [5 empty] | 1 | [6 empty] | 1
FA_SENF | [5 empty] | 4 | [6 empty] | 4
25 | [5 empty] | 2 | [6 empty] | 2
60 | [5 empty] | 2 | [6 empty] | 2
FA_SEPA | [5 empty] | 192 | [6 empty] | 192
(blank) | [5 empty] | 6 | [6 empty] | 6
20 | [5 empty] | 9 | [6 empty] | 9
21 | [5 empty] | 6 | [6 empty] | 6
22 | [5 empty] | 9 | [6 empty] | 9
25 | [5 empty] | 24 | [6 empty] | 24
27 | [5 empty] | 3 | [6 empty] | 3
28 | [5 empty] | 10 | [6 empty] | 10
29 | [5 empty] | 9 | [6 empty] | 9
30 | [5 empty] | 28 | [6 empty] | 28
52 | [5 empty] | 4 | [6 empty] | 4
60 | [5 empty] | 50 | [6 empty] | 50
66 | [5 empty] | 16 | [6 empty] | 16
81 | [5 empty] | 18 | [6 empty] | 18
FA_SEPC | [10 empty] | 59 |  | 59
20 | [10 empty] | 10 |  | 10
21 | [10 empty] | 1 |  | 1
25 | [10 empty] | 6 |  | 6
27 | [10 empty] | 7 |  | 7
28 | [10 empty] | 12 |  | 12
42 | [10 empty] | 1 |  | 1
45 | [10 empty] | 1 |  | 1
46 | [10 empty] | 3 |  | 3
47 | [10 empty] | 2 |  | 2
57 | [10 empty] | 6 |  | 6
60 | [10 empty] | 1 |  | 1
64 | [10 empty] | 4 |  | 4
87 | [10 empty] | 5 |  | 5
FA_SEPHC | [5 empty] | 2 | [6 empty] | 2
21 | [5 empty] | 2 | [6 empty] | 2
FA_SEPHS | [5 empty] | 186 |  |  |  |  | 4 |  | 190
20 | [5 empty] | 9 | [6 empty] | 9
21 | [5 empty] | 8 | [6 empty] | 8
22 | [5 empty] | 3 | [6 empty] | 3
24 | [5 empty] | 9 | [6 empty] | 9
25 | [5 empty] | 18 | [6 empty] | 18
27 | [5 empty] | 6 | [6 empty] | 6
28 | [5 empty] | 6 | [6 empty] | 6
29 | [5 empty] | 7 | [6 empty] | 7
30 | [5 empty] | 10 | [6 empty] | 10
40 | [5 empty] | 1 | [6 empty] | 1
42 | [5 empty] | 1 | [6 empty] | 1
43 | [5 empty] | 3 | [6 empty] | 3
44 | [5 empty] | 1 | [6 empty] | 1
45 | [5 empty] | 2 | [6 empty] | 2
46 | [5 empty] | 1 | [6 empty] | 1
47 | [5 empty] | 2 | [6 empty] | 2
52 | [5 empty] | 1 | [6 empty] | 1
53 | [5 empty] | 2 | [6 empty] | 2
57 | [5 empty] | 7 | [6 empty] | 7
60 | [5 empty] | 26 | [6 empty] | 26
63 | [5 empty] | 6 | [6 empty] | 6
64 | [5 empty] | 23 | [6 empty] | 23
65 | [5 empty] | 6 |  |  |  |  | 4 |  | 10
66 | [5 empty] | 4 | [6 empty] | 4
67 | [5 empty] | 6 | [6 empty] | 6
87 | [5 empty] | 2 | [6 empty] | 2
91 | [5 empty] | 16 | [6 empty] | 16
FA_SES | [5 empty] | 16 |  | 56 |  |  |  |  | 72
24 | [5 empty] | 16 | [6 empty] | 16
47 | [7 empty] | 16 |  |  |  |  | 16
51 | [7 empty] | 8 |  |  |  |  | 8
52 | [7 empty] | 32 |  |  |  |  | 32
FA_SETAC | [5 empty] | 60 | [6 empty] | 60
05 | [5 empty] | 2 | [6 empty] | 2
21 | [5 empty] | 2 | [6 empty] | 2
24 | [5 empty] | 10 | [6 empty] | 10
28 | [5 empty] | 5 | [6 empty] | 5
29 | [5 empty] | 4 | [6 empty] | 4
30 | [5 empty] | 7 | [6 empty] | 7
51 | [5 empty] | 3 | [6 empty] | 3
52 | [5 empty] | 6 | [6 empty] | 6
53 | [5 empty] | 1 | [6 empty] | 1
56 | [5 empty] | 1 | [6 empty] | 1
62 | [5 empty] | 3 | [6 empty] | 3
67 | [5 empty] | 2 | [6 empty] | 2
81 | [5 empty] | 9 | [6 empty] | 9
87 | [5 empty] | 4 | [6 empty] | 4
91 | [5 empty] | 1 | [6 empty] | 1
FA_SETAP | [5 empty] | 28 |  | 5 |  | 7 |  |  | 40
28 | [5 empty] | 3 | [6 empty] | 3
56 | [5 empty] | 6 | [6 empty] | 6
57 | [5 empty] | 3 | [6 empty] | 3
58 | [5 empty] | 3 | [6 empty] | 3
60 | [5 empty] | 1 | [6 empty] | 1
65 | [5 empty] | 5 | [6 empty] | 5
67 | [5 empty] | 3 | [6 empty] | 3
82 | [5 empty] | 4 | [6 empty] | 4
N/A | [7 empty] | 5 |  | 7 |  |  | 12
FA_SETPC | [5 empty] | 1 |  |  |  |  | 10 |  | 11
57 | [10 empty] | 1 |  | 1
81 | [10 empty] | 5 |  | 5
87 | [5 empty] | 1 |  |  |  |  | 4 |  | 5
FA_SEZ | [5 empty] | 2 |  | 62 |  |  |  |  | 64
42 | [7 empty] | 1 |  |  |  |  | 1
63 | [5 empty] | 2 | [6 empty] | 2
64 | [7 empty] | 1 |  |  |  |  | 1
65 | [7 empty] | 30 |  |  |  |  | 30
66 | [7 empty] | 1 |  |  |  |  | 1
87 | [7 empty] | 1 |  |  |  |  | 1
91 | [7 empty] | 28 |  |  |  |  | 28
FA_SQFC | [8 empty] | 21 |  |  |  | 21
81 | [8 empty] | 21 |  |  |  | 21
FA_SQFDF |  |  | 392 | [7 empty] | 28 |  | 420
78 |  |  | 376 | [7 empty] | 26 |  | 402
87 |  |  | 4 | [9 empty] | 4
91 |  |  | 12 | [9 empty] | 12
N/A | [10 empty] | 2 |  | 2
FA_SQFDG |  |  | 719 | [7 empty] | 20 |  | 739
78 |  |  | 693 | [7 empty] | 18 |  | 711
87 |  |  | 2 | [9 empty] | 2
91 |  |  | 24 | [9 empty] | 24
N/A | [10 empty] | 2 |  | 2
FA_SQFDS |  |  | 140 | [9 empty] | 140
78 |  |  | 140 | [9 empty] | 140
FA_SQFFD | [5 empty] | 9 |  | 12 | 5 |  |  |  | 26
20 | [5 empty] | 2 | [6 empty] | 2
21 | [5 empty] | 5 | [6 empty] | 5
27 | [5 empty] | 1 | [6 empty] | 1
45 | [5 empty] | 1 | [6 empty] | 1
81 | [8 empty] | 5 |  |  |  | 5
91 | [7 empty] | 12 |  |  |  |  | 12
FA_SQFFH | [8 empty] | 3 |  |  |  | 3
81 | [8 empty] | 3 |  |  |  | 3
FA_SQFFM | [8 empty] | 23 |  |  |  | 23
81 | [8 empty] | 23 |  |  |  | 23
FA_SQFFY | [8 empty] | 118 |  |  |  | 118
81 | [8 empty] | 118 |  |  |  | 118
FA_SQFRA |  |  | 241 |  | 1 | [5 empty] | 2 |  | 244
60 |  |  |  |  | 1 | [7 empty] | 1
78 |  |  | 203 | [7 empty] | 2 |  | 205
81 |  |  | 29 | [9 empty] | 29
82 |  |  | 1 | [9 empty] | 1
91 |  |  | 8 | [9 empty] | 8
FA_SQFRE | [8 empty] | 20 |  |  |  | 20
53 | [8 empty] | 20 |  |  |  | 20
FA_SQMT | [5 empty] | 2 | [6 empty] | 2
24 | [5 empty] | 2 | [6 empty] | 2
FA_SQTA |  |  | 35 |  | 15 | [5 empty] | 10 |  | 60
25 |  |  |  |  | 12 | [7 empty] | 12
78 |  |  | 18 | [7 empty] | 7 |  | 25
81 |  |  | 12 |  | 3 | [7 empty] | 15
87 |  |  | 5 | [9 empty] | 5
N/A | [10 empty] | 3 |  | 3
FA_SQTB |  |  | 61 |  | 8 | [5 empty] | 14 | 86 | 169
78 |  |  | 16 | [9 empty] | 16
81 |  |  | 45 | [9 empty] | 45
91 |  |  |  |  | 8 | [7 empty] | 8
98 | [10 empty] | 8 | 86 | 94
N/A | [10 empty] | 6 |  | 6
FA_SQTE | [10 empty] | 5 | 28 | 33
83 | [10 empty] | 1 | 27 | 28
99 | [11 empty] | 1 | 1
N/A | [10 empty] | 4 |  | 4
FA_SQTH | [11 empty] | 95 | 95
83 | [11 empty] | 20 | 20
96 | [11 empty] | 75 | 75
FA_SQTL | [10 empty] | 219 | 268 | 487
98 | [10 empty] | 187 | 268 | 455
N/A | [10 empty] | 32 |  | 32
FA_SQTN | [11 empty] | 3 | 3
99 | [11 empty] | 3 | 3
FA_SQTOF | [10 empty] | 2 | 4 | 6
99 | [11 empty] | 4 | 4
N/A | [10 empty] | 2 |  | 2
FA_SQTP | [10 empty] | 104 |  | 104
98 | [10 empty] | 12 |  | 12
N/A | [10 empty] | 92 |  | 92
FA_SQTS | [10 empty] | 67 | 34 | 101
83 | [10 empty] | 9 | 1 | 10
97 | [10 empty] | 1 | 31 | 32
98 | [10 empty] | 2 |  | 2
99 | [11 empty] | 2 | 2
N/A | [10 empty] | 55 |  | 55
FA_SQTV | [10 empty] | 75 | 92 | 167
76 | [11 empty] | 18 | 18
83 | [10 empty] | 1 |  | 1
96 | [10 empty] | 74 | 74 | 148
FA_SQTW | [10 empty] | 17 |  | 17
N/A | [10 empty] | 17 |  | 17
FA_SQTY | [10 empty] | 4 |  | 4
78 | [10 empty] | 4 |  | 4
FA_SYLH | 25 |  |  | 2 |  | 6 | 283 | [5 empty] | 316
(blank) | 25 | [5 empty] | 220 | [5 empty] | 245
05 | [6 empty] | 1 | [5 empty] | 1
20 | [6 empty] | 2 | [5 empty] | 2
21 | [6 empty] | 2 | [5 empty] | 2
22 | [6 empty] | 1 | [5 empty] | 1
24 | [6 empty] | 1 | [5 empty] | 1
25 | [6 empty] | 2 | [5 empty] | 2
27 | [6 empty] | 2 | [5 empty] | 2
28 | [6 empty] | 2 | [5 empty] | 2
29 | [6 empty] | 2 | [5 empty] | 2
30 | [6 empty] | 1 | [5 empty] | 1
40 | [6 empty] | 2 | [5 empty] | 2
41 | [6 empty] | 1 | [5 empty] | 1
42 | [6 empty] | 2 | [5 empty] | 2
43 | [6 empty] | 1 | [5 empty] | 1
44 | [5 empty] | 1 | 2 | [5 empty] | 3
45 | [6 empty] | 1 | [5 empty] | 1
46 | [6 empty] | 2 | [5 empty] | 2
47 | [6 empty] | 2 | [5 empty] | 2
48 | [6 empty] | 1 | [5 empty] | 1
51 | [6 empty] | 1 | [5 empty] | 1
52 | [6 empty] | 1 | [5 empty] | 1
53 | [6 empty] | 2 | [5 empty] | 2
54 | [6 empty] | 2 | [5 empty] | 2
56 | [6 empty] | 2 | [5 empty] | 2
57 | [6 empty] | 2 | [5 empty] | 2
58 | [6 empty] | 2 | [5 empty] | 2
60 | [6 empty] | 1 | [5 empty] | 1
61 | [6 empty] | 1 | [5 empty] | 1
62 | [6 empty] | 2 | [5 empty] | 2
63 | [6 empty] | 2 | [5 empty] | 2
64 | [6 empty] | 2 | [5 empty] | 2
65 | [6 empty] | 1 | [5 empty] | 1
66 | [6 empty] | 1 | [5 empty] | 1
67 | [6 empty] | 1 | [5 empty] | 1
81 | [5 empty] | 3 | 3 | [5 empty] | 6
82 | [6 empty] | 1 | [5 empty] | 1
86 | [6 empty] | 1 | [5 empty] | 1
87 | [5 empty] | 2 | 1 | [5 empty] | 3
91 | [6 empty] | 1 | [5 empty] | 1
94 |  |  |  | 2 | [8 empty] | 2
N/A | [6 empty] | 3 | [5 empty] | 3
FA_WECO | [5 empty] | 11 | [6 empty] | 11
24 | [5 empty] | 2 | [6 empty] | 2
27 | [5 empty] | 8 | [6 empty] | 8
91 | [5 empty] | 1 | [6 empty] | 1
FA_WEHY | [5 empty] | 2 | [6 empty] | 2
30 | [5 empty] | 2 | [6 empty] | 2
SOFT |  |  |  |  | 28 | [7 empty] | 28
22 |  |  |  |  | 2 | [7 empty] | 2
24 |  |  |  |  | 2 | [7 empty] | 2
60 |  |  |  |  | 20 | [7 empty] | 20
66 |  |  |  |  | 3 | [7 empty] | 3
87 |  |  |  |  | 1 | [7 empty] | 1
Grand Total | 25 | 3802 | 2143 | 28 | 10765 | 15129 | 283 | 12916 | 191 | 1046 | 1426 | 681 | 48435

## FailureCodeDefaultCriticality
Copied from Failure Codes list after filtering |  |  | Defaults to use initially | [11 empty] | Ratings from AGT Criticality / UMCL spreadsheet
Caution - codes may disappear from the list, check before pasting | [14 empty] | 3 | E08 | H02 | H02 | H02 | 8 | 2 | 2 | 2 | 8 | A
FailureCode | Description | Number found in ASSET-C WND | Likelihood | SC_Impact | EC_Impact | PC_impact | BC_Impact | SC_Likelihood | EC_Likelihood | PC_Likelihood | BC_Likelihood | 1-10 | ABC | Basis | L | - | EC | PC | BC | SC | EC2 | PC3 | BC4 | 1-10 | ABC
FA_CFBC | CONTROL ROOM | 6 | 3 | E08 | H02 | H02 | H02 | 3 | 3 | 3 | 3 | 8 | A | Copied From AGT UMCL Criticality Guide | 3 | E08 | H02 | H02 | H02 | 8 | 2 | 2 | 2 | 8 | A
FA_CFSGA | ACCESS CONTROL GATE | 37 | 7 | G04 | H02 | H02 | H02 | 7 | 7 | 7 | 7 | 4 | B | Copied From AGT UMCL Criticality Guide | 7 | G04 | H02 | H02 | H02 | 4 | 2 | 2 | 2 | 4 | B
FA_CFSGW | WALL OR FENCE | 5 | 6 | G04 | H02 | H02 | H02 | 6 | 6 | 6 | 6 | 4 | B | Copied From AGT UMCL Criticality Guide | 6 | G04 | H02 | H02 | H02 | 4 | 2 | 2 | 2 | 4 | B
FA_CFSSE | EQUIPMENT SUPPORT STRUCTURE | 104 | 5 | E08 | H02 | H02 | G04 | 5 | 5 | 5 | 5 | 8 | A | Copied From AGT UMCL Criticality Guide | 5 | E08 | H02 | H02 | G04 | 8 | 2 | 2 | 4 | 8 | A
FA_CFSSF | STRUCTURAL FOUNDATION | 19 | 5 | F06 | H02 | H02 | H02 | 5 | 5 | 5 | 5 | 6 | B | Copied From AGT UMCL Criticality Guide | 5 | F06 | H02 | H02 | H02 | 6 | 2 | 2 | 2 | 6 | B
FA_CFSST | STRUCTURAL BASE | 917 | 7 | E08 | H02 | H02 | G04 | 7 | 7 | 7 | 7 | 8 | A | Copied From AGT UMCL Criticality Guide | 7 | E08 | H02 | H02 | G04 | 8 | 2 | 2 | 4 | 8 | A
FA_EECF | LIGHT FITTING | 398 | 7 | E08 | H02 | H02 | H02 | 7 | 7 | 7 | 7 | 8 | A | Copied From AGT UMCL Criticality Guide | 7 | E08 | H02 | H02 | H02 | 8 | 2 | 2 | 2 | 8 | A
FA_EECH | ELECTRIC HEATER | 123 | 6 | E | H | F | H | 6 | 6 | 6 | 6 | 8 | A | Initial Estimate based quick judegment (not in AGT) | 6 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_EECMD | DC ELECTRIC MOTOR | 7 | 6 | E | H | F | H | 6 | 6 | 6 | 6 | 8 | A | Initial Estimate based quick judegment (not in AGT) | 6 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_EECMI | AC INDUCTION ELECTRIC MOTOR | 645 | 6 | E | H | F | H | 6 | 6 | 6 | 6 | 8 | A | Initial Estimate based quick judegment (not in AGT) | 6 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_EECMS | AC SYNCHRONOUS ELECTRIC MOTOR | 9 | 6 | E | H | F | H | 6 | 6 | 6 | 6 | 8 | A | Initial Estimate based quick judegment (not in AGT) | 6 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_EECO | ELECTRIC SOCKET OUTLET | 21 | 6 | G04 | H02 | H02 | H02 | 6 | 6 | 6 | 6 | 4 | B | Copied From AGT UMCL Criticality Guide | 6 | G04 | H02 | H02 | H02 | 4 | 2 | 2 | 2 | 4 | B
FA_EECT | TRACE HEATING CIRCUIT | 2 | 6 | G04 | H02 | H02 | G04 | 6 | 6 | 6 | 6 | 4 | B | Copied From AGT UMCL Criticality Guide | 6 | G04 | H02 | H02 | G04 | 4 | 2 | 2 | 4 | 4 | B
FA_EEPBA | AIR CIRCUIT BREAKER | 868 | 6 | E | H | F | H | 6 | 6 | 6 | 6 | 8 | A | Initial Estimate based quick judegment (not in AGT) | 6 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_EEPBV | VACUUM CIRCUIT BREAKER | 48 | 6 | E | H | F | H | 6 | 6 | 6 | 6 | 8 | A | Initial Estimate based quick judegment (not in AGT) | 6 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_EEPCS | SACRIFICIAL ANODE | 114 | 5 | H02 | H02 | H02 | G04 | 5 | 5 | 5 | 5 | 4 | B | Copied From AGT UMCL Criticality Guide | 5 | H02 | H02 | H02 | G04 | 2 | 2 | 2 | 4 | 4 | B
FA_EEPNE | EARTHING BAR | 118 | 6 | F06 | H02 | G04 | G04 | 6 | 6 | 6 | 6 | 6 | B | Copied From AGT UMCL Criticality Guide | 6 | F06 | H02 | G04 | G04 | 6 | 2 | 4 | 4 | 6 | B
FA_EEPNN | NEUTRAL GROUND RESISTOR | 8 | 6 | E08 | H02 | F06 | G04 | 6 | 6 | 6 | 6 | 8 | A | Copied From AGT UMCL Criticality Guide | 6 | E08 | H02 | F06 | G04 | 8 | 2 | 6 | 4 | 8 | A
FA_EEPS | START / STOP SWITCH | 347 | 6 | E | H | F | H | 6 | 6 | 6 | 6 | 8 | A | Initial Estimate based quick judegment (not in AGT) | 7 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_EEPU | UNINTERRUPTIBLE POWER SUPPLY | 29 | 7 | D10 | H02 | F06 | F06 | 7 | 7 | 7 | 7 | 10 | A | Copied From AGT UMCL Criticality Guide | 7 | D10 | H02 | F06 | F06 | 10 | 2 | 6 | 6 | 10 | A
FA_EETA | REACTOR / INDUCTOR | 6 | 5 | E08 | H02 | F06 | F06 | 5 | 5 | 5 | 5 | 8 | A | Copied From AGT UMCL Criticality Guide | 5 | E08 | H02 | F06 | F06 | 8 | 2 | 6 | 6 | 8 | A
FA_EETB | BATTERY | 39 | 7 | E08 | H02 | F06 | F06 | 7 | 7 | 7 | 7 | 8 | A | Copied From AGT UMCL Criticality Guide | 7 | E08 | H02 | F06 | F06 | 8 | 2 | 6 | 6 | 8 | A
FA_EETC | BATTERY CHARGER | 57 | 7 | E08 | H02 | F06 | F06 | 7 | 7 | 7 | 7 | 8 | A | Copied From AGT UMCL Criticality Guide | 7 | E08 | H02 | F06 | F06 | 8 | 2 | 6 | 6 | 8 | A
FA_EETD | BUS DUCT / BUS BAR | 70 | 3 | F05 | H01 | F05 | G03 | 3 | 3 | 3 | 3 | 5 | B | Copied From AGT UMCL Criticality Guide | 3 | F05 | H01 | F05 | G03 | 5 | 1 | 5 | 3 | 5 | B
FA_EETFW | WET TRANSFORMER | 21 | 4 | H02 | H02 | F06 | F06 | 4 | 4 | 4 | 4 | 6 | B | Copied From AGT UMCL Criticality Guide | 4 | H02 | H02 | F06 | F06 | 2 | 2 | 6 | 6 | 6 | B
FA_EETGA | AC ELECTRIC GENERATOR | 10 | 5 | G04 | H02 | F06 | G04 | 5 | 5 | 5 | 5 | 6 | B | Copied From AGT UMCL Criticality Guide | 5 | G04 | H02 | F06 | G04 | 4 | 2 | 6 | 4 | 6 | B
FA_EETI | ELECTRIC ISOLATOR | 25 | 6 | G04 | H02 | H02 | H02 | 6 | 6 | 6 | 6 | 4 | B | Copied From AGT UMCL Criticality Guide | 6 | G04 | H02 | H02 | H02 | 4 | 2 | 2 | 2 | 4 | B
FA_EETM | MOTOR CONTROL CENTER | 910 | 6 | E | H | F | H | 6 | 6 | 6 | 6 | 8 | A | Initial Estimate based quick judegment (not in AGT) | 7 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_EETO | POWER / CONTROL MODULE | 5 | 6 | E | H | F | H | 6 | 6 | 6 | 6 | 8 | A | Initial Estimate based quick judegment (not in AGT) | 7 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_EETP | ELECTRICAL PANEL | 3 | 4 | E08 | H02 | F06 | F06 | 4 | 4 | 4 | 4 | 8 | A | Copied From AGT UMCL Criticality Guide | 4 | E08 | H02 | F06 | F06 | 8 | 2 | 6 | 6 | 8 | A
FA_EETQ | VARIABLE FREQUENCY DRIVE | 66 | 6 | E | H | F | H | 6 | 6 | 6 | 6 | 8 | A | Initial Estimate based quick judegment (not in AGT) | 7 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_EETR | POWER RECTIFIER | 15 | 4 | H02 | H02 | F06 | F06 | 4 | 4 | 4 | 4 | 6 | B | Copied From AGT UMCL Criticality Guide | 4 | H02 | H02 | F06 | F06 | 2 | 2 | 6 | 6 | 6 | B
FA_EETW | SWITCHGEAR | 171 | 6 | E | H | F | H | 6 | 6 | 6 | 6 | 8 | A | Initial Estimate based quick judegment (not in AGT) | 4 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_EETY | POWER SUPPLY | 28 | 4 | E | H | F | H | 4 | 4 | 4 | 4 | 8 | B | Initial Estimate based quick judegment (not in AGT) | 4 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_INAM | FLOW METER | 17 | 6 | H | H | G | H | 6 | 6 | 6 | 6 | 4 | B | Initial Estimate based quick judegment (not in AGT) | 7 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_INAP | SAMPLER | 10 | 7 | H02 | H02 | H02 | G04 | 7 | 7 | 7 | 7 | 4 | B | Copied From AGT UMCL Criticality Guide | 7 | H02 | H02 | H02 | G04 | 2 | 2 | 2 | 4 | 4 | B
FA_INDC | LOCAL CONTROLLER | 13 | 6 | H | H | F | H | 6 | 6 | 6 | 6 | 6 | B | Initial Estimate based quick judegment (not in AGT) | 7 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_INDFD | DAMPER | 22 | 8 | E08 | H02 | H02 | G04 | 8 | 8 | 8 | 8 | 8 | A | Copied From AGT UMCL Criticality Guide | 8 | E08 | H02 | H02 | G04 | 8 | 2 | 2 | 4 | 8 | A
FA_INDFS | SOLENOID VALVE | 262 | 6 | H | H | F | H | 6 | 6 | 6 | 6 | 6 | B | Initial Estimate based quick judegment (not in AGT) | 7 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_INDI | INDICATOR | 1673 | 7 | H02 | H02 | H02 | H02 | 7 | 7 | 7 | 7 | 2 | C | Copied From AGT UMCL Criticality Guide | 7 | H02 | H02 | H02 | H02 | 2 | 2 | 2 | 2 | 2 | C
FA_INDMS | SENSING ELEMENT | 1859 | 6 | H | H | F | H | 6 | 6 | 6 | 6 | 6 | B | Initial Estimate based quick judegment (not in AGT) | 7 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_INDMT | TRANSMITTER | 3373 | 5 | H | H | F | H | 5 | 5 | 5 | 5 | 6 | B | Initial Estimate based quick judegment (not in AGT) | 7 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_INDP | PRINTER / RECORDER | 1 | 7 | G04 | G04 | G04 | G04 | 7 | 7 | 7 | 7 | 4 | B | Copied From AGT UMCL Criticality Guide | 7 | G04 | G04 | G04 | G04 | 4 | 4 | 4 | 4 | 4 | B
FA_INDS | INSTRUMENT SWITCH | 1863 | 6 | H | H | F | H | 6 | 6 | 6 | 6 | 6 | B | Initial Estimate based quick judegment (not in AGT) | 7 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_INDT | TRANSDUCER | 33 | 5 | H | H | F | H | 5 | 5 | 5 | 5 | 6 | B | Initial Estimate based quick judegment (not in AGT) | 7 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_INSC | PLC PANEL | 13 | 7 | G04 | H02 | H02 | H02 | 7 | 7 | 7 | 7 | 4 | B | Copied From AGT UMCL Criticality Guide | 7 | G04 | H02 | H02 | H02 | 4 | 2 | 2 | 2 | 4 | B
FA_INSD | DISTRIBUTED CONTROL PANEL | 9 | 7 | G04 | H02 | H02 | H02 | 7 | 7 | 7 | 7 | 4 | B | Copied From AGT UMCL Criticality Guide | 7 | G04 | H02 | H02 | H02 | 4 | 2 | 2 | 2 | 4 | B
FA_INSJ | JUNCTION BOX | 866 | 7 | F06 | G04 | G04 | G04 | 7 | 7 | 7 | 7 | 6 | B | Copied From AGT UMCL Criticality Guide | 7 | F06 | G04 | G04 | G04 | 6 | 4 | 4 | 4 | 6 | B
FA_INSL | LOCAL CONTROL PANEL | 218 | 5 | H | H | F | H | 5 | 5 | 5 | 5 | 6 | B | Initial Estimate based quick judegment (not in AGT) | 7 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_INSS | OPERATOR STATION | 12 | 7 | G04 | H02 | H02 | H02 | 7 | 7 | 7 | 7 | 4 | B | Copied From AGT UMCL Criticality Guide | 7 | G04 | H02 | H02 | H02 | 4 | 2 | 2 | 2 | 4 | B
FA_INST | TERMINATION RACK | 3 | 7 | G04 | H02 | H02 | H02 | 7 | 7 | 7 | 7 | 4 | B | Copied From AGT UMCL Criticality Guide | 7 | G04 | H02 | H02 | H02 | 4 | 2 | 2 | 2 | 4 | B
FA_INSY | SAFETY INSTRUMENT SYSTEM PANEL | 19 | 7 | E08 | H02 | G04 | G04 | 7 | 7 | 7 | 7 | 8 | A | Copied From AGT UMCL Criticality Guide | 7 | E08 | H02 | G04 | G04 | 8 | 2 | 4 | 4 | 8 | A
FA_PEA | SELF-ACTUATING VALVE | 152 | 5 | H02 | H02 | G04 | G04 | 5 | 5 | 5 | 5 | 4 | B | Copied From AGT UMCL Criticality Guide, undefined likelihood set at 5 | 0 | H02 | H02 | G04 | G04 | 2 | 2 | 4 | 4 | 4 | B
FA_PEG | PIPING | 33308 | 4 | E08 | G04 | H02 | F06 | 4 | 4 | 4 | 4 | 8 | A | Copied From AGT UMCL Criticality Guide | 4 | E08 | G04 | H02 | F06 | 8 | 4 | 2 | 6 | 8 | A
FA_PEL | PIG LAUNCHER / RECEIVER | 1 | 4 | H02 | H02 | G04 | F06 | 4 | 4 | 4 | 4 | 6 | B | Copied From AGT UMCL Criticality Guide | 4 | H02 | H02 | G04 | F06 | 2 | 2 | 4 | 6 | 6 | B
FA_PEM | MANIFOLD | 134 | 4 | H02 | H02 | F06 | G04 | 4 | 4 | 4 | 4 | 6 | B | Copied From AGT UMCL Criticality Guide | 4 | H02 | H02 | F06 | G04 | 2 | 2 | 6 | 4 | 6 | B
FA_PEO | RESTRICTIVE ORIFICE | 566 | 4 | H02 | H02 | H02 | H02 | 4 | 4 | 4 | 4 | 2 | C | Copied From AGT UMCL Criticality Guide | 4 | H02 | H02 | H02 | H02 | 2 | 2 | 2 | 2 | 2 | C
FA_PESC | CONVENTIONAL PRESSURE SAFETY VALVE | 697 | 5 | E | F | F | H | 5 | 5 | 5 | 5 | 8 | A | Initial Estimate based quick judegment (not in AGT) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
FA_PESR | RUPTURE DISC | 58 | 5 | E | F | F | H | 5 | 5 | 5 | 5 | 8 | A | Initial Estimate based quick judegment (not in AGT) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
FA_PESV | VACUUM RELIEF PRESSURE SAFETY VALVE | 24 | 5 | E | F | F | H | 5 | 5 | 5 | 5 | 8 | A | Initial Estimate based quick judegment (not in AGT) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
FA_PET | THERMOWELL | 642 | 4 | H02 | H02 | H02 | H02 | 4 | 4 | 4 | 4 | 2 | C | Copied From AGT UMCL Criticality Guide | 4 | H02 | H02 | H02 | H02 | 2 | 2 | 2 | 2 | 2 | C
FA_PEVB | BALL VALVE | 16102 | 5 | G | G | G | H | 5 | 5 | 5 | 5 | 4 | C | Initial Estimate based quick judegment (not in AGT) | 0 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_PEVC | CHECK VALVE | 1822 | 5 | G | G | G | H | 5 | 5 | 5 | 5 | 4 | C | Initial Estimate based quick judegment (not in AGT) | 0 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_PEVD | DIAPHRAGM VALVE | 3 | 5 | G | G | G | H | 5 | 5 | 5 | 5 | 4 | C | Initial Estimate based quick judegment (not in AGT) | 0 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_PEVG | GATE VALVE | 4952 | 5 | G | G | G | H | 5 | 5 | 5 | 5 | 4 | C | Initial Estimate based quick judegment (not in AGT) | 0 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_PEVL | GLOBE VALVE | 1740 | 5 | G | G | G | H | 5 | 5 | 5 | 5 | 4 | C | Initial Estimate based quick judegment (not in AGT) | 0 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_PEVM | MULTIPLE ORIFICE VALVE | 19 | 6 | G | G | G | H | 6 | 6 | 6 | 6 | 4 | B | Initial Estimate based quick judegment (not in AGT) | 0 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_PEVN | NEEDLE VALVE | 254 | 5 | H02 | H02 | H02 | H02 | 5 | 5 | 5 | 5 | 2 | C | Copied From AGT UMCL Criticality Guide, undefined likelihood set at 5 | 0 | H02 | H02 | H02 | H02 | 2 | 2 | 2 | 2 | 2 | C
FA_PEVX | DIVERTER VALVE | 6 | 5 | D09 | F05 | F05 | E07 | 5 | 5 | 5 | 5 | 9 | A | Copied From AGT UMCL Criticality Guide, undefined likelihood set at 5 | 0 | D09 | F05 | F05 | E07 | 9 | 5 | 5 | 7 | 9 | A
FA_PEVY | BUTTERFLY VALVE | 65 | 6 | G | G | G | H | 6 | 6 | 6 | 6 | 4 | B | Initial Estimate based quick judegment (not in AGT) | 0 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_REBC | BLOWER, CENTRIFUGAL | 13 | 7 | D09 | H01 | G03 | G03 | 7 | 7 | 7 | 7 | 9 | A | Copied From AGT UMCL Criticality Guide | 7 | D09 | H01 | G03 | G03 | 9 | 1 | 3 | 3 | 9 | A
FA_REC | CENTRIFUGE | 4 | 7 | G04 | H02 | G04 | G04 | 7 | 7 | 7 | 7 | 4 | B | Copied From AGT UMCL Criticality Guide | 7 | G04 | H02 | G04 | G04 | 4 | 2 | 4 | 4 | 4 | B
FA_REDH | HYDRAULIC MOTOR | 6 | 7 | G | G | G | H | 7 | 7 | 7 | 7 | 4 | B | Initial Estimate based quick judegment (not in AGT) | 7 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_REDP | PNEUMATIC MOTOR | 26 | 7 | G | G | G | H | 7 | 7 | 7 | 7 | 4 | B | Initial Estimate based quick judegment (not in AGT) | 7 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_REEL | LIQUID FUEL COMBUSTION ENGINE | 5 | 7 | D10 | H02 | H02 | F06 | 7 | 7 | 7 | 7 | 10 | A | Copied From AGT UMCL Criticality Guide | 7 | D10 | H02 | H02 | F06 | 10 | 2 | 2 | 6 | 10 | A
FA_REFA | AXIAL FAN | 32 | 7 | G | G | F | F | 7 | 7 | 7 | 7 | 6 | A | Initial Estimate based quick judegment (not in AGT) | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
FA_REFC | CENTRIFUGAL FAN | 162 | 7 | E08 | H02 | G04 | G04 | 7 | 7 | 7 | 7 | 8 | A | Copied From AGT UMCL Criticality Guide | 7 | E08 | H02 | G04 | G04 | 8 | 2 | 4 | 4 | 8 | A
FA_REMC | CENTRIFUGAL COMPRESSOR | 6 | 6 | G | G | E | F | 6 | 6 | 6 | 6 | 8 | A | Initial Estimate based quick judegment (not in AGT) | 7 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_REMR | RECIPROCATING COMPRESSOR | 6 | 6 | G | G | E | F | 6 | 6 | 6 | 6 | 8 | A | Initial Estimate based quick judegment (not in AGT) | 7 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_REMT | ROTARY COMPRESSOR | 11 | 6 | G | G | F | F | 6 | 6 | 6 | 6 | 6 | B | Initial Estimate based quick judegment (not in AGT) | 7 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_RENG | GAS TURBINE | 16 | 7 | F06 | G04 | E08 | F06 | 7 | 7 | 7 | 7 | 8 | A | Copied From AGT UMCL Criticality Guide | 7 | F06 | G04 | E08 | F06 | 6 | 4 | 8 | 6 | 8 | A
FA_REPC | CENTRIFUGAL PUMP | 367 | 7 | H01 | H01 | E07 | G03 | 7 | 7 | 7 | 7 | 7 | B | Copied From AGT UMCL Criticality Guide | 7 | H01 | H01 | E07 | G03 | 1 | 1 | 7 | 3 | 7 | B
FA_REPD | POSITIVE DISPLACEMENT PUMP | 39 | 6 | G | G | F | F | 6 | 6 | 6 | 6 | 6 | B | Initial Estimate based quick judegment (not in AGT) | 7 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_RER | RAKE / SCRAPER | 4 | 6 | G | G | G | G | 6 | 6 | 6 | 6 | 4 | B | Initial Estimate based quick judegment (not in AGT) | 7 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_RETG | GEARBOX | 5 | 6 | H | H | F | H | 6 | 6 | 6 | 6 | 6 | B | Initial Estimate based quick judegment (not in AGT) | 7 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_RETP | COUPLING | 5 | 6 | F | H | F | H | 6 | 6 | 6 | 6 | 6 | B | Initial Estimate based quick judegment (not in AGT) | 7 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_REUC | CHEMICAL INJECTION SYSTEM | 1 | 7 | H02 | H02 | G04 | G04 | 7 | 7 | 7 | 7 | 4 | B | Copied From AGT UMCL Criticality Guide | 7 | H02 | H02 | G04 | G04 | 2 | 2 | 4 | 4 | 4 | B
FA_SEC | CYCLONE | 6 | 5 | H | G | G | G | 5 | 5 | 5 | 5 | 4 | C | Initial Estimate based quick judegment (not in AGT) | 5 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_SEE | EJECTOR / EDUCTOR | 3 | 5 | F | H | F | H | 5 | 5 | 5 | 5 | 6 | B | Initial Estimate based quick judegment (not in AGT) | 7 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_SEFB | BASKET STRAINER FILTER | 323 | 7 | H | H | G | H | 7 | 7 | 7 | 7 | 4 | B | Initial Estimate based quick judegment (not in AGT) | 7 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_SEFE | ELEMENT FILTER | 229 | 7 | H | H | G | H | 7 | 7 | 7 | 7 | 4 | B | Initial Estimate based quick judegment (not in AGT) | 7 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_SEFS | SCREEN FILTER | 39 | 7 | H02 | H02 | H02 | H02 | 7 | 7 | 7 | 7 | 2 | C | Copied From AGT UMCL Criticality Guide | 7 | H02 | H02 | H02 | H02 | 2 | 2 | 2 | 2 | 2 | C
FA_SEHF | FINNED COIL HEAT EXCHANGER | 112 | 5 | H02 | H02 | - | H02 | 5 | 5 | 5 | 5 | 2 | C | Copied From AGT UMCL Criticality Guide | 5 | H02 | H02 | - | H02 | 2 | 2 | - | 2 | 2 | C
FA_SEHS | SPIRAL HEAT EXCHANGER | 48 | 5 | H02 | H02 | - | H02 | 5 | 5 | 5 | 5 | 2 | C | Copied From AGT UMCL Criticality Guide | 5 | H02 | H02 | - | H02 | 2 | 2 | - | 2 | 2 | C
FA_SEHT | SHELL & TUBE HEAT EXCHANGER | 56 | 5 | G04 | H02 | - | G04 | 5 | 5 | 5 | 5 | 4 | B | Copied From AGT UMCL Criticality Guide | 5 | G04 | H02 | - | G04 | 4 | 2 | - | 4 | 4 | B
FA_SEL | FLAME ARRESTOR | 53 | 5 | E08 | H02 | H02 | H02 | 5 | 5 | 5 | 5 | 8 | A | Copied From AGT UMCL Criticality Guide | 5 | E08 | H02 | H02 | H02 | 8 | 2 | 2 | 2 | 8 | A
FA_SEM | FLARE | 5 | 5 | E08 | G04 | E08 | F06 | 5 | 5 | 5 | 5 | 8 | A | Copied From AGT UMCL Criticality Guide | 5 | E08 | G04 | E08 | F06 | 8 | 4 | 8 | 6 | 8 | A
FA_SENF | FIRED HEATER FURNACE | 4 | 5 | H02 | G04 | - | G04 | 5 | 5 | 5 | 5 | 4 | B | Copied From AGT UMCL Criticality Guide | 5 | H02 | G04 | - | G04 | 2 | 4 | - | 4 | 4 | B
FA_SEPA | ACCUMULATOR | 192 | 5 | E08 | H02 | H02 | G04 | 5 | 5 | 5 | 5 | 8 | A | Copied From AGT UMCL Criticality Guide | 5 | E08 | H02 | H02 | G04 | 8 | 2 | 2 | 4 | 8 | A
FA_SEPC | CYLINDER | 63 | 5 | H01 | H01 | H01 | G03 | 5 | 5 | 5 | 5 | 3 | C | Copied From AGT UMCL Criticality Guide | 5 | H01 | H01 | H01 | G03 | 1 | 1 | 1 | 3 | 3 | C
FA_SEPHC | CONDENSER VESSEL | 2 | 5 | H02 | H02 | - | G04 | 5 | 5 | 5 | 5 | 4 | B | Copied From AGT UMCL Criticality Guide | 5 | H02 | H02 | - | G04 | 2 | 2 | - | 4 | 4 | B
FA_SEPHS | SEPARATOR VESSEL | 209 | 5 | H02 | H02 | - | G04 | 5 | 5 | 5 | 5 | 4 | B | Copied From AGT UMCL Criticality Guide | 5 | H02 | H02 | - | G04 | 2 | 2 | - | 4 | 4 | B
FA_SES | PULSATION DAMPENER | 132 | 5 | G04 | H02 | G04 | H02 | 5 | 5 | 5 | 5 | 4 | B | Copied From AGT UMCL Criticality Guide | 5 | G04 | H02 | G04 | H02 | 4 | 2 | 4 | 2 | 4 | B
FA_SETAC | CLOSED ROOF ATMOSPHERIC TANK | 82 | 5 | H02 | H02 | - | G04 | 5 | 5 | 5 | 5 | 4 | B | Copied From AGT UMCL Criticality Guide | 5 | H02 | H02 | - | G04 | 2 | 2 | - | 4 | 4 | B
FA_SETAP | PIT / SUMP | 49 | 5 | H02 | G04 | - | G04 | 5 | 5 | 5 | 5 | 4 | B | Copied From AGT UMCL Criticality Guide | 5 | H02 | G04 | - | G04 | 2 | 4 | - | 4 | 4 | B
FA_SETPC | CYLINDRICAL PRESSURISED TANK | 11 | 5 | D10 | H02 | G04 | F06 | 5 | 5 | 5 | 5 | 10 | A | Copied From AGT UMCL Criticality Guide (Likelihood mnaully corrected due to lookup error) | 0 | D10 | H02 | G04 | F06 | 10 | 2 | 4 | 6 | 10 | A
FA_SEZ | SILENCER / MUFFLER | 64 | 5 | H02 | G04 | H02 | H02 | 5 | 5 | 5 | 5 | 4 | B | Copied From AGT UMCL Criticality Guide | 5 | H02 | G04 | H02 | H02 | 2 | 4 | 2 | 2 | 4 | B
FA_SQFC | EQUIPMENT CABINET | 21 | 4 | E08 | H02 | H02 | H02 | 4 | 4 | 4 | 4 | 8 | A | Copied From AGT UMCL Criticality Guide | 4 | E08 | H02 | H02 | H02 | 8 | 2 | 2 | 2 | 8 | A
FA_SQFDF | FLAME DETECTOR | 485 | 7 | D10 | H02 | H02 | H02 | 7 | 7 | 7 | 7 | 10 | A | Copied From AGT UMCL Criticality Guide | 7 | D10 | H02 | H02 | H02 | 10 | 2 | 2 | 2 | 10 | A
FA_SQFDG | FIXED GAS DETECTOR | 758 | 7 | D10 | H02 | H02 | H02 | 7 | 7 | 7 | 7 | 10 | A | Copied From AGT UMCL Criticality Guide | 7 | D10 | H02 | H02 | H02 | 10 | 2 | 2 | 2 | 10 | A
FA_SQFDS | SMOKE DETECTOR | 145 | 7 | D10 | H02 | H02 | H02 | 7 | 7 | 7 | 7 | 10 | A | Copied From AGT UMCL Criticality Guide | 7 | D10 | H02 | H02 | H02 | 10 | 2 | 2 | 2 | 10 | A
FA_SQFFD | FIREWATER DELUGE SYSTEM | 43 | 7 | D10 | H02 | F06 | F06 | 7 | 7 | 7 | 7 | 10 | A | Copied From AGT UMCL Criticality Guide | 7 | D10 | H02 | F06 | F06 | 10 | 2 | 6 | 6 | 10 | A
FA_SQFFH | FIRE HOSE | 3 | 7 | D10 | H02 | H02 | F06 | 7 | 7 | 7 | 7 | 10 | A | Copied From AGT UMCL Criticality Guide | 7 | D10 | H02 | H02 | F06 | 10 | 2 | 2 | 6 | 10 | A
FA_SQFFM | FIRE WATER/FOAM MONITOR | 23 | 6 | D10 | H02 | H02 | H02 | 6 | 6 | 6 | 6 | 10 | A | Copied From AGT UMCL Criticality Guide | 6 | D10 | H02 | H02 | H02 | 10 | 2 | 2 | 2 | 10 | A
FA_SQFFY | FIRE HYDRANT | 118 | 5 | D10 | H01 | H01 | F05 | 5 | 5 | 5 | 5 | 10 | A | Copied From AGT UMCL Criticality Guide | 5 | D10 | H01 | H01 | F05 | 10 | 1 | 1 | 5 | 10 | A
FA_SQFRA | EMERGENCY ALARM DEVICE | 248 | 7 | D10 | H02 | H02 | H02 | 7 | 7 | 7 | 7 | 10 | A | Copied From AGT UMCL Criticality Guide | 7 | D10 | H02 | H02 | H02 | 10 | 2 | 2 | 2 | 10 | A
FA_SQFRE | SAFETY SHOWER OR EYE BATH | 36 | 5 | E08 | H02 | H02 | H02 | 5 | 5 | 5 | 5 | 8 | A | Copied From AGT UMCL Criticality Guide | 5 | E08 | H02 | H02 | H02 | 8 | 2 | 2 | 2 | 8 | A
FA_SQMT | MAINTENANCE TOOL | 2 | 7 | H02 | H02 | H02 | H02 | 7 | 7 | 7 | 7 | 2 | C | Copied From AGT UMCL Criticality Guide | 7 | H02 | H02 | H02 | H02 | 2 | 2 | 2 | 2 | 2 | C
FA_SQTA | PUBLIC ADDRESS AND ALARM SYSTEM | 87 | 7 | D09 | H01 | H01 | G03 | 7 | 7 | 7 | 7 | 9 | A | Copied From AGT UMCL Criticality Guide | 7 | D09 | H01 | H01 | G03 | 9 | 1 | 1 | 3 | 9 | A
FA_SQTB | NON DIRECTIONAL BEACON | 172 | 7 | D09 | H01 | H01 | G03 | 7 | 7 | 7 | 7 | 9 | A | Copied From AGT UMCL Criticality Guide | 7 | D09 | H01 | H01 | G03 | 9 | 1 | 1 | 3 | 9 | A
FA_SQTE | TELECOMMUNICATION CABINET | 35 | 7 | E07 | H01 | G03 | G03 | 7 | 7 | 7 | 7 | 7 | B | Copied From AGT UMCL Criticality Guide | 7 | E07 | H01 | G03 | G03 | 7 | 1 | 3 | 3 | 7 | B
FA_SQTH | PATCH PANEL | 95 | 7 | E07 | H01 | G03 | G03 | 7 | 7 | 7 | 7 | 7 | B | Copied From AGT UMCL Criticality Guide | 7 | E07 | H01 | G03 | G03 | 7 | 1 | 3 | 3 | 7 | B
FA_SQTL | LOUDSPEAKER | 487 | 7 | D09 | H01 | H01 | G03 | 7 | 7 | 7 | 7 | 9 | A | Copied From AGT UMCL Criticality Guide | 7 | D09 | H01 | H01 | G03 | 9 | 1 | 1 | 3 | 9 | A
FA_SQTN | ANTENNA | 3 | 8 | D09 | H01 | G03 | G03 | 8 | 8 | 8 | 8 | 9 | A | Copied From AGT UMCL Criticality Guide | 8 | D09 | H01 | G03 | G03 | 9 | 1 | 3 | 3 | 9 | A
FA_SQTOF | FIXED RADIO | 6 | 7 | D09 | H01 | G03 | G03 | 7 | 7 | 7 | 7 | 9 | A | Copied From AGT UMCL Criticality Guide | 7 | D09 | H01 | G03 | G03 | 9 | 1 | 3 | 3 | 9 | A
FA_SQTP | COMPUTER PERIPHERAL | 108 | 7 | H01 | H01 | H01 | H01 | 7 | 7 | 7 | 7 | 1 | C | Copied From AGT UMCL Criticality Guide | 7 | H01 | H01 | H01 | H01 | 1 | 1 | 1 | 1 | 1 | C
FA_SQTS | TELEPHONE OR MULTIMEDIA EQUIPMENT | 122 | 7 | D09 | H01 | G03 | G03 | 7 | 7 | 7 | 7 | 9 | A | Copied From AGT UMCL Criticality Guide | 7 | D09 | H01 | G03 | G03 | 9 | 1 | 3 | 3 | 9 | A
FA_SQTV | CCTV CAMERA UNIT | 167 | 7 | D09 | G03 | G03 | G03 | 7 | 7 | 7 | 7 | 9 | A | Copied From AGT UMCL Criticality Guide | 7 | D09 | G03 | G03 | G03 | 9 | 3 | 3 | 3 | 9 | A
FA_SQTW | WIRELESS COMMUNICATION OR CONTROL EQUIPMENT | 39 | 7 | E | H | G | H | 7 | 7 | 7 | 7 | 8 | A | Initial Estimate based quick judegment (not in AGT) | 7 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_SQTY | RECEIVER / TRANSMITTER | 4 | 8 | E07 | H01 | G03 | G03 | 8 | 8 | 8 | 8 | 7 | B | Copied From AGT UMCL Criticality Guide | 8 | E07 | H01 | G03 | G03 | 7 | 1 | 3 | 3 | 7 | B
FA_SYLH | SYSTEM LEVEL HIERARCHY | 627 | 7 | E | E | E | E | 7 | 7 | 7 | 7 | 8 | A | Initial Estimate based quick judegment (not in AGT) | 0 | - | - | - | - | - | - | - | - | 0 | #N/A
FA_WECO | OVERHEAD CRANE | 13 | 7 | H02 | H02 | G04 | F06 | 7 | 7 | 7 | 7 | 6 | B | Copied From AGT UMCL Criticality Guide | 7 | H02 | H02 | G04 | F06 | 2 | 2 | 4 | 6 | 6 | B
FA_WEHY | CONVEYOR | 4 | 6 | H02 | H02 | H02 | G04 | 6 | 6 | 6 | 6 | 4 | B | Copied From AGT UMCL Criticality Guide | 6 | H02 | H02 | H02 | G04 | 2 | 2 | 2 | 4 | 4 | B
Note on AB2: Author: copy/paste of FA_CFBC to check formula first row
Note on G3: Financial
Note on H3: Non-Financial
Note on K3: Financial
Note on L3: Non-Financial
Note on U3: Financial
Note on V3: Non-Financial
Note on Y3: Financial
Note on Z3: Non-Financial

## MAHBarrierSetup
|  |  |  | For Process Systems |  |  |  |  | For Utility systems
This is not a live query, be careful if overwriting as may lose table alignment | [11 empty] | Same as Process
[7 empty] | Add text this column | Use this column to select MAH barrier component for failure code |  |  |  | Differs
FailureCode | Description | Number found in ASSET-C WND | MAH_Family_ID | MAH_Barrier_Family | MAH_Barrier_Component | Typ_Criticality | Comment | MAH_Selector | MAH_Family_ID_U | MAH_Barrier_Family_U | MAH_Barrier_Component_U | Typ_Criticality_U | Comments_U | MAH_Selector_U
FA_CFBC | CONTROL ROOM | 4 | M3 | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | GES only allows for high criticality control rooms. Monthlycomfort check & 4yrly inspection | M3 ¦ Personnel Address (PA) System ¦ Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_CFBE | ELECTRICAL SUBSTATION | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_CFBI | INSTRUMENT HOUSE | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_CFBL | LIVING ACCOMMODATION | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_CFBO | OFFICE BUILDING | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_CFDL | LAGOON | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_CFDO | OUTFALL | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_CFSGA | ACCESS CONTROL GATE | #REF! | #N/A | #N/A | #N/A | #N/A | None allocated |  | #N/A | #N/A | #N/A | #N/A
FA_CFSGB | BRIDGE | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_CFSGC | CONTAINMENT | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_CFSGP | PARKING LOT | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_CFSGR | ROAD | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_CFSGS | STORAGE YARD | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_CFSGT | WASTE STORAGE | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_CFSGW | WALL OR FENCE | 5 | P2 | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | None allocated, initially, treated as secondary structures | P2 ¦ Structural Integrity ¦ Secondary Structures - Single component failure results in hydrocarbon LOPC | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_CFSPD | FIRE DOOR | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_CFSPW | FIRE / BLAST WALL | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_CFSSA | ANCHOR | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_CFSSD | DERRICK OR FRAME | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_CFSSE | EQUIPMENT SUPPORT STRUCTURE | 104 | P2 | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | For supports for LOPC systems if fails | P2 ¦ Structural Integrity ¦ Secondary Structures - Single component failure results in hydrocarbon LOPC | P4 | Process Containment Integrity | All other supports, paint and bolting | C | Non hazardous system supports, unknown systems | P4 ¦ Process Containment Integrity ¦ All other supports, paint and bolting
FA_CFSSF | STRUCTURAL FOUNDATION | 19 | P2 | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | For supports for LOPC systems if fails | P2 ¦ Structural Integrity ¦ Secondary Structures - Single component failure results in hydrocarbon LOPC | P2 | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | Support for non-hazardous system, unknown systems | P2 ¦ Structural Integrity ¦ Secondary Structures - Single component failure has no immediate consequence
FA_CFSSI | PILE | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_CFSSP | PEDESTAL | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_CFSSS | STABILISATION OR GUIDANCE EQUIPMENT | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_CFSST | STRUCTURAL BASE | 907 | P2 | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | For supports for LOPC systems if fails | P2 ¦ Structural Integrity ¦ Secondary Structures - Single component failure results in hydrocarbon LOPC | P2 | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | Support for non-hazardous system, unknown systems | P2 ¦ Structural Integrity ¦ Secondary Structures - Single component failure has no immediate consequence
FA_EECF | LIGHT FITTING | 398 | M3 | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | Emergency lighting, Ex non-emergency lighting | M3 ¦ Emergency Lighting ¦ Emergency Lighting - supplied from Emergency Generator Switchboard | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_EECH | ELECTRIC HEATER | 109 | P4.5 | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | For Process heaters | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | P4 | Process Containment Integrity | All other pressure Equipment and pipework | C | system 64 | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_EECMD | DC ELECTRIC MOTOR | 7 | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | Motors for emergency systems | M7 ¦ Fire protection ¦ Firewater pumps (main and jockey), drivers, their controls and control panels | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_EECMI | AC INDUCTION ELECTRIC MOTOR | 466 | M4 | Ignition Prevention | For Equipment in Zone 2 | B | Zone 2 assumed by default | M4 ¦ Ignition Prevention ¦ For Equipment in Zone 2 | M4 | Ignition Prevention | For Equipment in Zone 2 | B | Non-priority induction motors | M4 ¦ Ignition Prevention ¦ For Equipment in Zone 2
FA_EECMS | AC SYNCHRONOUS ELECTRIC MOTOR | 1 | M4 | Ignition Prevention | For Equipment in Zone 2 | B | Flare Tip Davit Winch Motor | M4 ¦ Ignition Prevention ¦ For Equipment in Zone 2 | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_EECO | ELECTRIC SOCKET OUTLET | 21 | M4 | Ignition Prevention | For Equipment in Zone 2 | B | Zone 2 assumed by default | M4 ¦ Ignition Prevention ¦ For Equipment in Zone 2 | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_EECT | TRACE HEATING CIRCUIT | 2 | M4 | Ignition Prevention | For Equipment in Zone 2 | B | Zone 2 assumed by default | M4 ¦ Ignition Prevention ¦ For Equipment in Zone 2 | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_EEHC | AIR CONDITIONING UNIT | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_EEHH | AIR HANDLING UNIT | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_EEHV | CONSTANT VOLUME UNIT | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_EEPA | SURGE ARRESTOR | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A |  | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable
FA_EEPBA | AIR CIRCUIT BREAKER | 868 | M4 | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | Emergency circuits | M4 ¦ Ignition Prevention ¦ Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_EEPBG | GAS CIRCUIT BREAKER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A |  | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable
FA_EEPBL | LIQUID CIRCUIT BREAKER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_EEPBV | VACUUM CIRCUIT BREAKER | 48 | M4 | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | Assumed part of emergency curcuit until reviewed otherwise | M4 ¦ Ignition Prevention ¦ Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_EEPCI | IMPRESSED CURRENT CATHODE | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A |  | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable
FA_EEPCS | SACRIFICIAL ANODE | 109 | P4.5 | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 6 valid tags all corrosion coupons on process lines, GES only allows for high priority on 4 yrly inspections | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_EEPE | ELECTRICAL DISCONNECT SWITCH | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A |  | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable
FA_EEPNE | EARTHING BAR | 118 | P6 | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | Criticality makes no difference to GES task scheduling, promote LoPs | P6 ¦ Control systems - non LoPs, LOPA initiating causes ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI sc | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_EEPNN | NEUTRAL GROUND RESISTOR | 8 | P6 | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | Same maintenance schedule all criticalities | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_EEPP | PROTECTIVE RELAY | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A |  | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable
FA_EEPS | START / STOP SWITCH | 221 | P6 | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | None allocated, tested each time you use it, so fix on fail in practice? | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable | P6 | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | system 59,65 are utility. Same maintenance schedule all criticalities | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable
FA_EEPU | UNINTERRUPTIBLE POWER SUPPLY | 29 | M3 | Emergency Power | UPS Systems | A | De-escalate for non-critical units | M3 ¦ Emergency Power ¦ UPS Systems | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_EETA | REACTOR / INDUCTOR | 6 | P6 | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | None allocated, no VALID tags yet | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_EETB | BATTERY | 39 | P6 | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | Escalate by system / location | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_EETC | BATTERY CHARGER | 57 | P6 | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | Escalate by system / location | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_EETD | BUS DUCT / BUS BAR | 70 | P6 | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | None allocated | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_EETFD | DRY TRANSFORMER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_EETFE | ENCAPSULATED TRANSFORMER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_EETFW | WET TRANSFORMER | 20 | M4 | Ignition Prevention | For Equipment in Zone 2 | B | De-escalate outside Hazardous zones | M4 ¦ Ignition Prevention ¦ For Equipment in Zone 2 | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_EETGA | AC ELECTRIC GENERATOR | 10 | M3 | Emergency Power | Emergency Generator | A | De-escalate non-emergency generators | M3 ¦ Emergency Power ¦ Emergency Generator | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_EETGD | DC ELECTRIC GENERATOR | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_EETH | ELECTRICAL SLIP RING | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_EETI | ELECTRIC ISOLATOR | 25 | M4 | Ignition Prevention | For Equipment in Zone 2 | B | None allocated | M4 ¦ Ignition Prevention ¦ For Equipment in Zone 2 | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_EETL | SOLAR PANEL | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_EETM | MOTOR CONTROL CENTER | 910 | P6 | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | None allocated, escalate for any emergency systems | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_EETO | POWER / CONTROL MODULE | 5 | #N/A | #N/A | #N/A | #N/A | None allocated, escalate for any emergency systems |  | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_EETP | ELECTRICAL PANEL | 3 | #N/A | #N/A | #N/A | #N/A | None allocated, escalate for any emergency systems |  | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_EETQ | VARIABLE FREQUENCY DRIVE | 64 | #N/A | #N/A | #N/A | #N/A | None allocated, escalate for any emergency systems |  | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_EETR | POWER RECTIFIER | 15 | #N/A | #N/A | #N/A | #N/A | None allocated, escalate for any emergency systems |  | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_EETS | ELECTRICAL TRANSFER SWITCH | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_EETT | ELECTRICAL CAPACITOR | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_EETV | POWER INVERTER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_EETW | SWITCHGEAR | 170 | #N/A | #N/A | #N/A | #N/A | None allocated, escalate for any emergency systems |  | P6 | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | system 94 tags are utility | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable
FA_EETY | POWER SUPPLY | 28 | #N/A | #N/A | #N/A | #N/A | None allocated, All multi-cable transits |  | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_INAA | GAS ANALYSER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_INAC | GAS CHROMATOGRAPH | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_INAF | FLOW COMPUTER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_INAL | LIQUID CHROMATOGRAPH | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_INAM | FLOW METER | 17 | #N/A | #N/A | #N/A | #N/A | None allocated, escalate for SIS |  | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_INAP | SAMPLER | 10 | #N/A | #N/A | #N/A | #N/A | None allocated - High usage item? Condition likely to be trigger |  | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_INAS | LIQUID ANALYSER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_INDC | LOCAL CONTROLLER | 9 | P6 | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B |  | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_INDFA | ACTUATOR | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_INDFD | DAMPER | 20 | P4 | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | Treat as executive element in F&G protection, all on generatr / em-gen packages | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Fire & Gas System | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_INDFS | SOLENOID VALVE | 230 | P6 | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | Escalate by system / SIS | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable | P6 | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | systems 63,64,65 | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable
FA_INDI | INDICATOR | 1479 | #N/A | #N/A | #N/A | #N/A | None allocated, Fix on fail, escalate any SIS |  | #N/A | #N/A | #N/A | #N/A | Escalate SIS, otherwise no MAH allocated
FA_INDMS | SENSING ELEMENT | 1691 | P6 | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | Escalate if SIL requires, demote if system requires | P6 ¦ Control systems - non LoPs, LOPA initiating causes ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI sc | P6 | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B |  | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable
FA_INDMT | TRANSMITTER | 2715 | P6 | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | Escalate if SIL requires, demote if system requires | P6 ¦ Control systems - non LoPs, LOPA initiating causes ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI sc | P6 | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B |  | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable
FA_INDP | PRINTER / RECORDER | #REF! | P8 | Alarms & operator response | Instruments associated with non-Safety Related Alarms - transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | B | De-escalate if valid and not alarm response related | P8 ¦ Alarms & operator response ¦ Instruments associated with non-Safety Related Alarms - transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distributio | P8 | Alarms & operator response | Instruments associated with non-Safety Related Alarms - transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | B
FA_INDS | INSTRUMENT SWITCH | 1553 | P6 | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | Escalate if SIL requires, demote if system requires | P6 ¦ Control systems - non LoPs, LOPA initiating causes ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI sc | P6 | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B |  | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable
FA_INDT | TRANSDUCER | 33 | P6 | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | Mostly machinery protection sensors | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable | P6 | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B |  | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable
FA_INSC | PLC PANEL | 13 | P6 | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | Escalate if SIL requires, demote if system requires | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_INSD | DISTRIBUTED CONTROL PANEL | 9 | P6 | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | Escalate for emergency systems | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_INSJ | JUNCTION BOX | 866 | P6 | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | Escalate where SIS or in SIL | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable | P6 | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B |  | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable
FA_INSL | LOCAL CONTROL PANEL | 218 | P6 | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | Escalate where SIS or in SIL | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable | P4 | Process Containment Integrity | All other pressure Equipment and pipework | C |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_INSM | METEOROLOGICAL SYSTEM PANEL | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_INSP | CONDITION MONITORING SYSTEM PANEL | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_INSS | OPERATOR STATION | 8 | P6 | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | Assumed to be replace on fail / non-BPCS devices | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_INST | TERMINATION RACK | 3 | P6 | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | Assumed to be replace on fail / non-BPCS devices | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_INSY | SAFETY INSTRUMENT SYSTEM PANEL | 19 | P6 | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | Assume SIL rated will get escalated | P6 ¦ Control systems - non LoPs, LOPA initiating causes ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI sc | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_PEA | SELF-ACTUATING VALVE | 133 | P6 | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | Mostly PCVs, some process, some utility, some package. De-escalate by System / Package. Arguably some will also be Process containment equipment for gas =>A criticality | P6 ¦ Control systems - non LoPs, LOPA initiating causes ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI sc | P4 | Process Containment Integrity | All other pressure Equipment and pipework | C |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_PEB | BUOYANCY DEVICE | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_PEC | DUCT | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_PED | DIVERTER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_PEE | EXPANSION DEVICE | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_PEG | PIPING | 12600 | P4.5 | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | demote by system | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | P4 | Process Containment Integrity | All other pressure Equipment and pipework | C |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_PEH | BUNKERING HOSE | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_PEI | BUCKLE INITIATOR | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_PEL | PIG LAUNCHER / RECEIVER | 1 | P4.5 | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | Assumed as high criticality item | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_PEM | MANIFOLD | 134 | P4 | Process Containment Integrity | All other pressure Equipment and pipework | C | All utility (air, oil) service by default | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | P4 | Process Containment Integrity | All other pressure Equipment and pipework | C | sys 63 - instrument air manifold | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_PEN | METER PROVER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_PEO | RESTRICTIVE ORIFICE | 482 | P5 | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | Demote by System, package (line?) | P5 ¦ Overpressure Protection ¦ ROs (or FOs) that restrict gas flow to flare | P5 | Overpressure Protection | ROs in pump recirculation lines | B |  | P5 ¦ Overpressure Protection ¦ ROs in pump recirculation lines
FA_PEP | BLOWOUT PREVENTER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_PEQ | TURRET EQUIPMENT | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_PER | RISER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_PESC | CONVENTIONAL PRESSURE SAFETY VALVE | 550 | P5 | Overpressure Protection | All other PSVs | B | Escalate by system | P5 ¦ Overpressure Protection ¦ All other PSVs | P5 | Overpressure Protection | All other PSVs | B |  | P5 ¦ Overpressure Protection ¦ All other PSVs
FA_PESP | PILOT OPERATED PRESSURE SAFETY VALVE | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_PESR | RUPTURE DISC | 49 | P5 | Overpressure Protection | Other bursting disks | B | Escalate by system, package | P5 ¦ Overpressure Protection ¦ Other bursting disks | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_PESV | VACUUM RELIEF PRESSURE SAFETY VALVE | 15 | P5 | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | Escalate by system, package if hazardous | P5 ¦ Overpressure Protection ¦ Other Vacuum breakers not covered by the descriptions above. | P4 | Process Containment Integrity | All other pressure Equipment and pipework | C | system 64 | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_PET | THERMOWELL | 548 | P6 | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | GES give 5 yrly inspection, demote by system if required | P6 ¦ Control systems - non LoPs, LOPA initiating causes ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI sc | P6 | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B |  | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable
FA_PEU | UMBILICAL | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A |  | M3 ¦ Personnel Address (PA) System ¦ Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights
FA_PEVB | BALL VALVE | 9510 | P4.5 | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | Escalate by system, package if required | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | P4 | Process Containment Integrity | All other pressure Equipment and pipework | C |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_PEVC | CHECK VALVE | 1564 | P5 | Overpressure Protection | All other NRVs | C | Escalate by system, package, consequence | P5 ¦ Overpressure Protection ¦ All other NRVs | P5 | Overpressure Protection | All other NRVs | C |  | P5 ¦ Overpressure Protection ¦ All other NRVs
FA_PEVD | DIAPHRAGM VALVE | 3 | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 3 valves on firepump starter systems, GES gives annual inspect, test, overhaul 6 yrly | M7 ¦ Fire protection ¦ Firewater pumps (main and jockey), drivers, their controls and control panels | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_PEVG | GATE VALVE | 2589 | P4.5 | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | Demote by system, if required | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | P4 | Process Containment Integrity | All other pressure Equipment and pipework | C |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_PEVH | SHEAR VALVE | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A |  | M3 ¦ Facility radio system ¦ Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers
FA_PEVL | GLOBE VALVE | 969 | P4.5 | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | Demote by system, if required | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | P4 | Process Containment Integrity | All other pressure Equipment and pipework | C |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_PEVM | MULTIPLE ORIFICE VALVE | 9 | P4.5 | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | Demote by system, if required | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_PEVN | NEEDLE VALVE | 79 | P4.5 | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | Demote by system, if required | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | P4 | Process Containment Integrity | All other pressure Equipment and pipework | C | system 64 | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_PEVS | SUBSURFACE SAFETY VALVE | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_PEVX | DIVERTER VALVE | 4 | P4.5 | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | Demote by system, if required | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_PEVY | BUTTERFLY VALVE | 65 | P4.5 | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | Demote by system, if required | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | P4 | Process Containment Integrity | All other pressure Equipment and pipework | C | sys 63,34,35 | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_PEW | SWIVEL | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_PEX | X-MAS TREE / WELLHEAD | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_PEZ | TUBING HANGER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_REBC | BLOWER, CENTRIFUGAL | 4 | P4 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | Escalate by system if required( flare blowers most likely) | P4 ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | P4 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | sys 82 | P4 ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below)
FA_REBR | ROTARY LOBE BLOWER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_REC | CENTRIFUGE | 4 | P4 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | MEG system may override? | P4 ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_REDH | HYDRAULIC MOTOR | 6 | P4 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | Fire pump starters, should get maintained whe parent serviced? | P4 ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_REDP | PNEUMATIC MOTOR | 26 | P4 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | Utility / starter motors (inc EmGen black start?) should be checked as part of parent servicing? | P4 ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_REDT | TOP DRIVE | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_REEG | GAS FUEL COMBUSTION ENGINE | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_REEL | LIQUID FUEL COMBUSTION ENGINE | 4 | P4 | Diesel Driven Packages | Diesel Engine | B | Firepumps and EmGens | P4 ¦ Diesel Driven Packages ¦ Diesel Engine | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_REFA | AXIAL FAN | 24 | #N/A | #N/A | #N/A | #N/A | None allocated, assume fan criticality is mainly non-safety role, except enclosure ventilation which should be caught by package? |  | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_REFC | CENTRIFUGAL FAN | 131 | #N/A | #N/A | #N/A | #N/A | None allocated, assume fan criticality is mainly non-safety role, except enclosure ventilation which should be caught by package / Fire and gas?? |  | #N/A | #N/A | #N/A | #N/A | sys 65
FA_REI | MIXER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_REMA | AXIAL COMPRESSOR | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_REMC | CENTRIFUGAL COMPRESSOR | 3 | P4.5 | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | Main gas compressors, but air / em-gen start / nitrogen compressors caught by this rule | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | #N/A | #N/A | #N/A | #N/A | no valid tags in utility systems
FA_REMR | RECIPROCATING COMPRESSOR | 6 | P4.5 | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | Flash gas compressors, so treat a gas containing equipment. | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_REMT | ROTARY COMPRESSOR | 11 | P4 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | Air compressors | P4 ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | P4 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | air compressors, sys 65 | P4 ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below)
FA_RENG | GAS TURBINE | 10 | P4 | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | Driver of package, driven equipment could be different criticality | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Gas Generator | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_RENS | STEAM TURBINE | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_REPB | BEAM PUMP | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_REPC | CENTRIFUGAL PUMP | 275 | P4 | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | Based on process pumps, but catches a lot of package equipment, UMCL only distinguishes 4 hydraulic pumps | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ All Shaft Seals | P4 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B |  | P4 ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below)
FA_REPD | POSITIVE DISPLACEMENT PUMP | 39 | P4 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | Mostly HPU / hydraulic starter pumps | P4 ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_REPG | PROGRESSIVE CAVITY PUMP | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_REPR | RECIPROCATING PUMP | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_REPV | CONTROLLED VOLUME PUMP | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_RER | RAKE / SCRAPER | 2 | #N/A | #N/A | #N/A | #N/A | Oil skimmers, none allocated |  | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_RES | SOOTBLOWER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_RETC | CLUTCH | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_RETG | GEARBOX | 5 | #N/A | #N/A | #N/A | #N/A | None in MEL (yet), only breather system for gearbox had this code (corrected) |  | #N/A | #N/A | #N/A | #N/A | no tags in MEL
FA_RETH | HYDRAULIC / TORQUE CONVERTER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_RETP | COUPLING | 5 | P4 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | couplings only identified on air compressors, redundancy and loss of function not MAH? | P4 ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | P4 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | sys 65 only - no tags in process systems | P4 ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below)
FA_RETV | CONTINOUSLY VARIABLE TRANSMISSION | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_REUC | CHEMICAL INJECTION SYSTEM | 1 | P4 | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | Review detail of what this is | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ All Shaft Seals | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_REUH | HYDRAULIC SYSTEM | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_REXA | AXIAL TURBO EXPANDER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_REXC | CENTRIFUGAL TURBO EXPANDER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_REZ | ROTARY DRUM FILTER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SEA | AIR DRYER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SEBF | FIRETUBE BOILER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SEBH | WASTE HEAT BOILER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SEBW | WATERTUBE BOILER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SEC | CYCLONE | 6 | #N/A | #N/A | #N/A | #N/A | Vortex coolers to air compressor panels, no MAH role |  | #N/A | #N/A | #N/A | #N/A | sys 65 only - no tags in process systems
FA_SED | DRAIN POT | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SEE | EJECTOR / EDUCTOR | 3 | P4.5 | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | Mixers for MEG storage tanks. | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_SEFB | BASKET STRAINER FILTER | 310 | P4.5 | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | Escalate by sytem if required | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | P4 | Process Containment Integrity | All other pressure Equipment and pipework | C | sys 53,65 utilities | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_SEFC | COALESCER FILTER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SEFE | ELEMENT FILTER | 194 | #N/A | #N/A | #N/A | #N/A | Generally for equipment reliability, rather than MAH, None allocated |  | #N/A | #N/A | #N/A | #N/A | Generally for equipment reliability, rather than MAH, None allocated - sys 63,64,65;
FA_SEFM | MEDIA FILTER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SEFP | ELECTROSTATIC PRECIPITATOR FILTER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SEFR | REVERSE OSMOSIS FILTER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SEFS | SCREEN FILTER | 18 | #N/A | #N/A | #N/A | #N/A | Generally for equipment reliability, rather than MAH, None allocated |  | #N/A | #N/A | #N/A | #N/A | Generally for equipment reliability, rather than MAH, None allocated - sys 64
FA_SEHC | CALORIFIER HEAT EXCHANGER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SEHF | FINNED COIL HEAT EXCHANGER | 70 | P4.5 | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | Mix of process and equipment coolers, modify for system | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | P4 | Process Containment Integrity | All other pressure Equipment and pipework | C | sys 63,65 | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_SEHP | PLATE & FRAME HEAT EXCHANGER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SEHR | RECUPERATOR HEAT EXCHANGER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SEHS | SPIRAL HEAT EXCHANGER | 48 | P4.5 | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | Mix from seal plan coolers ro process | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_SEHT | SHELL & TUBE HEAT EXCHANGER | 51 | P4.5 | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | Mixed duty, may need to modify based on system | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_SEI | BIN / HOPPER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SEL | FLAME ARRESTOR | 53 | M4 | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | May be able to downgrade if not in hazardous zone, argument is if its not zone 2 why have a flame arrestor? Hazardous zone schedule may help with parent tags for pieces of equipment | M4 ¦ Ignition Prevention ¦ For Equipment in Zone 0 and Zone 1 | M4 | Ignition Prevention | For Equipment in Zone 2 | B | system 58 | M4 ¦ Ignition Prevention ¦ For Equipment in Zone 2
FA_SEM | FLARE | 5 | P5 | Blowdown vent and flare | Flare tips | A | Flare tips defined as A, flare stack assumed to be A as P4-C support to crit A pressure systems | P5 ¦ Blowdown vent and flare ¦ Flare tips | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_SENF | FIRED HEATER FURNACE | 4 | M4 | Ignition Prevention | For Equipment in Zone 2 | B | Assuming hot surface potential, but otherwise might not be classified as MAH | M4 ¦ Ignition Prevention ¦ For Equipment in Zone 2 | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_SENI | INCINERATOR FURNACE | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SENT | THERMAL OXIDIZER FURNACE | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SEPA | ACCUMULATOR | 192 | P4 | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | Assume generally high pressure containment | P4 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_SEPC | CYLINDER | 59 | P4.5 | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | Primarily sample cylinders, so gas containing | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | P4 | Process Containment Integrity | All other pressure Equipment and pipework | C | sys 64 | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_SEPHC | CONDENSER VESSEL | 2 | P4.5 | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | demote for non-process | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_SEPHS | SEPARATOR VESSEL | 190 | P4.5 | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | Compressor suction seps to air dryer vessels in compressors, so demote for non-process | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | P4 | Process Containment Integrity | All other pressure Equipment and pipework | C | sys 53,64,65 | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_SEPHV | VAPORISER VESSEL | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SEPRL | FLUIDISED BED REACTOR | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SEPRR | REGENERATOR REACTOR | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SEPRX | FIXED BED REACTOR | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SEPVA | ABSORBER COLUMN | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SEPVC | CONTACTOR COLUMN | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SEPVS | SCRUBBER COLUMN | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SEPVT | STRIPPER COLUMN | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SER | STATIC MIXER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SES | PULSATION DAMPENER | 72 | P4.5 | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | Mainly chemical with some process, demote for non-process | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_SETAC | CLOSED ROOF ATMOSPHERIC TANK | 60 | P4 | Oil Storage & Offloading | Hydrocarbon Tanks | A | Fuel, MEG, Condensate, lube oil, reservoirs included, demote if non-hazardous? | P4 ¦ Oil Storage & Offloading ¦ Hydrocarbon Tanks | #N/A | #N/A | #N/A | #N/A | sys 53,63; no MAH barrier for non-HC tank
FA_SETAF | FLOATING ROOF ATMOSPHERIC TANK | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SETAO | OPEN ROOF ATMOSPHERIC TANK | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SETAP | PIT / SUMP | 40 | P2 | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | Air comp oil sump to sewage pits | P2 ¦ Structural Integrity ¦ Tertiary Structures - Failure may result in fall 1 - 3m | P2 | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | sys 58,59,65,82 | P2 ¦ Structural Integrity ¦ Tertiary Structures - Failure may result in fall 1 - 3m
FA_SETAR | RESERVOIR | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SETPC | CYLINDRICAL PRESSURISED TANK | 11 | P4 | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | Air receiver, water, air, seal oil, N2 tanks. Assume high pressure system until reviewed at detail level. | P4 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_SETPS | SPHERICAL PRESSURISED TANK | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SEV | LOUVRE | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SEY | HYDRAULIC HATCH | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SEZ | SILENCER / MUFFLER | 64 | P4 | Process Containment Integrity | All other pressure Equipment and pipework | C | Exhaust / vent systems (some intakes),loss of function has level F or below impact | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | P4 | Process Containment Integrity | All other pressure Equipment and pipework | C | sys 63,64,65 | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_SQFC | EQUIPMENT CABINET | 21 | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | Fire hydrant cabinets set with this code, could escalate for 'primary' fire fighting systems | M7 ¦ Fire protection ¦ Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_SQFDD | DUST DETECTOR | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQFDF | FLAME DETECTOR | 420 | M6 | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | Gonna be an A… | M6 ¦ Fire & Gas systems ¦ Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_SQFDG | FIXED GAS DETECTOR | 739 | M6 | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | Gonna be an A… | M6 ¦ Fire & Gas systems ¦ Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_SQFDH | PERSONAL H2S MONITOR | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQFDM | MOTION DETECTOR | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQFDP | PORTABLE GAS MONITOR | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQFDR | PERSONAL RADIATION MONITOR | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQFDS | SMOKE DETECTOR | 140 | M6 | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | Gonna be an A… | M6 ¦ Fire & Gas systems ¦ Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_SQFFD | FIREWATER DELUGE SYSTEM | 26 | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | Code Applied to gas turbine deluge nozzles, othe deluge skids. Treat as primary fire fighting system | M7 ¦ Fire protection ¦ Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_SQFFE | FIRE EXTINGUISHER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQFFF | FIRE FIGHTING FOAM SYSTEM | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQFFH | FIRE HOSE | 3 | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | Fire hydrant cabinets set with this code, could escalate for 'primary' fire fighting systems | M7 ¦ Fire protection ¦ Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_SQFFM | FIRE WATER/FOAM MONITOR | 23 | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | Fire hydrant cabinets set with this code, could escalate for 'primary' fire fighting systems | M7 ¦ Fire protection ¦ Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_SQFFS | FIRE EXTINGUISHING SYSTEM | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQFFT | FIRE TRUCK | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQFFY | FIRE HYDRANT | 118 | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | Treat as supplementary until told otherwise | M7 ¦ Fire protection ¦ Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_SQFRA | EMERGENCY ALARM DEVICE | 244 | M3 | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | Mostly Manual alarm call points | M3 ¦ Alarm Annunciation System: ¦ External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | M3 | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | system 82 utility | M3 ¦ Alarm Annunciation System: ¦ External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers
FA_SQFRB | BREATHING AIR BOTTLE | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQFRC | DESCENT DEVICE | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQFRD | AUTOMATED EXTERNAL DEFIBRILLATOR | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQFRE | SAFETY SHOWER OR EYE BATH | 20 | P4 | Process Containment Integrity | All other pressure Equipment and pipework | C | Not MAH lifesaving equipment? | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | P4 | Process Containment Integrity | All other pressure Equipment and pipework | C | system 53 only - no process system tags | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_SQFRJ | LIFEJACKET | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQFRK | PERSONNEL BASKET | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQFRL | LIFEBOAT AND DAVIT | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQFRP | SELF-CONTAINED BREATHING APPARATUS | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQFRR | LIFERAFT | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQFRS | BREATHING AIR SYSTEM | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQFRT | RESCUE BOAT | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQFRV | SURVIVAL SUIT | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQFRY | LIFEBUOY | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQL | LABORATORY EQUIPMENT | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQMC | PORTABLE COMPRESSOR | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQMD | TESTING DEVICE | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQMG | PORTABLE GENERATOR | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQML | PORTABLE LIGHT PLANT | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQMT | MAINTENANCE TOOL | 2 | P4 | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | Barring devices for flash gas compressors | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Auxiliaries like (cleaning system, control system, utilities) | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_SQMW | WELDING MACHINE | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQNB | SIGNAL BUOY | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQNL | NAVIGATION LIGHT | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQNP | POSITIONING EQUIPMENT | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQR | OIL SPILL RESPONSE EQUIPMENT | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQTA | PUBLIC ADDRESS AND ALARM SYSTEM | 60 | M3 | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | Includes some un-validated MAC points. | M3 ¦ Personnel Address (PA) System ¦ Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_SQTB | NON DIRECTIONAL BEACON | 169 | M3 | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | Alarm / status signals | M3 ¦ Personnel Address (PA) System ¦ Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_SQTC | COMPASS | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQTD | RADAR | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQTE | TELECOMMUNICATION CABINET | 33 | M3 | Telecommunications | Class A Telecommunication UPS & Shut down | A | Treating all cabinets as class A | M3 ¦ Telecommunications ¦ Class A Telecommunication UPS & Shut down | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_SQTF | FACSIMILE MACHINE | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQTH | PATCH PANEL | 95 | P6 | Digital security | Fire walls Remote access servers Architecture Staging servers for Anti-virus and OS patches | A | Unvalidated fibre optic panels. Picked digital security, but could be Telecoms. No difference in GES between High and Medium criticality | P6 ¦ Digital security ¦ Fire walls Remote access servers Architecture Staging servers for Anti-virus and OS patches | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_SQTI | INTERCOM SYSTEM | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQTL | LOUDSPEAKER | 487 | M3 | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | PAGA loudspeakers, outdoor and in | M3 ¦ Personnel Address (PA) System ¦ Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_SQTM | AMPLIFIER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQTN | ANTENNA | 3 | M3 | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A |  | M3 ¦ Facility radio system ¦ Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_SQTOF | FIXED RADIO | 6 | M3 | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A |  | M3 ¦ Facility radio system ¦ Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_SQTOP | PAGER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQTOR | PORTABLE RADIO | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQTP | COMPUTER PERIPHERAL | 104 | #N/A | #N/A | #N/A | #N/A | all NOTAGS, RJ45 network sockets - none allocated |  | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_SQTR | PROXIMITY READER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQTS | TELEPHONE OR MULTIMEDIA EQUIPMENT | 101 | M3 | Facility Emergency Telephone & Hot line systems | Call control - PABX/IPT Ex telephones Designated emergency phones (Control rooms muster points etc.) Interconnecting cable plant and networks | A | Includes outdoor EX call points as well as control room IP phone, so will want to downrate non-EX phones | M3 ¦ Facility Emergency Telephone & Hot line systems ¦ Call control - PABX/IPT Ex telephones Designated emergency phones (Control rooms muster points etc.) Interconnecting cable plant and networks | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_SQTT | SATELLITE EQUIPMENT | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQTV | CCTV CAMERA UNIT | 167 | #N/A | #N/A | #N/A | #N/A | None allocated - not explicitly listed in MAH table, Ex equipment to be escalated |  | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_SQTW | WIRELESS COMMUNICATION OR CONTROL EQUIPMENT | 17 | #N/A | #N/A | #N/A | #N/A | NOTAGged personnel badge readers, described as access control, not electronic muster system so None allocated |  | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_SQTX | MULTIPLEXER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQTY | RECEIVER / TRANSMITTER | 4 | M6 | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | NOTTAGged gas detectors | M6 ¦ Fire & Gas systems ¦ Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_SQUC | CLEANING EQUIPMENT | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQUE | EXERCISE EQUIPMENT | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SQUG | GALLEY EQUIPMENT | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SRFRN | VENTILATOR | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_SYLH | SYSTEM LEVEL HIERARCHY | 316 | #N/A | #N/A | #N/A | #N/A | None allocated - Assumed non-physically meaningful or pending proper classification |  | #N/A | #N/A | #N/A | #N/A | Not equipment tags, no criticality assignment required
FA_WECM | MOBILE CRANE | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WECO | OVERHEAD CRANE | 11 | P4 | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | Maintenance equipment on RE packages | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Auxiliaries like (cleaning system, control system, utilities) | M5 | Cranes | Maintenance Equipment | C | system 65 gantry crane | M5 ¦ Cranes ¦ Maintenance Equipment
FA_WECP | PEDESTAL CRANE | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WECT | TOWER CRANE | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WED | LOADING ARM | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WEHC | CUTTING DRILL | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WEHR | CRUSHER / SHREDDER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WEHS | SHAKER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WEHY | CONVEYOR | 2 | #N/A | #N/A | #N/A | #N/A | None allocatedSalt discharge screw conveyors, no MAH role identified |  | #N/A | #N/A | #N/A | #N/A | no tags in utility systems
FA_WELB | CHAIN BLOCK | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WELC | CABLE OR CHAIN | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WELD | DAVIT | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WELE | ELEVATOR | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WELF | FORKLIFT | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WELG | SLING | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WELH | HOIST | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WELJ | JACK | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WELM | MAN LIFT / BASKET / CHERRY PICKER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WELN | CONTAINER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WELP | SPREADER FRAME / BAR | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WELS | SHEAVE OR PULLEY | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WELT | MONORAIL / TROLLEY | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WELW | WINCH | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WESR | REMOTE OPERATED VEHICLE (ROV) | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WEST | RUNNING TOOL | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WETRA | AUTOMOBILE | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WETRC | ROAD COMPACTOR | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WETRL | LAWNMOWER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WETRO | TRACTOR | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WETRR | TRAILER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WETRS | ROAD SCRAPER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WETRT | TRUCK | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WETRW | ROAD SWEEPER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WETWB | BARGE | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WETWF | MARINE FENDER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WETWT | MARINE THRUSTER | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A
FA_WETWV | MARINE VESSEL | #REF! | #N/A | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A | #N/A

## MAHBarrierSetup (pass 2)
|  |  | For Process Systems |  |  |  |  | For Utility systems
This is not a live query, be careful if overwriting as may lose table alignment | [9 empty] | Same as Process
[6 empty] | Add text this column | Use this column to select MAH barrier component for failure code |  |  | Differs
FailureCode | Description | Number found in ASSET-C WND | MAH_Barrier_Family | MAH_Barrier_Component | Typ_Criticality | Comment | MAH_Selector | MAH_Barrier_Family_U | MAH_Barrier_Component_U | Typ_Criticality_U | Comments_U | MAH_Selector_U
FA_CFBC | CONTROL ROOM | 4 | #N/A | #N/A | #N/A | GES only allows for high criticality control rooms. Monthlycomfort check & 4yrly inspection | M3-A ¦ Personnel Address (PA) System ¦ Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | #N/A | #N/A | #N/A | GES only allows for high criticality control rooms. Monthlycomfort check & 4yrly inspection | M3-A ¦ Personnel Address (PA) System ¦ Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights
FA_CFBE | ELECTRICAL SUBSTATION | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P2-A/B ¦ Structural Integrity ¦ Secondary Structures - Single component failure has no immediate consequence
FA_CFBI | INSTRUMENT HOUSE | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P2-A/B ¦ Structural Integrity ¦ Secondary Structures - Single component failure has no immediate consequence
FA_CFBL | LIVING ACCOMMODATION | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P2-A/B ¦ Structural Integrity ¦ Secondary Structures - Single component failure has no immediate consequence
FA_CFBO | OFFICE BUILDING | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P2-A/B ¦ Structural Integrity ¦ Secondary Structures - Single component failure has no immediate consequence
FA_CFDL | LAGOON | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | M3-D ¦ Emergency Lighting ¦ Emergency Lighting - supplied from Emergency Generator Switchboard
FA_CFDO | OUTFALL | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P4-C ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C
FA_CFSGA | ACCESS CONTROL GATE | #REF! | #N/A | #N/A | #N/A | None allocated |  | #N/A | #N/A | #N/A |  | M4-A ¦ Ignition Prevention ¦ For Equipment in Zone 2
FA_CFSGB | BRIDGE | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | M4-A ¦ Ignition Prevention ¦ For Equipment in Zone 2
FA_CFSGC | CONTAINMENT | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | M4-A ¦ Ignition Prevention ¦ For Equipment in Zone 0 and Zone 1
FA_CFSGP | PARKING LOT | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | M4-A ¦ Ignition Prevention ¦ For Equipment in Zone 2
FA_CFSGR | ROAD | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | M4-A ¦ Ignition Prevention ¦ For Equipment in Zone 2
FA_CFSGS | STORAGE YARD | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | M4-A ¦ Ignition Prevention ¦ Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc).
FA_CFSGT | WASTE STORAGE | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | M4-A ¦ Ignition Prevention ¦ Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc).
FA_CFSGW | WALL OR FENCE | 5 | #N/A | #N/A | #N/A | None allocated, initially, treated as secondary structures | P2-A/B ¦ Structural Integrity ¦ Secondary Structures - Single component failure results in hydrocarbon LOPC | #N/A | #N/A | #N/A |  | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_CFSPD | FIRE DOOR | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab
FA_CFSPW | FIRE / BLAST WALL | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab
FA_CFSSA | ANCHOR | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_CFSSD | DERRICK OR FRAME | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | M3-C ¦ Emergency Power ¦ UPS Systems
FA_CFSSE | EQUIPMENT SUPPORT STRUCTURE | 104 | #N/A | #N/A | #N/A | For supports for LOPC systems if fails | P2-A/B ¦ Structural Integrity ¦ Secondary Structures - Single component failure results in hydrocarbon LOPC | #N/A | #N/A | #N/A | Non hazardous system supports | P4-C ¦ Process Containment Integrity ¦ All other supports, paint and bolting
FA_CFSSF | STRUCTURAL FOUNDATION | 19 | #N/A | #N/A | #N/A | For supports for LOPC systems if fails | P2-A/B ¦ Structural Integrity ¦ Secondary Structures - Single component failure results in hydrocarbon LOPC | #N/A | #N/A | #N/A | Support for non-hazardous system | P2-A/B ¦ Structural Integrity ¦ Secondary Structures - Single component failure has no immediate consequence
FA_CFSSI | PILE | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab
FA_CFSSP | PEDESTAL | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_CFSSS | STABILISATION OR GUIDANCE EQUIPMENT | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | M4-A ¦ Ignition Prevention ¦ For Equipment in Zone 2
FA_CFSST | STRUCTURAL BASE | 907 | #N/A | #N/A | #N/A | For supports for LOPC systems if fails | P2-A/B ¦ Structural Integrity ¦ Secondary Structures - Single component failure results in hydrocarbon LOPC | #N/A | #N/A | #N/A | Support for non-hazardous system | P2-A/B ¦ Structural Integrity ¦ Secondary Structures - Single component failure has no immediate consequence
FA_EECF | LIGHT FITTING | 398 | #N/A | #N/A | #N/A | Emergency lighting, Ex non-emergency lighting | M3-D ¦ Emergency Lighting ¦ Emergency Lighting - supplied from Emergency Generator Switchboard | #N/A | #N/A | #N/A | For non-Emergency lighting | P4-C ¦ Process Containment Integrity ¦ All other supports, paint and bolting
FA_EECH | ELECTRIC HEATER | 109 | #N/A | #N/A | #N/A | For Process heaters | P4-C ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | #N/A | #N/A | #N/A | Heaters not in process systems | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_EECMD | DC ELECTRIC MOTOR | 7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | Motors for emergency systems | M7 ¦ Fire protection ¦ Firewater pumps (main and jockey), drivers, their controls and control panels | #N/A | #N/A | #N/A | Non-emergency motors | M4-A ¦ Ignition Prevention ¦ For Equipment in Zone 2
FA_EECMI | AC INDUCTION ELECTRIC MOTOR | 466 | #N/A | #N/A | #N/A | Assumed to be zone 2 until indicated otherwise | M4-A ¦ Ignition Prevention ¦ For Equipment in Zone 2 | #N/A | #N/A | #N/A | Non-priority induction motors | P4-C ¦ Process Containment Integrity ¦ All other supports, paint and bolting
FA_EECMS | AC SYNCHRONOUS ELECTRIC MOTOR | 1 | #N/A | #N/A | #N/A | Flare Tip Davit Winch Motor | M4-A ¦ Ignition Prevention ¦ For Equipment in Zone 0 and Zone 1 | #N/A | #N/A | #N/A | Single motor on Flare Tip Davit winch | M4-A ¦ Ignition Prevention ¦ For Equipment in Zone 0 and Zone 1
FA_EECO | ELECTRIC SOCKET OUTLET | 21 | #N/A | #N/A | #N/A | Zone 2 assumed by default | M4-A ¦ Ignition Prevention ¦ For Equipment in Zone 2 | #N/A | #N/A | #N/A | Non-ex sockets | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab
FA_EECT | TRACE HEATING CIRCUIT | 2 | #N/A | #N/A | #N/A | Zone 2 assumed by default | M4-A ¦ Ignition Prevention ¦ For Equipment in Zone 2 | #N/A | #N/A | #N/A | Low criticality trace heating | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab
FA_EEHC | AIR CONDITIONING UNIT | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_EEHH | AIR HANDLING UNIT | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_EEHV | CONSTANT VOLUME UNIT | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_EEPA | SURGE ARRESTOR | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab
FA_EEPBA | AIR CIRCUIT BREAKER | 868 | #N/A | #N/A | #N/A | Emergency circuits | M4-A ¦ Ignition Prevention ¦ Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | #N/A | #N/A | #N/A | Utility breakers | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab
FA_EEPBG | GAS CIRCUIT BREAKER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab
FA_EEPBL | LIQUID CIRCUIT BREAKER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_EEPBV | VACUUM CIRCUIT BREAKER | 48 | #N/A | #N/A | #N/A | Assumed part of emergency curcuit until reviewed otherwise | M4-A ¦ Ignition Prevention ¦ Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | #N/A | #N/A | #N/A | Utility breakers | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab
FA_EEPCI | IMPRESSED CURRENT CATHODE | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab
FA_EEPCS | SACRIFICIAL ANODE | 109 | #N/A | #N/A | #N/A | 6 valid tags all corrosion coupons on process lines, GES only allows for high priority on 4 yrly inspections | P4-C ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | #N/A | #N/A | #N/A | Only high priority in GES | P4-C ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C
FA_EEPE | ELECTRICAL DISCONNECT SWITCH | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab
FA_EEPNE | EARTHING BAR | 118 | #N/A | #N/A | #N/A | Criticality makes no difference to GES task scehduling | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab | #N/A | #N/A | #N/A | Criticality makes no difference to GES task scehduling | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab
FA_EEPNN | NEUTRAL GROUND RESISTOR | 8 | #N/A | #N/A | #N/A | Same maintenance schedule all criticalities | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab | #N/A | #N/A | #N/A | Same maintenance schedule all criticalities | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab
FA_EEPP | PROTECTIVE RELAY | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab
FA_EEPS | START / STOP SWITCH | 221 | #N/A | #N/A | #N/A | None allocated, tested each time you use it, so fix on fail in practice? | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab | #N/A | #N/A | #N/A | Same maintenance schedule all criticalities | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab
FA_EEPU | UNINTERRUPTIBLE POWER SUPPLY | 29 | #N/A | #N/A | #N/A | De-escalate for non-critical units | M3-C ¦ Emergency Power ¦ UPS Systems | #N/A | #N/A | #N/A | For utility systems | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab
FA_EETA | REACTOR / INDUCTOR | 6 | #N/A | #N/A | #N/A | None allocated, no VALID tags yet | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab | #N/A | #N/A | #N/A | For Utility systems | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab
FA_EETB | BATTERY | 39 | #N/A | #N/A | #N/A | Escalate by system / location | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab | #N/A | #N/A | #N/A |  | P6-A ¦ Control systems - non LoPs, LOPA initiating causes ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI
FA_EETC | BATTERY CHARGER | 57 | #N/A | #N/A | #N/A | Escalate by system / location | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab | #N/A | #N/A | #N/A |  | P6-A ¦ Control systems - non LoPs, LOPA initiating causes ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI
FA_EETD | BUS DUCT / BUS BAR | 70 | #N/A | #N/A | #N/A | None allocated | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab | #N/A | #N/A | #N/A |  | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_EETFD | DRY TRANSFORMER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P4-C ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C
FA_EETFE | ENCAPSULATED TRANSFORMER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_EETFW | WET TRANSFORMER | 20 | #N/A | #N/A | #N/A | De-escalate outside Hazardous zones | M4-A ¦ Ignition Prevention ¦ For Equipment in Zone 2 | #N/A | #N/A | #N/A |  | P5-A ¦ Overpressure Protection ¦ ROs (or FOs) that restrict gas flow to flare
FA_EETGA | AC ELECTRIC GENERATOR | 10 | #N/A | #N/A | #N/A | De-escalate non-emergency generators | M3-C ¦ Emergency Power ¦ Emergency Generator | #N/A | #N/A | #N/A |  | P5-A ¦ Overpressure Protection ¦ All other PSVs
FA_EETGD | DC ELECTRIC GENERATOR | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P5-A ¦ Overpressure Protection ¦ Other bursting disks
FA_EETH | ELECTRICAL SLIP RING | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P5-A ¦ Overpressure Protection ¦ Other Vacuum breakers not covered by the descriptions above.
FA_EETI | ELECTRIC ISOLATOR | 25 | #N/A | #N/A | #N/A | None allocated |  | #N/A | #N/A | #N/A |  | P4-C ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C
FA_EETL | SOLAR PANEL | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_EETM | MOTOR CONTROL CENTER | 910 | #N/A | #N/A | #N/A | None allocated, escalate for any emergency systems |  | #N/A | #N/A | #N/A |  | P5-A ¦ Overpressure Protection ¦ All other NRVs
FA_EETO | POWER / CONTROL MODULE | 5 | #N/A | #N/A | #N/A | None allocated, escalate for any emergency systems |  | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A |  | M7 ¦ Fire protection ¦ Firewater pumps (main and jockey), drivers, their controls and control panels
FA_EETP | ELECTRICAL PANEL | 3 | #N/A | #N/A | #N/A | None allocated, escalate for any emergency systems |  | #N/A | #N/A | #N/A |  | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_EETQ | VARIABLE FREQUENCY DRIVE | 64 | #N/A | #N/A | #N/A | None allocated, escalate for any emergency systems |  | #N/A | #N/A | #N/A |  | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_EETR | POWER RECTIFIER | 15 | #N/A | #N/A | #N/A | None allocated, escalate for any emergency systems |  | #N/A | #N/A | #N/A |  | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_EETS | ELECTRICAL TRANSFER SWITCH | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_EETT | ELECTRICAL CAPACITOR | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_EETV | POWER INVERTER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_EETW | SWITCHGEAR | 170 | #N/A | #N/A | #N/A | None allocated, escalate for any emergency systems |  | #N/A | #N/A | #N/A |  | P4-D ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below)
FA_EETY | POWER SUPPLY | 28 | #N/A | #N/A | #N/A | None allocated, All multi-cable transits |  | #N/A | #N/A | #N/A |  | P4-D ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below)
FA_INAA | GAS ANALYSER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P4-D ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below)
FA_INAC | GAS CHROMATOGRAPH | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P4-D ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below)
FA_INAF | FLOW COMPUTER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P4-D ¦ Diesel Driven Packages ¦ Diesel Engine
FA_INAL | LIQUID CHROMATOGRAPH | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_INAM | FLOW METER | 17 | #N/A | #N/A | #N/A | None allocated, escalate for SIS |  | #N/A | #N/A | #N/A
FA_INAP | SAMPLER | 10 | #N/A | #N/A | #N/A | None allocated - High usage item? Condition likely to be trigger |  | #N/A | #N/A | #N/A |  | P4-D ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below)
FA_INAS | LIQUID ANALYSER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P4-C ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C
FA_INDC | LOCAL CONTROLLER | 9 | #N/A | #N/A | #N/A |  | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab | #N/A | #N/A | #N/A |  | P4-D ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below)
FA_INDFA | ACTUATOR | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P4-D ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Gas Generator
FA_INDFD | DAMPER | 20 | #N/A | #N/A | #N/A | Treat as executive element in F&G protection, all on generatr / em-gen packages | P4-D ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Fire & Gas System | #N/A | #N/A | #N/A |  | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_INDFS | SOLENOID VALVE | 230 | #N/A | #N/A | #N/A | Escalate by system / SIS | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab | #N/A | #N/A | #N/A |  | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_INDI | INDICATOR | 1479 | #N/A | #N/A | #N/A | None allocated, Fix on fail, escalate any SIS |  | #N/A | #N/A | #N/A
FA_INDMS | SENSING ELEMENT | 1691 | #N/A | #N/A | #N/A | Escalate if system / SIL requires | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab | #N/A | #N/A | #N/A
FA_INDMT | TRANSMITTER | 2715 | #N/A | #N/A | #N/A | Escalate if system / SIL requires | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab | #N/A | #N/A | #N/A |  | P4-D ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below)
FA_INDP | PRINTER / RECORDER | #REF! | #N/A | #N/A | #N/A | De-escalate if valid and not alarm response related | P8 ¦ Alarms & operator response ¦ Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | #N/A | #N/A | #N/A |  | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_INDS | INSTRUMENT SWITCH | 1553 | #N/A | #N/A | #N/A | Escalate if system / SIL requires | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab | #N/A | #N/A | #N/A
FA_INDT | TRANSDUCER | 33 | #N/A | #N/A | #N/A | Mostly machinery protection sensors | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab | #N/A | #N/A | #N/A |  | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_INSC | PLC PANEL | 13 | #N/A | #N/A | #N/A | Escalate if system / SIL requires | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab | #N/A | #N/A | #N/A |  | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_INSD | DISTRIBUTED CONTROL PANEL | 9 | #N/A | #N/A | #N/A | Escalate for emergency systems | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab | #N/A | #N/A | #N/A
FA_INSJ | JUNCTION BOX | 866 | #N/A | #N/A | #N/A | Escalate where SIS or in SIL | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab | #N/A | #N/A | #N/A
FA_INSL | LOCAL CONTROL PANEL | 218 | #N/A | #N/A | #N/A | Escalate where SIS or in SIL | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab | #N/A | #N/A | #N/A |  | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_INSM | METEOROLOGICAL SYSTEM PANEL | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_INSP | CONDITION MONITORING SYSTEM PANEL | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_INSS | OPERATOR STATION | 8 | #N/A | #N/A | #N/A | Assumed to be replace on fail / non-BPCS devices | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab | #N/A | #N/A | #N/A |  | M4-A ¦ Ignition Prevention ¦ For Equipment in Zone 2
FA_INST | TERMINATION RACK | 3 | #N/A | #N/A | #N/A | Assumed to be replace on fail / non-BPCS devices | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab | #N/A | #N/A | #N/A |  | P5-B ¦ Blowdown vent and flare ¦ Flare tips
FA_INSY | SAFETY INSTRUMENT SYSTEM PANEL | 19 | #N/A | #N/A | #N/A | Assume SIL rated will get escalated | P6-A ¦ Control systems - non LoPs, LOPA initiating causes ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI | #N/A | #N/A | #N/A |  | M4-A ¦ Ignition Prevention ¦ For Equipment in Zone 2
FA_PEA | SELF-ACTUATING VALVE | 133 | #N/A | #N/A | #N/A | Mostly PCVs, some process, some utility, some package. De-escalate by System / Package. Arguably some will also be Process containment equipment for gas =>A criticality | P6-A ¦ Control systems - non LoPs, LOPA initiating causes ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI | #N/A | #N/A | #N/A |  | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_PEB | BUOYANCY DEVICE | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_PEC | DUCT | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_PED | DIVERTER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_PEE | EXPANSION DEVICE | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P4-C ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C
FA_PEG | PIPING | 12600 | #N/A | #N/A | #N/A | Escalate by system | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | #N/A | #N/A | #N/A |  | P4-E ¦ Oil Storage & Offloading ¦ Hydrocarbon Tanks
FA_PEH | BUNKERING HOSE | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P2-A/B ¦ Structural Integrity ¦ Tertiary Structures - Failure may result in fall 1 - 3m
FA_PEI | BUCKLE INITIATOR | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P4-C ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300
FA_PEL | PIG LAUNCHER / RECEIVER | 1 | #N/A | #N/A | #N/A | Assumed as high criticality item | P4-C ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | #N/A | #N/A | #N/A |  | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_PEM | MANIFOLD | 134 | #N/A | #N/A | #N/A | All utility (air, oil) service by default | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B |  | M7 ¦ Fire protection ¦ Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system)
FA_PEN | METER PROVER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | M6-A ¦ Fire & Gas systems ¦ Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel
FA_PEO | RESTRICTIVE ORIFICE | 482 | #N/A | #N/A | #N/A | Demote by System, package (line?) | P5-A ¦ Overpressure Protection ¦ ROs (or FOs) that restrict gas flow to flare | #N/A | #N/A | #N/A |  | M6-A ¦ Fire & Gas systems ¦ Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel
FA_PEP | BLOWOUT PREVENTER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | M6-A ¦ Fire & Gas systems ¦ Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel
FA_PEQ | TURRET EQUIPMENT | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | M7 ¦ Fire protection ¦ Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system)
FA_PER | RISER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | M7 ¦ Fire protection ¦ Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system)
FA_PESC | CONVENTIONAL PRESSURE SAFETY VALVE | 550 | #N/A | #N/A | #N/A | Escalate by system | P5-A ¦ Overpressure Protection ¦ All other PSVs | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B |  | M7 ¦ Fire protection ¦ Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system)
FA_PESP | PILOT OPERATED PRESSURE SAFETY VALVE | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | M7 ¦ Fire protection ¦ Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system)
FA_PESR | RUPTURE DISC | 49 | #N/A | #N/A | #N/A | Escalate by system, package | P5-A ¦ Overpressure Protection ¦ Other bursting disks | #N/A | #N/A | #N/A |  | M6-A ¦ Fire & Gas systems ¦ Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel
FA_PESV | VACUUM RELIEF PRESSURE SAFETY VALVE | 15 | #N/A | #N/A | #N/A | Escalate by system, package if hazardous | P5-A ¦ Overpressure Protection ¦ Other Vacuum breakers not covered by the descriptions above. | #N/A | #N/A | #N/A |  | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_PET | THERMOWELL | 548 | #N/A | #N/A | #N/A | GES give 5 yrly inspection, demote by system if required | P4-C ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | #N/A | #N/A | #N/A |  | P4-D ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Auxiliaries like (cleaning system, control system, utilities)
FA_PEU | UMBILICAL | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | M3-A ¦ Personnel Address (PA) System ¦ Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights
FA_PEVB | BALL VALVE | 9510 | #N/A | #N/A | #N/A | Escalate by system, package if required | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | #N/A | #N/A | #N/A |  | M3-A ¦ Personnel Address (PA) System ¦ Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights
FA_PEVC | CHECK VALVE | 1564 | #N/A | #N/A | #N/A | Escalate by system, package, consequence | P5-A ¦ Overpressure Protection ¦ All other NRVs | #N/A | #N/A | #N/A |  | M3-B ¦ Telecommunications ¦ Class A Telecommunication UPS & Shut down
FA_PEVD | DIAPHRAGM VALVE | 3 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 3 valves on firepump starter systems, GES gives annual inspect, test, overhaul 6 yrly | M7 ¦ Fire protection ¦ Firewater pumps (main and jockey), drivers, their controls and control panels | #N/A | #N/A | #N/A |  | P6-A ¦ Digital security ¦ Fire walls
FA_PEVG | GATE VALVE | 2589 | #N/A | #N/A | #N/A | Escalate by sytem, | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | #N/A | #N/A | #N/A |  | M3-A ¦ Personnel Address (PA) System ¦ Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights
FA_PEVH | SHEAR VALVE | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | M3-B ¦ Facility radio system ¦ Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers
FA_PEVL | GLOBE VALVE | 969 | #N/A | #N/A | #N/A | Escalate by sytem, | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | #N/A | #N/A | #N/A |  | M3-B ¦ Facility radio system ¦ Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers
FA_PEVM | MULTIPLE ORIFICE VALVE | 9 | #N/A | #N/A | #N/A | Escalate by sytem, | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | #N/A | #N/A | #N/A
FA_PEVN | NEEDLE VALVE | 79 | #N/A | #N/A | #N/A | Escalate by sytem, if required | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | #N/A | #N/A | #N/A |  | M3-B ¦ Facility Emergency Telephone & Hot line systems ¦ Call control - PABX/IPT Ex telephones Designated emergency phones (Control rooms muster points etc.) Interconnecting cable plant and networks
FA_PEVS | SUBSURFACE SAFETY VALVE | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_PEVX | DIVERTER VALVE | 4 | #N/A | #N/A | #N/A | Escalate by sytem, if required | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | #N/A | #N/A | #N/A
FA_PEVY | BUTTERFLY VALVE | 65 | #N/A | #N/A | #N/A | Escalate by sytem, if required | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | #N/A | #N/A | #N/A |  | M6-A ¦ Fire & Gas systems ¦ Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel
FA_PEW | SWIVEL | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_PEX | X-MAS TREE / WELLHEAD | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A |  | P4-D ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Auxiliaries like (cleaning system, control system, utilities)
FA_PEZ | TUBING HANGER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_REBC | BLOWER, CENTRIFUGAL | 4 | #N/A | #N/A | #N/A | Escalate by system if required( flare blowers most likely) | P4-D ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | #N/A | #N/A | #N/A
FA_REBR | ROTARY LOBE BLOWER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_REC | CENTRIFUGE | 4 | #N/A | #N/A | #N/A | MEG system may override? | P4-D ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | #N/A | #N/A | #N/A
FA_REDH | HYDRAULIC MOTOR | 6 | #N/A | #N/A | #N/A | Fire pump starters, should get maintained whe parent serviced? | P4-D ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | #N/A | #N/A | #N/A
FA_REDP | PNEUMATIC MOTOR | 26 | #N/A | #N/A | #N/A | Utility / starter motors (inc EmGen black start?) should be checked as part of parent servicing? | P4-D ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | #N/A | #N/A | #N/A
FA_REDT | TOP DRIVE | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_REEG | GAS FUEL COMBUSTION ENGINE | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_REEL | LIQUID FUEL COMBUSTION ENGINE | 4 | #N/A | #N/A | #N/A | Firepumps and EmGens | P4-D ¦ Diesel Driven Packages ¦ Diesel Engine | #N/A | #N/A | #N/A
FA_REFA | AXIAL FAN | 24 | #N/A | #N/A | #N/A | None allocated, assume fan criticality is mainly non-safety role, except enclosure ventilation which should be caught by package? |  | #N/A | #N/A | #N/A
FA_REFC | CENTRIFUGAL FAN | 131 | #N/A | #N/A | #N/A | None allocated, assume fan criticality is mainly non-safety role, except enclosure ventilation which should be caught by package / Fire and gas?? |  | #N/A | #N/A | #N/A
FA_REI | MIXER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_REMA | AXIAL COMPRESSOR | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_REMC | CENTRIFUGAL COMPRESSOR | 3 | #N/A | #N/A | #N/A | Gas compressors may get modified by system (ROCE .AND. HC containing type rule), otherwise em-gen starter compressor | P4-D ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | #N/A | #N/A | #N/A
FA_REMR | RECIPROCATING COMPRESSOR | 6 | #N/A | #N/A | #N/A | Flash gas compressors, so treat a gas containing equipment. | P4-C ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | #N/A | #N/A | #N/A
FA_REMT | ROTARY COMPRESSOR | 11 | #N/A | #N/A | #N/A | Air compressors | P4-D ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | #N/A | #N/A | #N/A
FA_RENG | GAS TURBINE | 10 | #N/A | #N/A | #N/A | Driver of package, driven equipment could be different criticality | P4-D ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Gas Generator | #N/A | #N/A | #N/A
FA_RENS | STEAM TURBINE | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_REPB | BEAM PUMP | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_REPC | CENTRIFUGAL PUMP | 275 | #N/A | #N/A | #N/A | Override for hazardous systems by system id | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | #N/A | #N/A | #N/A
FA_REPD | POSITIVE DISPLACEMENT PUMP | 39 | #N/A | #N/A | #N/A | Override for hazardous systems by system id? | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | #N/A | #N/A | #N/A
FA_REPG | PROGRESSIVE CAVITY PUMP | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_REPR | RECIPROCATING PUMP | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_REPV | CONTROLLED VOLUME PUMP | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_RER | RAKE / SCRAPER | 2 | #N/A | #N/A | #N/A | Oil skimmers, none allocated |  | #N/A | #N/A | #N/A
FA_RES | SOOTBLOWER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_RETC | CLUTCH | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_RETG | GEARBOX | 5 | #N/A | #N/A | #N/A | None in MEL (yet), only breather system for gearbox had this code (corrected) |  | #N/A | #N/A | #N/A
FA_RETH | HYDRAULIC / TORQUE CONVERTER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_RETP | COUPLING | 5 | #N/A | #N/A | #N/A | couplings only identified on air compressors, redundancy and loss of function not MAH? | P4-D ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | #N/A | #N/A | #N/A
FA_RETV | CONTINOUSLY VARIABLE TRANSMISSION | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_REUC | CHEMICAL INJECTION SYSTEM | 1 | #N/A | #N/A | #N/A | Review detail of what this is | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | #N/A | #N/A | #N/A
FA_REUH | HYDRAULIC SYSTEM | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_REXA | AXIAL TURBO EXPANDER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_REXC | CENTRIFUGAL TURBO EXPANDER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_REZ | ROTARY DRUM FILTER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SEA | AIR DRYER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SEBF | FIRETUBE BOILER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SEBH | WASTE HEAT BOILER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SEBW | WATERTUBE BOILER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SEC | CYCLONE | 6 | #N/A | #N/A | #N/A | Vortex coolers to air compressor panels, no MAH role |  | #N/A | #N/A | #N/A
FA_SED | DRAIN POT | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SEE | EJECTOR / EDUCTOR | 3 | #N/A | #N/A | #N/A | Mixers for MEG storage tanks. | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | #N/A | #N/A | #N/A
FA_SEFB | BASKET STRAINER FILTER | 310 | #N/A | #N/A | #N/A | Escalate by sytem if required | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | #N/A | #N/A | #N/A
FA_SEFC | COALESCER FILTER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SEFE | ELEMENT FILTER | 194 | #N/A | #N/A | #N/A | Generally for equipment reliability, rather than MAH, None allocated |  | #N/A | #N/A | #N/A
FA_SEFM | MEDIA FILTER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SEFP | ELECTROSTATIC PRECIPITATOR FILTER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SEFR | REVERSE OSMOSIS FILTER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SEFS | SCREEN FILTER | 18 | #N/A | #N/A | #N/A | Generally for equipment reliability, rather than MAH, None allocated |  | #N/A | #N/A | #N/A
FA_SEHC | CALORIFIER HEAT EXCHANGER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SEHF | FINNED COIL HEAT EXCHANGER | 70 | #N/A | #N/A | #N/A | Mix of process and equipment coolers, modify for system | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | #N/A | #N/A | #N/A
FA_SEHP | PLATE & FRAME HEAT EXCHANGER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SEHR | RECUPERATOR HEAT EXCHANGER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SEHS | SPIRAL HEAT EXCHANGER | 48 | #N/A | #N/A | #N/A | Mix from seal plan coolers ro process | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | #N/A | #N/A | #N/A
FA_SEHT | SHELL & TUBE HEAT EXCHANGER | 51 | #N/A | #N/A | #N/A | Mixed duty, may need to escalate based on system | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | #N/A | #N/A | #N/A
FA_SEI | BIN / HOPPER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SEL | FLAME ARRESTOR | 53 | #N/A | #N/A | #N/A | May be able to downgrade if not in hazardous zone, argument is if its not zone 2 why have a flame arrestor? Hazardous zone schedule may help with parent tags for pieces of equipment | M4-A ¦ Ignition Prevention ¦ For Equipment in Zone 2 | #N/A | #N/A | #N/A
FA_SEM | FLARE | 5 | #N/A | #N/A | #N/A | Flare tips defined as A, flare stack assumed to be A as P4-C support to crit A pressure systems | P5-B ¦ Blowdown vent and flare ¦ Flare tips | #N/A | #N/A | #N/A
FA_SENF | FIRED HEATER FURNACE | 4 | #N/A | #N/A | #N/A | Assuming hot surface potential, but otherwise might not be classified as MAH | M4-A ¦ Ignition Prevention ¦ For Equipment in Zone 2 | #N/A | #N/A | #N/A
FA_SENI | INCINERATOR FURNACE | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SENT | THERMAL OXIDIZER FURNACE | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SEPA | ACCUMULATOR | 192 | #N/A | #N/A | #N/A | Escalate for hazardous fluids | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | #N/A | #N/A | #N/A
FA_SEPC | CYLINDER | 59 | #N/A | #N/A | #N/A | Escalate for hazardous fluids? | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | #N/A | #N/A | #N/A
FA_SEPHC | CONDENSER VESSEL | 2 | #N/A | #N/A | #N/A | Escalate for hazardous fluids? | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | #N/A | #N/A | #N/A
FA_SEPHS | SEPARATOR VESSEL | 190 | #N/A | #N/A | #N/A | Compressor suction seps to air dryer vessels in compressors, so escalate by system | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | #N/A | #N/A | #N/A
FA_SEPHV | VAPORISER VESSEL | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SEPRL | FLUIDISED BED REACTOR | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SEPRR | REGENERATOR REACTOR | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SEPRX | FIXED BED REACTOR | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SEPVA | ABSORBER COLUMN | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SEPVC | CONTACTOR COLUMN | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SEPVS | SCRUBBER COLUMN | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SEPVT | STRIPPER COLUMN | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SER | STATIC MIXER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SES | PULSATION DAMPENER | 72 | #N/A | #N/A | #N/A | Mainly chemical with some process | P4-C ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | #N/A | #N/A | #N/A
FA_SETAC | CLOSED ROOF ATMOSPHERIC TANK | 60 | #N/A | #N/A | #N/A | Fuel, MEG, Condensate, lube oil, reservoirs included, demote if non-hazardous? | P4-E ¦ Oil Storage & Offloading ¦ Hydrocarbon Tanks | #N/A | #N/A | #N/A
FA_SETAF | FLOATING ROOF ATMOSPHERIC TANK | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SETAO | OPEN ROOF ATMOSPHERIC TANK | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SETAP | PIT / SUMP | 40 | #N/A | #N/A | #N/A | Air comp oil sump to sewage pits | P2-A/B ¦ Structural Integrity ¦ Tertiary Structures - Failure may result in fall 1 - 3m | #N/A | #N/A | #N/A
FA_SETAR | RESERVOIR | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SETPC | CYLINDRICAL PRESSURISED TANK | 11 | #N/A | #N/A | #N/A | Air receiver, water, air, seal oil, N2 tanks. Assume high pressure system until reviewed at detail level. | P4-C ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | #N/A | #N/A | #N/A
FA_SETPS | SPHERICAL PRESSURISED TANK | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SEV | LOUVRE | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SEY | HYDRAULIC HATCH | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SEZ | SILENCER / MUFFLER | 64 | #N/A | #N/A | #N/A | Exhaust / vent systems (some intakes),loss of function has level F or below impact | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | #N/A | #N/A | #N/A
FA_SQFC | EQUIPMENT CABINET | 21 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | Fire hydrant cabinets set with this code, could escalate for 'primary' fire fighting systems | M7 ¦ Fire protection ¦ Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | #N/A | #N/A | #N/A
FA_SQFDD | DUST DETECTOR | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQFDF | FLAME DETECTOR | 420 | #N/A | #N/A | #N/A | Gonna be an A… | M6-A ¦ Fire & Gas systems ¦ Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | #N/A | #N/A | #N/A
FA_SQFDG | FIXED GAS DETECTOR | 739 | #N/A | #N/A | #N/A | Gonna be an A… | M6-A ¦ Fire & Gas systems ¦ Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | #N/A | #N/A | #N/A
FA_SQFDH | PERSONAL H2S MONITOR | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQFDM | MOTION DETECTOR | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQFDP | PORTABLE GAS MONITOR | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQFDR | PERSONAL RADIATION MONITOR | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQFDS | SMOKE DETECTOR | 140 | #N/A | #N/A | #N/A | Gonna be an A… | M6-A ¦ Fire & Gas systems ¦ Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | #N/A | #N/A | #N/A
FA_SQFFD | FIREWATER DELUGE SYSTEM | 26 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | Code Applied to gas turbine deluge nozzles, othe deluge skids. Treat as primary fire fighting system | M7 ¦ Fire protection ¦ Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | #N/A | #N/A | #N/A
FA_SQFFE | FIRE EXTINGUISHER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQFFF | FIRE FIGHTING FOAM SYSTEM | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQFFH | FIRE HOSE | 3 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | Fire hydrant cabinets set with this code, could escalate for 'primary' fire fighting systems | M7 ¦ Fire protection ¦ Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | #N/A | #N/A | #N/A
FA_SQFFM | FIRE WATER/FOAM MONITOR | 23 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | Fire hydrant cabinets set with this code, could escalate for 'primary' fire fighting systems | M7 ¦ Fire protection ¦ Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | #N/A | #N/A | #N/A
FA_SQFFS | FIRE EXTINGUISHING SYSTEM | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQFFT | FIRE TRUCK | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQFFY | FIRE HYDRANT | 118 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | Treat as supplementary until told otherwise | M7 ¦ Fire protection ¦ Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | #N/A | #N/A | #N/A
FA_SQFRA | EMERGENCY ALARM DEVICE | 244 | #N/A | #N/A | #N/A | Mostly Manual alarm call points | M6-A ¦ Fire & Gas systems ¦ Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | #N/A | #N/A | #N/A
FA_SQFRB | BREATHING AIR BOTTLE | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQFRC | DESCENT DEVICE | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQFRD | AUTOMATED EXTERNAL DEFIBRILLATOR | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQFRE | SAFETY SHOWER OR EYE BATH | 20 | #N/A | #N/A | #N/A | Not MAH lifesaving equipment | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | #N/A | #N/A | #N/A
FA_SQFRJ | LIFEJACKET | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQFRK | PERSONNEL BASKET | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQFRL | LIFEBOAT AND DAVIT | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQFRP | SELF-CONTAINED BREATHING APPARATUS | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQFRR | LIFERAFT | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQFRS | BREATHING AIR SYSTEM | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQFRT | RESCUE BOAT | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQFRV | SURVIVAL SUIT | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQFRY | LIFEBUOY | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQL | LABORATORY EQUIPMENT | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQMC | PORTABLE COMPRESSOR | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQMD | TESTING DEVICE | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQMG | PORTABLE GENERATOR | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQML | PORTABLE LIGHT PLANT | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQMT | MAINTENANCE TOOL | 2 | #N/A | #N/A | #N/A | Barring devices for flash gas compressors | P4-D ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Auxiliaries like (cleaning system, control system, utilities) | #N/A | #N/A | #N/A
FA_SQMW | WELDING MACHINE | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQNB | SIGNAL BUOY | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQNL | NAVIGATION LIGHT | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQNP | POSITIONING EQUIPMENT | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQR | OIL SPILL RESPONSE EQUIPMENT | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQTA | PUBLIC ADDRESS AND ALARM SYSTEM | 60 | #N/A | #N/A | #N/A | Includes some un-validated MAC points. | M3-A ¦ Personnel Address (PA) System ¦ Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | #N/A | #N/A | #N/A
FA_SQTB | NON DIRECTIONAL BEACON | 169 | #N/A | #N/A | #N/A | Alarm / status signals | M3-A ¦ Personnel Address (PA) System ¦ Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | #N/A | #N/A | #N/A
FA_SQTC | COMPASS | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQTD | RADAR | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQTE | TELECOMMUNICATION CABINET | 33 | #N/A | #N/A | #N/A | Treating all cabinets as class A | M3-B ¦ Telecommunications ¦ Class A Telecommunication UPS & Shut down | #N/A | #N/A | #N/A
FA_SQTF | FACSIMILE MACHINE | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQTH | PATCH PANEL | 95 | #N/A | #N/A | #N/A | Unvalidated fibre optic panels. Picked digital security, but could be Telecoms. No difference in GES between High and Medium criticality | P6-A ¦ Digital security ¦ Fire walls | #N/A | #N/A | #N/A
FA_SQTI | INTERCOM SYSTEM | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQTL | LOUDSPEAKER | 487 | #N/A | #N/A | #N/A | PAGA loudspeakers, outdoor and in | M3-A ¦ Personnel Address (PA) System ¦ Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | #N/A | #N/A | #N/A
FA_SQTM | AMPLIFIER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQTN | ANTENNA | 3 | #N/A | #N/A | #N/A |  | M3-B ¦ Facility radio system ¦ Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | #N/A | #N/A | #N/A
FA_SQTOF | FIXED RADIO | 6 | #N/A | #N/A | #N/A |  | M3-B ¦ Facility radio system ¦ Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | #N/A | #N/A | #N/A
FA_SQTOP | PAGER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQTOR | PORTABLE RADIO | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQTP | COMPUTER PERIPHERAL | 104 | #N/A | #N/A | #N/A | all NOTAGS, RJ45 network sockets - none allocated |  | #N/A | #N/A | #N/A
FA_SQTR | PROXIMITY READER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQTS | TELEPHONE OR MULTIMEDIA EQUIPMENT | 101 | #N/A | #N/A | #N/A | Includes outdoor EX call points as well as control room IP phone, so will want to downrate non-EX phones | M3-B ¦ Facility Emergency Telephone & Hot line systems ¦ Call control - PABX/IPT Ex telephones Designated emergency phones (Control rooms muster points etc.) Interconnecting cable plant and networks | #N/A | #N/A | #N/A
FA_SQTT | SATELLITE EQUIPMENT | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQTV | CCTV CAMERA UNIT | 167 | #N/A | #N/A | #N/A | None allocated - not explicitly listed in MAH table |  | #N/A | #N/A | #N/A
FA_SQTW | WIRELESS COMMUNICATION OR CONTROL EQUIPMENT | 17 | #N/A | #N/A | #N/A | NOTAGged personnel badge readers, described as access control, not electronic muster system so None allocated |  | #N/A | #N/A | #N/A
FA_SQTX | MULTIPLEXER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQTY | RECEIVER / TRANSMITTER | 4 | #N/A | #N/A | #N/A | NOTTAGged gas detectors | M6-A ¦ Fire & Gas systems ¦ Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | #N/A | #N/A | #N/A
FA_SQUC | CLEANING EQUIPMENT | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQUE | EXERCISE EQUIPMENT | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SQUG | GALLEY EQUIPMENT | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SRFRN | VENTILATOR | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_SYLH | SYSTEM LEVEL HIERARCHY | 316 | #N/A | #N/A | #N/A | None allocated - Assumed non-physically meaningful or pending proper classification |  | #N/A | #N/A | #N/A
FA_WECM | MOBILE CRANE | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WECO | OVERHEAD CRANE | 11 | #N/A | #N/A | #N/A | Maintenance equipment on RE packages | P4-D ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Auxiliaries like (cleaning system, control system, utilities) | #N/A | #N/A | #N/A
FA_WECP | PEDESTAL CRANE | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WECT | TOWER CRANE | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WED | LOADING ARM | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WEHC | CUTTING DRILL | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WEHR | CRUSHER / SHREDDER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WEHS | SHAKER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WEHY | CONVEYOR | 2 | #N/A | #N/A | #N/A | None allocatedSalt discharge screw conveyors, no MAH role identified |  | #N/A | #N/A | #N/A
FA_WELB | CHAIN BLOCK | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WELC | CABLE OR CHAIN | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WELD | DAVIT | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WELE | ELEVATOR | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WELF | FORKLIFT | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WELG | SLING | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WELH | HOIST | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WELJ | JACK | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WELM | MAN LIFT / BASKET / CHERRY PICKER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WELN | CONTAINER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WELP | SPREADER FRAME / BAR | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WELS | SHEAVE OR PULLEY | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WELT | MONORAIL / TROLLEY | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WELW | WINCH | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WESR | REMOTE OPERATED VEHICLE (ROV) | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WEST | RUNNING TOOL | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WETRA | AUTOMOBILE | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WETRC | ROAD COMPACTOR | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WETRL | LAWNMOWER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WETRO | TRACTOR | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WETRR | TRAILER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WETRS | ROAD SCRAPER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WETRT | TRUCK | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WETRW | ROAD SWEEPER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WETWB | BARGE | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WETWF | MARINE FENDER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WETWT | MARINE THRUSTER | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A
FA_WETWV | MARINE VESSEL | #REF! | #N/A | #N/A | #N/A |  |  | #N/A | #N/A | #N/A

## MAHBarrierSetup (pass 1)
This is not a live query, be careful if overwriting as may lose table alignment
[6 empty] | Add text this column | Use this column to select MAH barrier component for failure code
FailureCode | Description | Number found in ASSET-C WND | MAH_Barrier_Family | MAH_Barrier_Component | Typ_Criticality | Comment | MAH_Selector
FA_CFBC | CONTROL ROOM | 4 | #N/A | #N/A | #N/A | None allocated initially, but GES only allows for high criticality anyway. Monthlycomfort check & 4yrly inspection | M3-A ¦ Personnel Address (PA) System ¦ Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights
FA_CFBE | ELECTRICAL SUBSTATION | #REF! | #N/A | #N/A | #N/A
FA_CFBI | INSTRUMENT HOUSE | #REF! | #N/A | #N/A | #N/A
FA_CFBL | LIVING ACCOMMODATION | #REF! | #N/A | #N/A | #N/A
FA_CFBO | OFFICE BUILDING | #REF! | #N/A | #N/A | #N/A
FA_CFDL | LAGOON | #REF! | #N/A | #N/A | #N/A
FA_CFDO | OUTFALL | #REF! | #N/A | #N/A | #N/A
FA_CFSGA | ACCESS CONTROL GATE | #REF! | #N/A | #N/A | #N/A | None allocated
FA_CFSGB | BRIDGE | #REF! | #N/A | #N/A | #N/A
FA_CFSGC | CONTAINMENT | #REF! | #N/A | #N/A | #N/A
FA_CFSGP | PARKING LOT | #REF! | #N/A | #N/A | #N/A
FA_CFSGR | ROAD | #REF! | #N/A | #N/A | #N/A
FA_CFSGS | STORAGE YARD | #REF! | #N/A | #N/A | #N/A
FA_CFSGT | WASTE STORAGE | #REF! | #N/A | #N/A | #N/A
FA_CFSGW | WALL OR FENCE | 5 | #N/A | #N/A | #N/A | None allocated, initially, treated as secondary structures | P2-A/B ¦ Structural Integrity ¦ Secondary Structures - Single component failure has no immediate consequence
FA_CFSPD | FIRE DOOR | #REF! | #N/A | #N/A | #N/A
FA_CFSPW | FIRE / BLAST WALL | #REF! | #N/A | #N/A | #N/A
FA_CFSSA | ANCHOR | #REF! | #N/A | #N/A | #N/A
FA_CFSSD | DERRICK OR FRAME | #REF! | #N/A | #N/A | #N/A
FA_CFSSE | EQUIPMENT SUPPORT STRUCTURE | 104 | #N/A | #N/A | #N/A | Expect to escalate by SYSTEM, Location | P2-A/B ¦ Structural Integrity ¦ Secondary Structures - Single component failure has no immediate consequence
FA_CFSSF | STRUCTURAL FOUNDATION | 19 | #N/A | #N/A | #N/A | Expect to escalate by SYSTEM, Location | P2-A/B ¦ Structural Integrity ¦ Secondary Structures - Single component failure has no immediate consequence
FA_CFSSI | PILE | #REF! | #N/A | #N/A | #N/A
FA_CFSSP | PEDESTAL | #REF! | #N/A | #N/A | #N/A
FA_CFSSS | STABILISATION OR GUIDANCE EQUIPMENT | #REF! | #N/A | #N/A | #N/A
FA_CFSST | STRUCTURAL BASE | 907 | #N/A | #N/A | #N/A | Expect to escalate by SYSTEM, Location | P2-A/B ¦ Structural Integrity ¦ Secondary Structures - Single component failure has no immediate consequence
FA_EECF | LIGHT FITTING | 398 | #N/A | #N/A | #N/A | Expect to de-escalate non-emergency lighting | M3-D ¦ Emergency Lighting ¦ Emergency Lighting - supplied from Emergency Generator Switchboard
FA_EECH | ELECTRIC HEATER | 109 | #N/A | #N/A | #N/A | Expect to de-escalate for non-hydrocarbon heaters | P4-C ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C
FA_EECMD | DC ELECTRIC MOTOR | 7 | #N/A | #N/A | #N/A | May modify fire pump started | M4-A ¦ Ignition Prevention ¦ For Equipment in Zone 2
FA_EECMI | AC INDUCTION ELECTRIC MOTOR | 466 | #N/A | #N/A | #N/A | Assumed to be zone 2 until indicated otherwise | M4-A ¦ Ignition Prevention ¦ For Equipment in Zone 2
FA_EECMS | AC SYNCHRONOUS ELECTRIC MOTOR | 1 | #N/A | #N/A | #N/A | Flare Tip Davit Winch Motor | M4-A ¦ Ignition Prevention ¦ For Equipment in Zone 0 and Zone 1
FA_EECO | ELECTRIC SOCKET OUTLET | 21 | #N/A | #N/A | #N/A | Zone 2 assumed by default | M4-A ¦ Ignition Prevention ¦ For Equipment in Zone 2
FA_EECT | TRACE HEATING CIRCUIT | 2 | #N/A | #N/A | #N/A | Zone 2 assumed by default | M4-A ¦ Ignition Prevention ¦ For Equipment in Zone 2
FA_EEHC | AIR CONDITIONING UNIT | #REF! | #N/A | #N/A | #N/A
FA_EEHH | AIR HANDLING UNIT | #REF! | #N/A | #N/A | #N/A
FA_EEHV | CONSTANT VOLUME UNIT | #REF! | #N/A | #N/A | #N/A
FA_EEPA | SURGE ARRESTOR | #REF! | #N/A | #N/A | #N/A
FA_EEPBA | AIR CIRCUIT BREAKER | 868 | #N/A | #N/A | #N/A | Assumed part of emergency curcuit until reviewed otherwise | M4-A ¦ Ignition Prevention ¦ Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc).
FA_EEPBG | GAS CIRCUIT BREAKER | #REF! | #N/A | #N/A | #N/A
FA_EEPBL | LIQUID CIRCUIT BREAKER | #REF! | #N/A | #N/A | #N/A
FA_EEPBV | VACUUM CIRCUIT BREAKER | 48 | #N/A | #N/A | #N/A | Assumed part of emergency curcuit until reviewed otherwise | M4-A ¦ Ignition Prevention ¦ Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc).
FA_EEPCI | IMPRESSED CURRENT CATHODE | #REF! | #N/A | #N/A | #N/A
FA_EEPCS | SACRIFICIAL ANODE | 109 | #N/A | #N/A | #N/A | 6 valid tags all corrosion coupons on process lines | P4-C ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C
FA_EEPE | ELECTRICAL DISCONNECT SWITCH | #REF! | #N/A | #N/A | #N/A
FA_EEPNE | EARTHING BAR | 118 | #N/A | #N/A | #N/A | None allocated initially, treat as lowest criticality control system element | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab
FA_EEPNN | NEUTRAL GROUND RESISTOR | 8 | #N/A | #N/A | #N/A | None allocated initially, treat as lowest criticality control system element | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab
FA_EEPP | PROTECTIVE RELAY | #REF! | #N/A | #N/A | #N/A
FA_EEPS | START / STOP SWITCH | 221 | #N/A | #N/A | #N/A | None allocated, tested each time you use it, so fix on fail
FA_EEPU | UNINTERRUPTIBLE POWER SUPPLY | 29 | #N/A | #N/A | #N/A | De-escalate for non-critical units | M3-C ¦ Emergency Power ¦ UPS Systems
FA_EETA | REACTOR / INDUCTOR | 6 | #N/A | #N/A | #N/A | None allocated, no VALID tags yet
FA_EETB | BATTERY | 39 | #N/A | #N/A | #N/A | Escalate by system / location | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab
FA_EETC | BATTERY CHARGER | 57 | #N/A | #N/A | #N/A | Escalate by system / location | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab
FA_EETD | BUS DUCT / BUS BAR | 70 | #N/A | #N/A | #N/A | None allocated
FA_EETFD | DRY TRANSFORMER | #REF! | #N/A | #N/A | #N/A
FA_EETFE | ENCAPSULATED TRANSFORMER | #REF! | #N/A | #N/A | #N/A
FA_EETFW | WET TRANSFORMER | 20 | #N/A | #N/A | #N/A | De-escalate outside Hazardous zones | M4-A ¦ Ignition Prevention ¦ For Equipment in Zone 2
FA_EETGA | AC ELECTRIC GENERATOR | 10 | #N/A | #N/A | #N/A | De-escalate non-emergency generators | M3-C ¦ Emergency Power ¦ Emergency Generator
FA_EETGD | DC ELECTRIC GENERATOR | #REF! | #N/A | #N/A | #N/A
FA_EETH | ELECTRICAL SLIP RING | #REF! | #N/A | #N/A | #N/A
FA_EETI | ELECTRIC ISOLATOR | 25 | #N/A | #N/A | #N/A | None allocated
FA_EETL | SOLAR PANEL | #REF! | #N/A | #N/A | #N/A
FA_EETM | MOTOR CONTROL CENTER | 910 | #N/A | #N/A | #N/A | None allocated, escalate for any emergency systems
FA_EETO | POWER / CONTROL MODULE | 5 | #N/A | #N/A | #N/A | None allocated, escalate for any emergency systems
FA_EETP | ELECTRICAL PANEL | 3 | #N/A | #N/A | #N/A | None allocated, escalate for any emergency systems
FA_EETQ | VARIABLE FREQUENCY DRIVE | 64 | #N/A | #N/A | #N/A | None allocated, escalate for any emergency systems
FA_EETR | POWER RECTIFIER | 15 | #N/A | #N/A | #N/A | None allocated, escalate for any emergency systems
FA_EETS | ELECTRICAL TRANSFER SWITCH | #REF! | #N/A | #N/A | #N/A
FA_EETT | ELECTRICAL CAPACITOR | #REF! | #N/A | #N/A | #N/A
FA_EETV | POWER INVERTER | #REF! | #N/A | #N/A | #N/A
FA_EETW | SWITCHGEAR | 170 | #N/A | #N/A | #N/A | None allocated, escalate for any emergency systems
FA_EETY | POWER SUPPLY | 28 | #N/A | #N/A | #N/A | None allocated, All multi-cable transits
FA_INAA | GAS ANALYSER | #REF! | #N/A | #N/A | #N/A
FA_INAC | GAS CHROMATOGRAPH | #REF! | #N/A | #N/A | #N/A
FA_INAF | FLOW COMPUTER | #REF! | #N/A | #N/A | #N/A
FA_INAL | LIQUID CHROMATOGRAPH | #REF! | #N/A | #N/A | #N/A
FA_INAM | FLOW METER | 17 | #N/A | #N/A | #N/A | None allocated, escalate for SIS
FA_INAP | SAMPLER | 10 | #N/A | #N/A | #N/A | None allocated - High usage item? Condition likely to be trigger
FA_INAS | LIQUID ANALYSER | #REF! | #N/A | #N/A | #N/A
FA_INDC | LOCAL CONTROLLER | 9 | #N/A | #N/A | #N/A |  | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab
FA_INDFA | ACTUATOR | #REF! | #N/A | #N/A | #N/A
FA_INDFD | DAMPER | 20 | #N/A | #N/A | #N/A | Treat as executive element in F&G protection, all on generatr / em-gen packages | P4-D ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Fire & Gas System
FA_INDFS | SOLENOID VALVE | 230 | #N/A | #N/A | #N/A | Escalate by system / SIS | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab
FA_INDI | INDICATOR | 1479 | #N/A | #N/A | #N/A | None allocated, Fix on fail, escalate any SIS
FA_INDMS | SENSING ELEMENT | 1691 | #N/A | #N/A | #N/A | Escalate if system / SIL requires | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab
FA_INDMT | TRANSMITTER | 2715 | #N/A | #N/A | #N/A | Escalate if system / SIL requires | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab
FA_INDP | PRINTER / RECORDER | #REF! | #N/A | #N/A | #N/A | De-escalate if valid and not alarm response related | P8 ¦ Alarms & operator response ¦ Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution.
FA_INDS | INSTRUMENT SWITCH | 1553 | #N/A | #N/A | #N/A | Escalate if system / SIL requires | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab
FA_INDT | TRANSDUCER | 33 | #N/A | #N/A | #N/A | Mostly machinery protection sensors | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab
FA_INSC | PLC PANEL | 13 | #N/A | #N/A | #N/A | Escalate if system / SIL requires | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab
FA_INSD | DISTRIBUTED CONTROL PANEL | 9 | #N/A | #N/A | #N/A | Escalate for emergency systems | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab
FA_INSJ | JUNCTION BOX | 866 | #N/A | #N/A | #N/A | Escalate where SIS or in SIL | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab
FA_INSL | LOCAL CONTROL PANEL | 218 | #N/A | #N/A | #N/A | Escalate where SIS or in SIL | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab
FA_INSM | METEOROLOGICAL SYSTEM PANEL | #REF! | #N/A | #N/A | #N/A
FA_INSP | CONDITION MONITORING SYSTEM PANEL | #REF! | #N/A | #N/A | #N/A
FA_INSS | OPERATOR STATION | 8 | #N/A | #N/A | #N/A | Assumed to be replace on fail / non-BPCS devices | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab
FA_INST | TERMINATION RACK | 3 | #N/A | #N/A | #N/A | Assumed to be replace on fail / non-BPCS devices | P6-A ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cab
FA_INSY | SAFETY INSTRUMENT SYSTEM PANEL | 19 | #N/A | #N/A | #N/A | Assume SIL rated will get escalated | P6-A ¦ Control systems - non LoPs, LOPA initiating causes ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI
FA_PEA | SELF-ACTUATING VALVE | 133 | #N/A | #N/A | #N/A | Mostly PCVs, some process, some utility, some package. De-escalate by System / Package. Arguably some will also be Process containment equipment for gas =>A criticality | P6-A ¦ Control systems - non LoPs, LOPA initiating causes ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI
FA_PEB | BUOYANCY DEVICE | #REF! | #N/A | #N/A | #N/A
FA_PEC | DUCT | #REF! | #N/A | #N/A | #N/A
FA_PED | DIVERTER | #REF! | #N/A | #N/A | #N/A
FA_PEE | EXPANSION DEVICE | #REF! | #N/A | #N/A | #N/A
FA_PEG | PIPING | 12600 | #N/A | #N/A | #N/A | Escalate by system | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_PEH | BUNKERING HOSE | #REF! | #N/A | #N/A | #N/A
FA_PEI | BUCKLE INITIATOR | #REF! | #N/A | #N/A | #N/A
FA_PEL | PIG LAUNCHER / RECEIVER | 1 | #N/A | #N/A | #N/A | Assumed as high criticality item | P4-C ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C
FA_PEM | MANIFOLD | 134 | #N/A | #N/A | #N/A | All utility (air, oil) service by default | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_PEN | METER PROVER | #REF! | #N/A | #N/A | #N/A
FA_PEO | RESTRICTIVE ORIFICE | 482 | #N/A | #N/A | #N/A | Demote by System, package (line?) | P5-A ¦ Overpressure Protection ¦ ROs (or FOs) that restrict gas flow to flare
FA_PEP | BLOWOUT PREVENTER | #REF! | #N/A | #N/A | #N/A
FA_PEQ | TURRET EQUIPMENT | #REF! | #N/A | #N/A | #N/A
FA_PER | RISER | #REF! | #N/A | #N/A | #N/A
FA_PESC | CONVENTIONAL PRESSURE SAFETY VALVE | 550 | #N/A | #N/A | #N/A | Escalate by system | P5-A ¦ Overpressure Protection ¦ All other PSVs
FA_PESP | PILOT OPERATED PRESSURE SAFETY VALVE | #REF! | #N/A | #N/A | #N/A
FA_PESR | RUPTURE DISC | 49 | #N/A | #N/A | #N/A | Escalate by system, package | P5-A ¦ Overpressure Protection ¦ Other bursting disks
FA_PESV | VACUUM RELIEF PRESSURE SAFETY VALVE | 15 | #N/A | #N/A | #N/A | Escalate by system, package if hazardous | P5-A ¦ Overpressure Protection ¦ Other Vacuum breakers not covered by the descriptions above.
FA_PET | THERMOWELL | 548 | #N/A | #N/A | #N/A | GES give 5 yrly inspection, demote by system if required | P4-C ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C
FA_PEU | UMBILICAL | #REF! | #N/A | #N/A | #N/A
FA_PEVB | BALL VALVE | 9510 | #N/A | #N/A | #N/A | Escalate by system, package if required | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_PEVC | CHECK VALVE | 1564 | #N/A | #N/A | #N/A | Escalate by system, package, consequence | P5-A ¦ Overpressure Protection ¦ All other NRVs
FA_PEVD | DIAPHRAGM VALVE | 3 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 3 valves on firepump starter systems, GES gives annual inspect, test, overhaul 6 yrly | M7 ¦ Fire protection ¦ Firewater pumps (main and jockey), drivers, their controls and control panels
FA_PEVG | GATE VALVE | 2589 | #N/A | #N/A | #N/A | Escalate by sytem, | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_PEVH | SHEAR VALVE | #REF! | #N/A | #N/A | #N/A
FA_PEVL | GLOBE VALVE | 969 | #N/A | #N/A | #N/A | Escalate by sytem, | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_PEVM | MULTIPLE ORIFICE VALVE | 9 | #N/A | #N/A | #N/A | Escalate by sytem, | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_PEVN | NEEDLE VALVE | 79 | #N/A | #N/A | #N/A | Escalate by sytem, if required | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_PEVS | SUBSURFACE SAFETY VALVE | #REF! | #N/A | #N/A | #N/A
FA_PEVX | DIVERTER VALVE | 4 | #N/A | #N/A | #N/A | Escalate by sytem, if required | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_PEVY | BUTTERFLY VALVE | 65 | #N/A | #N/A | #N/A | Escalate by sytem, if required | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_PEW | SWIVEL | #REF! | #N/A | #N/A | #N/A
FA_PEX | X-MAS TREE / WELLHEAD | #REF! | #N/A | #N/A | #N/A
FA_PEZ | TUBING HANGER | #REF! | #N/A | #N/A | #N/A
FA_REBC | BLOWER, CENTRIFUGAL | 4 | #N/A | #N/A | #N/A | Escalate by system if required( flare blowers most likely) | P4-D ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below)
FA_REBR | ROTARY LOBE BLOWER | #REF! | #N/A | #N/A | #N/A
FA_REC | CENTRIFUGE | 4 | #N/A | #N/A | #N/A | MEG system may override? | P4-D ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below)
FA_REDH | HYDRAULIC MOTOR | 6 | #N/A | #N/A | #N/A | Fire pump starters, should get maintained whe parent serviced? | P4-D ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below)
FA_REDP | PNEUMATIC MOTOR | 26 | #N/A | #N/A | #N/A | Utility / starter motors (inc EmGen black start?) should be checked as part of parent servicing? | P4-D ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below)
FA_REDT | TOP DRIVE | #REF! | #N/A | #N/A | #N/A
FA_REEG | GAS FUEL COMBUSTION ENGINE | #REF! | #N/A | #N/A | #N/A
FA_REEL | LIQUID FUEL COMBUSTION ENGINE | 4 | #N/A | #N/A | #N/A | Firepumps and EmGens | P4-D ¦ Diesel Driven Packages ¦ Diesel Engine
FA_REFA | AXIAL FAN | 24 | #N/A | #N/A | #N/A | None allocated, assume fan criticality is mainly non-safety role, except enclosure ventilation which should be caught by package?
FA_REFC | CENTRIFUGAL FAN | 131 | #N/A | #N/A | #N/A | None allocated, assume fan criticality is mainly non-safety role, except enclosure ventilation which should be caught by package / Fire and gas??
FA_REI | MIXER | #REF! | #N/A | #N/A | #N/A
FA_REMA | AXIAL COMPRESSOR | #REF! | #N/A | #N/A | #N/A
FA_REMC | CENTRIFUGAL COMPRESSOR | 3 | #N/A | #N/A | #N/A | Gas compressors may get modified by system (ROCE .AND. HC containing type rule), otherwise em-gen starter compressor | P4-D ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below)
FA_REMR | RECIPROCATING COMPRESSOR | 6 | #N/A | #N/A | #N/A | Flash gas compressors, so treat a gas containing equipment. | P4-C ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C
FA_REMT | ROTARY COMPRESSOR | 11 | #N/A | #N/A | #N/A | Air compressors | P4-D ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below)
FA_RENG | GAS TURBINE | 10 | #N/A | #N/A | #N/A | Driver of package, driven equipment could be different criticality | P4-D ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Gas Generator
FA_RENS | STEAM TURBINE | #REF! | #N/A | #N/A | #N/A
FA_REPB | BEAM PUMP | #REF! | #N/A | #N/A | #N/A
FA_REPC | CENTRIFUGAL PUMP | 275 | #N/A | #N/A | #N/A | Override for hazardous systems by system id | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_REPD | POSITIVE DISPLACEMENT PUMP | 39 | #N/A | #N/A | #N/A | Override for hazardous systems by system id? | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_REPG | PROGRESSIVE CAVITY PUMP | #REF! | #N/A | #N/A | #N/A
FA_REPR | RECIPROCATING PUMP | #REF! | #N/A | #N/A | #N/A
FA_REPV | CONTROLLED VOLUME PUMP | #REF! | #N/A | #N/A | #N/A
FA_RER | RAKE / SCRAPER | 2 | #N/A | #N/A | #N/A | Oil skimmers, none allocated
FA_RES | SOOTBLOWER | #REF! | #N/A | #N/A | #N/A
FA_RETC | CLUTCH | #REF! | #N/A | #N/A | #N/A
FA_RETG | GEARBOX | 5 | #N/A | #N/A | #N/A | None in MEL (yet), only breather system for gearbox had this code (corrected)
FA_RETH | HYDRAULIC / TORQUE CONVERTER | #REF! | #N/A | #N/A | #N/A
FA_RETP | COUPLING | 5 | #N/A | #N/A | #N/A | couplings only identified on air compressors, redundancy and loss of function not MAH? | P4-D ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below)
FA_RETV | CONTINOUSLY VARIABLE TRANSMISSION | #REF! | #N/A | #N/A | #N/A
FA_REUC | CHEMICAL INJECTION SYSTEM | 1 | #N/A | #N/A | #N/A | Review detail of what this is | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_REUH | HYDRAULIC SYSTEM | #REF! | #N/A | #N/A | #N/A
FA_REXA | AXIAL TURBO EXPANDER | #REF! | #N/A | #N/A | #N/A
FA_REXC | CENTRIFUGAL TURBO EXPANDER | #REF! | #N/A | #N/A | #N/A
FA_REZ | ROTARY DRUM FILTER | #REF! | #N/A | #N/A | #N/A
FA_SEA | AIR DRYER | #REF! | #N/A | #N/A | #N/A
FA_SEBF | FIRETUBE BOILER | #REF! | #N/A | #N/A | #N/A
FA_SEBH | WASTE HEAT BOILER | #REF! | #N/A | #N/A | #N/A
FA_SEBW | WATERTUBE BOILER | #REF! | #N/A | #N/A | #N/A
FA_SEC | CYCLONE | 6 | #N/A | #N/A | #N/A | Vortex coolers to air compressor panels, no MAH role
FA_SED | DRAIN POT | #REF! | #N/A | #N/A | #N/A
FA_SEE | EJECTOR / EDUCTOR | 3 | #N/A | #N/A | #N/A | Mixers for MEG storage tanks. | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_SEFB | BASKET STRAINER FILTER | 310 | #N/A | #N/A | #N/A | Escalate by sytem if required | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_SEFC | COALESCER FILTER | #REF! | #N/A | #N/A | #N/A
FA_SEFE | ELEMENT FILTER | 194 | #N/A | #N/A | #N/A | Generally for equipment reliability, rather than MAH, None allocated
FA_SEFM | MEDIA FILTER | #REF! | #N/A | #N/A | #N/A
FA_SEFP | ELECTROSTATIC PRECIPITATOR FILTER | #REF! | #N/A | #N/A | #N/A
FA_SEFR | REVERSE OSMOSIS FILTER | #REF! | #N/A | #N/A | #N/A
FA_SEFS | SCREEN FILTER | 18 | #N/A | #N/A | #N/A | Generally for equipment reliability, rather than MAH, None allocated
FA_SEHC | CALORIFIER HEAT EXCHANGER | #REF! | #N/A | #N/A | #N/A
FA_SEHF | FINNED COIL HEAT EXCHANGER | 70 | #N/A | #N/A | #N/A | Mix of process and equipment coolers, modify for system | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_SEHP | PLATE & FRAME HEAT EXCHANGER | #REF! | #N/A | #N/A | #N/A
FA_SEHR | RECUPERATOR HEAT EXCHANGER | #REF! | #N/A | #N/A | #N/A
FA_SEHS | SPIRAL HEAT EXCHANGER | 48 | #N/A | #N/A | #N/A | Mix from seal plan coolers ro process | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_SEHT | SHELL & TUBE HEAT EXCHANGER | 51 | #N/A | #N/A | #N/A | Mixed duty, may need to escalate based on system | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_SEI | BIN / HOPPER | #REF! | #N/A | #N/A | #N/A
FA_SEL | FLAME ARRESTOR | 53 | #N/A | #N/A | #N/A | May be able to downgrade if not in hazardous zone, argument is if its not zone 2 why have a flame arrestor? Hazardous zone schedule may help with parent tags for pieces of equipment | M4-A ¦ Ignition Prevention ¦ For Equipment in Zone 2
FA_SEM | FLARE | 5 | #N/A | #N/A | #N/A | Flare tips defined as A, flare stack assumed to be A as P4-C support to crit A pressure systems | P5-B ¦ Blowdown vent and flare ¦ Flare tips
FA_SENF | FIRED HEATER FURNACE | 4 | #N/A | #N/A | #N/A | Assuming hot surface potential, but otherwise might not be classified as MAH | M4-A ¦ Ignition Prevention ¦ For Equipment in Zone 2
FA_SENI | INCINERATOR FURNACE | #REF! | #N/A | #N/A | #N/A
FA_SENT | THERMAL OXIDIZER FURNACE | #REF! | #N/A | #N/A | #N/A
FA_SEPA | ACCUMULATOR | 192 | #N/A | #N/A | #N/A | Escalate for hazardous fluids | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_SEPC | CYLINDER | 59 | #N/A | #N/A | #N/A | Escalate for hazardous fluids? | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_SEPHC | CONDENSER VESSEL | 2 | #N/A | #N/A | #N/A | Escalate for hazardous fluids? | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_SEPHS | SEPARATOR VESSEL | 190 | #N/A | #N/A | #N/A | Compressor suction seps to air dryer vessels in compressors, so escalate by system | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_SEPHV | VAPORISER VESSEL | #REF! | #N/A | #N/A | #N/A
FA_SEPRL | FLUIDISED BED REACTOR | #REF! | #N/A | #N/A | #N/A
FA_SEPRR | REGENERATOR REACTOR | #REF! | #N/A | #N/A | #N/A
FA_SEPRX | FIXED BED REACTOR | #REF! | #N/A | #N/A | #N/A
FA_SEPVA | ABSORBER COLUMN | #REF! | #N/A | #N/A | #N/A
FA_SEPVC | CONTACTOR COLUMN | #REF! | #N/A | #N/A | #N/A
FA_SEPVS | SCRUBBER COLUMN | #REF! | #N/A | #N/A | #N/A
FA_SEPVT | STRIPPER COLUMN | #REF! | #N/A | #N/A | #N/A
FA_SER | STATIC MIXER | #REF! | #N/A | #N/A | #N/A
FA_SES | PULSATION DAMPENER | 72 | #N/A | #N/A | #N/A | Mainly chemical with some process | P4-C ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C
FA_SETAC | CLOSED ROOF ATMOSPHERIC TANK | 60 | #N/A | #N/A | #N/A | Fuel, MEG, Condensate, lube oil, reservoirs included, demote if non-hazardous? | P4-E ¦ Oil Storage & Offloading ¦ Hydrocarbon Tanks
FA_SETAF | FLOATING ROOF ATMOSPHERIC TANK | #REF! | #N/A | #N/A | #N/A
FA_SETAO | OPEN ROOF ATMOSPHERIC TANK | #REF! | #N/A | #N/A | #N/A
FA_SETAP | PIT / SUMP | 40 | #N/A | #N/A | #N/A | Air comp oil sump to sewage pits | P2-A/B ¦ Structural Integrity ¦ Tertiary Structures - Failure may result in fall 1 - 3m
FA_SETAR | RESERVOIR | #REF! | #N/A | #N/A | #N/A
FA_SETPC | CYLINDRICAL PRESSURISED TANK | 11 | #N/A | #N/A | #N/A | Air receiver, water, air, seal oil, N2 tanks. Assume high pressure system until reviewed at detail level. | P4-C ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300
FA_SETPS | SPHERICAL PRESSURISED TANK | #REF! | #N/A | #N/A | #N/A
FA_SEV | LOUVRE | #REF! | #N/A | #N/A | #N/A
FA_SEY | HYDRAULIC HATCH | #REF! | #N/A | #N/A | #N/A
FA_SEZ | SILENCER / MUFFLER | 64 | #N/A | #N/A | #N/A | Exhaust / vent systems (some intakes),loss of function has level F or below impact | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_SQFC | EQUIPMENT CABINET | 21 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | Fire hydrant cabinets set with this code, could escalate for 'primary' fire fighting systems | M7 ¦ Fire protection ¦ Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system)
FA_SQFDD | DUST DETECTOR | #REF! | #N/A | #N/A | #N/A
FA_SQFDF | FLAME DETECTOR | 420 | #N/A | #N/A | #N/A | Gonna be an A… | M6-A ¦ Fire & Gas systems ¦ Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel
FA_SQFDG | FIXED GAS DETECTOR | 739 | #N/A | #N/A | #N/A | Gonna be an A… | M6-A ¦ Fire & Gas systems ¦ Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel
FA_SQFDH | PERSONAL H2S MONITOR | #REF! | #N/A | #N/A | #N/A
FA_SQFDM | MOTION DETECTOR | #REF! | #N/A | #N/A | #N/A
FA_SQFDP | PORTABLE GAS MONITOR | #REF! | #N/A | #N/A | #N/A
FA_SQFDR | PERSONAL RADIATION MONITOR | #REF! | #N/A | #N/A | #N/A
FA_SQFDS | SMOKE DETECTOR | 140 | #N/A | #N/A | #N/A | Gonna be an A… | M6-A ¦ Fire & Gas systems ¦ Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel
FA_SQFFD | FIREWATER DELUGE SYSTEM | 26 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | Code Applied to gas turbine deluge nozzles, othe deluge skids. Treat as primary fire fighting system | M7 ¦ Fire protection ¦ Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system)
FA_SQFFE | FIRE EXTINGUISHER | #REF! | #N/A | #N/A | #N/A
FA_SQFFF | FIRE FIGHTING FOAM SYSTEM | #REF! | #N/A | #N/A | #N/A
FA_SQFFH | FIRE HOSE | 3 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | Fire hydrant cabinets set with this code, could escalate for 'primary' fire fighting systems | M7 ¦ Fire protection ¦ Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system)
FA_SQFFM | FIRE WATER/FOAM MONITOR | 23 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | Fire hydrant cabinets set with this code, could escalate for 'primary' fire fighting systems | M7 ¦ Fire protection ¦ Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system)
FA_SQFFS | FIRE EXTINGUISHING SYSTEM | #REF! | #N/A | #N/A | #N/A
FA_SQFFT | FIRE TRUCK | #REF! | #N/A | #N/A | #N/A
FA_SQFFY | FIRE HYDRANT | 118 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | Treat as supplementary until told otherwise | M7 ¦ Fire protection ¦ Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system)
FA_SQFRA | EMERGENCY ALARM DEVICE | 244 | #N/A | #N/A | #N/A | Mostly Manual alarm call points | M6-A ¦ Fire & Gas systems ¦ Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel
FA_SQFRB | BREATHING AIR BOTTLE | #REF! | #N/A | #N/A | #N/A
FA_SQFRC | DESCENT DEVICE | #REF! | #N/A | #N/A | #N/A
FA_SQFRD | AUTOMATED EXTERNAL DEFIBRILLATOR | #REF! | #N/A | #N/A | #N/A
FA_SQFRE | SAFETY SHOWER OR EYE BATH | 20 | #N/A | #N/A | #N/A | Not MAH lifesaving equipment | P4-C ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework
FA_SQFRJ | LIFEJACKET | #REF! | #N/A | #N/A | #N/A
FA_SQFRK | PERSONNEL BASKET | #REF! | #N/A | #N/A | #N/A
FA_SQFRL | LIFEBOAT AND DAVIT | #REF! | #N/A | #N/A | #N/A
FA_SQFRP | SELF-CONTAINED BREATHING APPARATUS | #REF! | #N/A | #N/A | #N/A
FA_SQFRR | LIFERAFT | #REF! | #N/A | #N/A | #N/A
FA_SQFRS | BREATHING AIR SYSTEM | #REF! | #N/A | #N/A | #N/A
FA_SQFRT | RESCUE BOAT | #REF! | #N/A | #N/A | #N/A
FA_SQFRV | SURVIVAL SUIT | #REF! | #N/A | #N/A | #N/A
FA_SQFRY | LIFEBUOY | #REF! | #N/A | #N/A | #N/A
FA_SQL | LABORATORY EQUIPMENT | #REF! | #N/A | #N/A | #N/A
FA_SQMC | PORTABLE COMPRESSOR | #REF! | #N/A | #N/A | #N/A
FA_SQMD | TESTING DEVICE | #REF! | #N/A | #N/A | #N/A
FA_SQMG | PORTABLE GENERATOR | #REF! | #N/A | #N/A | #N/A
FA_SQML | PORTABLE LIGHT PLANT | #REF! | #N/A | #N/A | #N/A
FA_SQMT | MAINTENANCE TOOL | 2 | #N/A | #N/A | #N/A | Barring devices for flash gas compressors | P4-D ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Auxiliaries like (cleaning system, control system, utilities)
FA_SQMW | WELDING MACHINE | #REF! | #N/A | #N/A | #N/A
FA_SQNB | SIGNAL BUOY | #REF! | #N/A | #N/A | #N/A
FA_SQNL | NAVIGATION LIGHT | #REF! | #N/A | #N/A | #N/A
FA_SQNP | POSITIONING EQUIPMENT | #REF! | #N/A | #N/A | #N/A
FA_SQR | OIL SPILL RESPONSE EQUIPMENT | #REF! | #N/A | #N/A | #N/A
FA_SQTA | PUBLIC ADDRESS AND ALARM SYSTEM | 60 | #N/A | #N/A | #N/A | Includes some un-validated MAC points. | M3-A ¦ Personnel Address (PA) System ¦ Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights
FA_SQTB | NON DIRECTIONAL BEACON | 169 | #N/A | #N/A | #N/A | Alarm / status signals | M3-A ¦ Personnel Address (PA) System ¦ Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights
FA_SQTC | COMPASS | #REF! | #N/A | #N/A | #N/A
FA_SQTD | RADAR | #REF! | #N/A | #N/A | #N/A
FA_SQTE | TELECOMMUNICATION CABINET | 33 | #N/A | #N/A | #N/A | Treating all cabinets as class A | M3-B ¦ Telecommunications ¦ Class A Telecommunication UPS & Shut down
FA_SQTF | FACSIMILE MACHINE | #REF! | #N/A | #N/A | #N/A
FA_SQTH | PATCH PANEL | 95 | #N/A | #N/A | #N/A | Unvalidated fibre optic panels. Picked digital security, but could be Telecoms. No difference in GES between High and Medium criticality | P6-A ¦ Digital security ¦ Fire walls
FA_SQTI | INTERCOM SYSTEM | #REF! | #N/A | #N/A | #N/A
FA_SQTL | LOUDSPEAKER | 487 | #N/A | #N/A | #N/A | PAGA loudspeakers, outdoor and in | M3-A ¦ Personnel Address (PA) System ¦ Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights
FA_SQTM | AMPLIFIER | #REF! | #N/A | #N/A | #N/A
FA_SQTN | ANTENNA | 3 | #N/A | #N/A | #N/A |  | M3-B ¦ Facility radio system ¦ Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers
FA_SQTOF | FIXED RADIO | 6 | #N/A | #N/A | #N/A |  | M3-B ¦ Facility radio system ¦ Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers
FA_SQTOP | PAGER | #REF! | #N/A | #N/A | #N/A
FA_SQTOR | PORTABLE RADIO | #REF! | #N/A | #N/A | #N/A
FA_SQTP | COMPUTER PERIPHERAL | 104 | #N/A | #N/A | #N/A | all NOTAGS, RJ45 network sockets - none allocated
FA_SQTR | PROXIMITY READER | #REF! | #N/A | #N/A | #N/A
FA_SQTS | TELEPHONE OR MULTIMEDIA EQUIPMENT | 101 | #N/A | #N/A | #N/A | Includes outdoor EX call points as well as control room IP phone, so will want to downrate non-EX phones | M3-B ¦ Facility Emergency Telephone & Hot line systems ¦ Call control - PABX/IPT Ex telephones Designated emergency phones (Control rooms muster points etc.) Interconnecting cable plant and networks
FA_SQTT | SATELLITE EQUIPMENT | #REF! | #N/A | #N/A | #N/A
FA_SQTV | CCTV CAMERA UNIT | 167 | #N/A | #N/A | #N/A | None allocated - not explicitly listed in MAH table
FA_SQTW | WIRELESS COMMUNICATION OR CONTROL EQUIPMENT | 17 | #N/A | #N/A | #N/A | NOTAGged personnel badge readers, described as access control, not electronic muster system so None allocated
FA_SQTX | MULTIPLEXER | #REF! | #N/A | #N/A | #N/A
FA_SQTY | RECEIVER / TRANSMITTER | 4 | #N/A | #N/A | #N/A | NOTTAGged gas detectors | M6-A ¦ Fire & Gas systems ¦ Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel
FA_SQUC | CLEANING EQUIPMENT | #REF! | #N/A | #N/A | #N/A
FA_SQUE | EXERCISE EQUIPMENT | #REF! | #N/A | #N/A | #N/A
FA_SQUG | GALLEY EQUIPMENT | #REF! | #N/A | #N/A | #N/A
FA_SRFRN | VENTILATOR | #REF! | #N/A | #N/A | #N/A
FA_SYLH | SYSTEM LEVEL HIERARCHY | 316 | #N/A | #N/A | #N/A | None allocated - Assumed non-physically meaningful or pending proper classification
FA_WECM | MOBILE CRANE | #REF! | #N/A | #N/A | #N/A
FA_WECO | OVERHEAD CRANE | 11 | #N/A | #N/A | #N/A | Maintenance equipment on RE packages | P4-D ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Auxiliaries like (cleaning system, control system, utilities)
FA_WECP | PEDESTAL CRANE | #REF! | #N/A | #N/A | #N/A
FA_WECT | TOWER CRANE | #REF! | #N/A | #N/A | #N/A
FA_WED | LOADING ARM | #REF! | #N/A | #N/A | #N/A
FA_WEHC | CUTTING DRILL | #REF! | #N/A | #N/A | #N/A
FA_WEHR | CRUSHER / SHREDDER | #REF! | #N/A | #N/A | #N/A
FA_WEHS | SHAKER | #REF! | #N/A | #N/A | #N/A
FA_WEHY | CONVEYOR | 2 | #N/A | #N/A | #N/A | None allocatedSalt discharge screw conveyors, no MAH role identified
FA_WELB | CHAIN BLOCK | #REF! | #N/A | #N/A | #N/A
FA_WELC | CABLE OR CHAIN | #REF! | #N/A | #N/A | #N/A
FA_WELD | DAVIT | #REF! | #N/A | #N/A | #N/A
FA_WELE | ELEVATOR | #REF! | #N/A | #N/A | #N/A
FA_WELF | FORKLIFT | #REF! | #N/A | #N/A | #N/A
FA_WELG | SLING | #REF! | #N/A | #N/A | #N/A
FA_WELH | HOIST | #REF! | #N/A | #N/A | #N/A
FA_WELJ | JACK | #REF! | #N/A | #N/A | #N/A
FA_WELM | MAN LIFT / BASKET / CHERRY PICKER | #REF! | #N/A | #N/A | #N/A
FA_WELN | CONTAINER | #REF! | #N/A | #N/A | #N/A
FA_WELP | SPREADER FRAME / BAR | #REF! | #N/A | #N/A | #N/A
FA_WELS | SHEAVE OR PULLEY | #REF! | #N/A | #N/A | #N/A
FA_WELT | MONORAIL / TROLLEY | #REF! | #N/A | #N/A | #N/A
FA_WELW | WINCH | #REF! | #N/A | #N/A | #N/A
FA_WESR | REMOTE OPERATED VEHICLE (ROV) | #REF! | #N/A | #N/A | #N/A
FA_WEST | RUNNING TOOL | #REF! | #N/A | #N/A | #N/A
FA_WETRA | AUTOMOBILE | #REF! | #N/A | #N/A | #N/A
FA_WETRC | ROAD COMPACTOR | #REF! | #N/A | #N/A | #N/A
FA_WETRL | LAWNMOWER | #REF! | #N/A | #N/A | #N/A
FA_WETRO | TRACTOR | #REF! | #N/A | #N/A | #N/A
FA_WETRR | TRAILER | #REF! | #N/A | #N/A | #N/A
FA_WETRS | ROAD SCRAPER | #REF! | #N/A | #N/A | #N/A
FA_WETRT | TRUCK | #REF! | #N/A | #N/A | #N/A
FA_WETRW | ROAD SWEEPER | #REF! | #N/A | #N/A | #N/A
FA_WETWB | BARGE | #REF! | #N/A | #N/A | #N/A
FA_WETWF | MARINE FENDER | #REF! | #N/A | #N/A | #N/A
FA_WETWT | MARINE THRUSTER | #REF! | #N/A | #N/A | #N/A
FA_WETWV | MARINE VESSEL | #REF! | #N/A | #N/A | #N/A

## FailureCodeTemplate
Failure Code | FAILURE_CODE |  |  |  | Number of Locations in failure code when defaults assigned: |  |  | Final Criticality Code |  | B
Description | FAILURE_CODE_DESCRIPTION
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 4 | 7 |  | Redundancy applies? | No
Environmental | E | 4 | 7 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | E | 4 | 7 |  |  | 8 |  | Annex D Mappings | S | B
Business | E | 4 | 7 |  |  | 8 |  |  | E | B
[6 empty] | 8 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 4 | 7 | 69 | DEFAULT |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable |  |  | B
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | E | 4 | 7 | 69 | DEFAULT
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | E | 4 | 7 | 69 | DEFAULT |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | E | 4 | 7 | 69 | DEFAULT |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## DataTables
Impact Codes | Likelihood Values | Combined_for_data_validation | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Discipline
A | 1 | P2 ¦ Structural Integrity ¦ Primary Structures - All Components | P2 | Structural Integrity | Primary Structures - All Components | A
B | 2 | P2 ¦ Structural Integrity ¦ Secondary Structures - Single component failure results in hydrocarbon LOPC | P2 | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | ELEC
C | 3 | P2B ¦ Structural Integrity ¦ Secondary Structures - Single component failure results in object dropping >3m | P2B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | F&G
D | 4 | P2 ¦ Structural Integrity ¦ Secondary Structures - Single component failure has no immediate consequence | P2 | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | HVAC
E | 5 | P2 ¦ Structural Integrity ¦ Tertiary Structures - Failure may result in fall >3m | P2 | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | INST
F | 6 | P2 ¦ Structural Integrity ¦ Tertiary Structures - Failure may result in fall 1 - 3m | P2 | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | MECH
G | 7 | P2 ¦ Structural Integrity ¦ Tertiary Structures - Failure may result in fall <1m | P2 | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | N/A
H | 8 | P3 ¦ Stability loading control & watertight integrity ¦ Ballast Pumps | P3 | Stability loading control & watertight integrity | Ballast Pumps | A | PIPING
|  | P3 ¦ Stability loading control & watertight integrity ¦ Sea Chest Valves | P3 | Stability loading control & watertight integrity | Sea Chest Valves | A | SAFETY
|  | P3 ¦ Stability loading control & watertight integrity ¦ Loading Computer | P3 | Stability loading control & watertight integrity | Loading Computer | A | STRUCTURE
|  | P3 ¦ Stability loading control & watertight integrity ¦ Tank/Draft Monitoring systems | P3 | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | TBC
|  | P3 ¦ Stability loading control & watertight integrity ¦ Ballast/Cargo/Slop tank Valve control monitoring system | P3 | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | TELE
|  | P3 ¦ Stability loading control & watertight integrity ¦ Bilge System Alarms CCR | P3 | Stability loading control & watertight integrity | Bilge System Alarms CCR | A
|  | P3 ¦ Stability loading control & watertight integrity ¦ Ballast Pump Hydraulic Power | P3 | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A
|  | P3 ¦ Stability loading control & watertight integrity ¦ Down-flooding Points | P3 | Stability loading control & watertight integrity | Down-flooding Points | A
|  | P3 ¦ Stability loading control & watertight integrity ¦ Tank Hatches | P3 | Stability loading control & watertight integrity | Tank Hatches | B
|  | P3 ¦ Stability loading control & watertight integrity ¦ Cargo transfer/loading system | P3 | Stability loading control & watertight integrity | Cargo transfer/loading system | A
|  | P3 ¦ Station Keeping ¦ Chain Stoppers | P3 | Station Keeping | Chain Stoppers | A
|  | P3 ¦ Station Keeping ¦ Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | P3 | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A
|  | P3 ¦ Station Keeping ¦ Suction Piles | P3 | Station Keeping | Suction Piles | A
|  | P3 ¦ Swivel Stack Assembly ¦ Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | P3 | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A
|  | P3 ¦ Swivel Stack Assembly ¦ Swivel Seals (Primary and Secondary Seals) | P3 | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A
|  | P3 ¦ Swivel Stack Assembly ¦ Fibre Optic Ring Joint | P3 | Swivel Stack Assembly | Fibre Optic Ring Joint | A
|  | P3 ¦ Swivel Fluid Barrier System ¦ HPU Reservoir | P3 | Swivel Fluid Barrier System | HPU Reservoir | A
|  | P3 ¦ Swivel Fluid Barrier System ¦ HPU Pumps, filters and automatic controls | P3 | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A
|  | P3 ¦ Swivel Fluid Barrier System ¦ N2 hydraulic Accumulators | P3 | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A
|  | P3 ¦ Swivel/Turret Pipework ¦ Hard piping, PSVs, Valves, etc. | P3 | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A
|  | P3 ¦ Swivel/Turret Pipework ¦ Flexible Hoses Required | P3 | Swivel/Turret Pipework | Flexible Hoses Required | A
|  | P3 ¦ Turret Chain Table ¦ Anchor Mooring Leg | P3 | Turret Chain Table | Anchor Mooring Leg | A
|  | P3 ¦ Turret Chain Table ¦ Riser/Umbilical Installation and Maintenance System | P3 | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A
|  | P3 ¦ Turret Chain Table ¦ (hydraulic winch, wire rope, and HPU) | P3 | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A
|  | P3 ¦ Turret Chain Table ¦ Adjusting Mooring Chain Tension | P3 | Turret Chain Table | Adjusting Mooring Chain Tension | A
|  | P3 ¦ Main Turret Bearing ¦ Grease Lubrication System (grease pump, | P3 | Main Turret Bearing | Grease Lubrication System (grease pump, | A
|  | P3 ¦ Main Turret Bearing ¦ metering valves, injector divider valves, etc.) | P3 | Main Turret Bearing | metering valves, injector divider valves, etc.) | A
|  | P3 ¦ Main Turret Bearing ¦ Main Bearing, Cover, Bearing Studs etc. | P3 | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A
|  | P4 ¦ Wellhead integrity ¦ Annulus Swab | P4 | Wellhead integrity | Annulus Swab | B
|  | P4 ¦ Wellhead integrity ¦ Annulus Master | P4 | Wellhead integrity | Annulus Master | B
|  | P4 ¦ Wellhead integrity ¦ Crossover | P4 | Wellhead integrity | Crossover | B
|  | P4 ¦ Wellhead integrity ¦ Production Swab | P4 | Wellhead integrity | Production Swab | B
|  | P4 ¦ Wellhead integrity ¦ Production Master | P4 | Wellhead integrity | Production Master | B
|  | P4 ¦ Wellhead integrity ¦ Production Wing | P4 | Wellhead integrity | Production Wing | B
|  | P4 ¦ Wellhead integrity ¦ SCSSV | P4 | Wellhead integrity | SCSSV | A
|  | P4 ¦ Subsea Integrity ¦ Production Tree | P4 | Subsea Integrity | Production Tree | A
|  | P4 ¦ Subsea Integrity ¦ Gas Injection Tree | P4 | Subsea Integrity | Gas Injection Tree | A
|  | P4 ¦ Subsea Integrity ¦ Water Injection Tree | P4 | Subsea Integrity | Water Injection Tree | A
|  | P4 ¦ Subsea Integrity ¦ Process Gas Pipeline | P4 | Subsea Integrity | Process Gas Pipeline | A
|  | P4 ¦ Subsea Integrity ¦ Oil Production Pipeline | P4 | Subsea Integrity | Oil Production Pipeline | A
|  | P4 ¦ Subsea Integrity ¦ Water Injection Pipeline | P4 | Subsea Integrity | Water Injection Pipeline | B
|  | P4 ¦ Subsea Integrity ¦ Subsea Pig Launcher / Receiver | P4 | Subsea Integrity | Subsea Pig Launcher / Receiver | A
|  | P4 ¦ Subsea Integrity ¦ Subsea Anchor Pile | P4 | Subsea Integrity | Subsea Anchor Pile | A
|  | P4 ¦ Subsea Integrity ¦ Subsea Buoyancy Tank | P4 | Subsea Integrity | Subsea Buoyancy Tank | A
|  | P4 ¦ Subsea Integrity ¦ Subsea Pipeline Crossing Support | P4 | Subsea Integrity | Subsea Pipeline Crossing Support | B
|  | P4 ¦ Subsea Integrity ¦ Subsea Electrical Flying Lead | P4 | Subsea Integrity | Subsea Electrical Flying Lead | B
|  | P4 ¦ Subsea Integrity ¦ Subsea Electrical Junction Box | P4 | Subsea Integrity | Subsea Electrical Junction Box | B
|  | P4 ¦ Subsea Integrity ¦ Subsea Extension Umbilical | P4 | Subsea Integrity | Subsea Extension Umbilical | B
|  | P4 ¦ Subsea Integrity ¦ Subsea Flowline Buckle Initiator | P4 | Subsea Integrity | Subsea Flowline Buckle Initiator | B
|  | P4 ¦ Subsea Integrity ¦ Subsea Flowline Holdback Pile | P4 | Subsea Integrity | Subsea Flowline Holdback Pile | A
|  | P4 ¦ Subsea Integrity ¦ Subsea Production Flexible Riser | P4 | Subsea Integrity | Subsea Production Flexible Riser | A
|  | P4 ¦ Subsea Integrity ¦ Subsea Gas Injection Flexible Riser | P4 | Subsea Integrity | Subsea Gas Injection Flexible Riser | A
|  | P4 ¦ Subsea Integrity ¦ Subsea Water Injection Flexible Riser | P4 | Subsea Integrity | Subsea Water Injection Flexible Riser | A
|  | P4 ¦ Subsea Integrity ¦ Subsea Service Flexible Riser | P4 | Subsea Integrity | Subsea Service Flexible Riser | A
|  | P4 ¦ Subsea Integrity ¦ Subsea Gas Injection Flexible Spur | P4 | Subsea Integrity | Subsea Gas Injection Flexible Spur | A
|  | P4 ¦ Subsea Integrity ¦ Subsea Water Injection Flexible Spur | P4 | Subsea Integrity | Subsea Water Injection Flexible Spur | B
|  | P4 ¦ Subsea Integrity ¦ Subsea Production Flowline Termination Assembly | P4 | Subsea Integrity | Subsea Production Flowline Termination Assembly | A
|  | P4 ¦ Subsea Integrity ¦ Subsea Gas Injection Flowline Termination Assembly | P4 | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A
|  | P4 ¦ Subsea Integrity ¦ Subsea Water Injection Flowline Termination Assembly | P4 | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B
|  | P4 ¦ Subsea Integrity ¦ Subsea Service Flowline Termination Assembly | P4 | Subsea Integrity | Subsea Service Flowline Termination Assembly | B
|  | P4 ¦ Subsea Integrity ¦ Subsea Riser Gas Lift Module | P4 | Subsea Integrity | Subsea Riser Gas Lift Module | A
|  | P4 ¦ Subsea Integrity ¦ Subsea Distribution (Hydraulic Control) Unit | P4 | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B
|  | P4 ¦ Subsea Integrity ¦ Subsea Hydraulic/Chemical Flying Lead | P4 | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B
|  | P4 ¦ Subsea Integrity ¦ Subsea Main Umbilical | P4 | Subsea Integrity | Subsea Main Umbilical | B
|  | P4 ¦ Subsea Integrity ¦ Subsea Hydraulic Power Unit | P4 | Subsea Integrity | Subsea Hydraulic Power Unit | A
|  | P4 ¦ Subsea Integrity ¦ Subsea Control Panel | P4 | Subsea Integrity | Subsea Control Panel | B
|  | P4 ¦ Subsea Integrity ¦ Subsea Production Inline Tee Assembly | P4 | Subsea Integrity | Subsea Production Inline Tee Assembly | A
|  | P4 ¦ Subsea Integrity ¦ Subsea Gas Injection Inline Tee Assembly | P4 | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A
|  | P4 ¦ Subsea Integrity ¦ Subsea Water Injection Inline Tee Assembly | P4 | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B
|  | P4 ¦ Subsea Integrity ¦ Subsea Service Inline Tee Assembly | P4 | Subsea Integrity | Subsea Service Inline Tee Assembly | B
|  | P4 ¦ Subsea Integrity ¦ Subsea Infield Umbilical | P4 | Subsea Integrity | Subsea Infield Umbilical | B
|  | P4 ¦ Subsea Integrity ¦ Subsea Master Control System | P4 | Subsea Integrity | Subsea Master Control System | A
|  | P4 ¦ Subsea Integrity ¦ Subsea Multiphase Flowmeter | P4 | Subsea Integrity | Subsea Multiphase Flowmeter | B
|  | P4 ¦ Subsea Integrity ¦ Subsea Manifold | P4 | Subsea Integrity | Subsea Manifold | A
|  | P4 ¦ Subsea Integrity ¦ Subsea Anchor Pile (Manifold Support Structure) | P4 | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B
|  | P4 ¦ Subsea Integrity ¦ Subsea Manifold Support Structure | P4 | Subsea Integrity | Subsea Manifold Support Structure | B
|  | P4 ¦ Subsea Integrity ¦ Subsea Riser Tower Monitoring System | P4 | Subsea Integrity | Subsea Riser Tower Monitoring System | B
|  | P4 ¦ Subsea Integrity ¦ Subsea Riser Tower | P4 | Subsea Integrity | Subsea Riser Tower | A
|  | P4 ¦ Subsea Integrity ¦ Subsea Rigid Riser | P4 | Subsea Integrity | Subsea Rigid Riser | A
|  | P4 ¦ Subsea Integrity ¦ Subsea Riser Base | P4 | Subsea Integrity | Subsea Riser Base | A
|  | P4 ¦ Subsea Integrity ¦ Subsea Control Module | P4 | Subsea Integrity | Subsea Control Module | B
|  | P4 ¦ Subsea Integrity ¦ Subsea Production Spool Piece | P4 | Subsea Integrity | Subsea Production Spool Piece | A
|  | P4 ¦ Subsea Integrity ¦ Subsea Gas Injection Spool Piece | P4 | Subsea Integrity | Subsea Gas Injection Spool Piece | A
|  | P4 ¦ Subsea Integrity ¦ Subsea Water Injection Spool Piece | P4 | Subsea Integrity | Subsea Water Injection Spool Piece | B
|  | P4 ¦ Subsea Integrity ¦ Subsea Service Spool Piece | P4 | Subsea Integrity | Subsea Service Spool Piece | A
|  | P4 ¦ Subsea Integrity ¦ Subsea Umbilical | P4 | Subsea Integrity | Subsea Umbilical | B
|  | P4 ¦ Subsea Integrity ¦ Subsea Production Tree Jumper | P4 | Subsea Integrity | Subsea Production Tree Jumper | B
|  | P4.5 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | P4.5 | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A
|  | P4 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | P4 | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A
|  | P4 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework operating at temperature greater than 120o C | P4 | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A
|  | P4 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework for highly toxic substances | P4 | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A
|  | P4 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework with corrosion resistant linings | P4 | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A
| TRUE | P4 ¦ Process Containment Integrity ¦ All pressure retaining Equipment and pipework associated with fire water delivery systems | P4 | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A
|  | P4 ¦ Process Containment Integrity ¦ Bilge and ballast pipework | P4 | Process Containment Integrity | Bilge and ballast pipework | A
|  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework | P4 | Process Containment Integrity | All other pressure Equipment and pipework | C
|  | P4 ¦ Process Containment Integrity ¦ Supports for criticality A pressure systems | P4 | Process Containment Integrity | Supports for criticality A pressure systems | A
|  | P4 ¦ Process Containment Integrity ¦ Insulation installed on criticality A pressure systems | P4 | Process Containment Integrity | Insulation installed on criticality A pressure systems | A
|  | P4 ¦ Process Containment Integrity ¦ Painting on criticality A pressure systems | P4 | Process Containment Integrity | Painting on criticality A pressure systems | A
|  | P4 ¦ Process Containment Integrity ¦ Bolting on criticality A pressure systems | P4 | Process Containment Integrity | Bolting on criticality A pressure systems | A
|  | P4 ¦ Process Containment Integrity ¦ All other supports, paint and bolting | P4 | Process Containment Integrity | All other supports, paint and bolting | C
|  | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Gas Generator | P4 | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A
|  | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Alternators | P4 | Gas Turbine Packages & Hydrocarbon RE | Alternators | B
|  | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Power Turbine | P4 | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B
|  | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ All Casing joints, fittings and seals | P4 | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B
|  | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ All Shaft Seals | P4 | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A
|  | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ All coupling members | P4 | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B
|  | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Pressurized Enclosures | P4 | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A
|  | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Fire & Gas System | P4 | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A
|  | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ All Shaft Seals System Ancillaries | P4 | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A
|  | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | P4 | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A
|  | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | P4 | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A
|  | P4 ¦ Gas Turbine Packages & Hydrocarbon RE ¦ Auxiliaries like (cleaning system, control system, utilities) | P4 | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B
|  | P4 ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | P4 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B
|  | P4 ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | P4 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A
|  | P4 ¦ Diesel Driven Packages ¦ Diesel Engine | P4 | Diesel Driven Packages | Diesel Engine | B
|  | P4 ¦ Diesel Driven Packages ¦ Alternators | P4 | Diesel Driven Packages | Alternators | B
|  | P4 ¦ Diesel Driven Packages ¦ All Fuel system Joints, Fittings and Seals | P4 | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B
|  | P4 ¦ Diesel Driven Packages ¦ All coupling members | P4 | Diesel Driven Packages | All coupling members | B
|  | P4 ¦ Diesel Driven Packages ¦ All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | P4 | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A
|  | P4 ¦ Diesel Driven Packages ¦ All other Systems (governor, control, utilities, etc.) | P4 | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B
|  | P4 ¦ Oil Storage & Offloading ¦ Export Booster Pumps | P4 | Oil Storage & Offloading | Export Booster Pumps | A
|  | P4 ¦ Oil Storage & Offloading ¦ Export Hose | P4 | Oil Storage & Offloading | Export Hose | A
|  | P4 ¦ Oil Storage & Offloading ¦ Marine Growth Prevention Equipment | P4 | Oil Storage & Offloading | Marine Growth Prevention Equipment | B
|  | P4 ¦ Oil Storage & Offloading ¦ Cargo Tank Cleaning Systems | P4 | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B
|  | P4 ¦ Oil Storage & Offloading ¦ Cargo & Ballast Hydraulic Valve Control | P4 | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A
|  | P4 ¦ Oil Storage & Offloading ¦ Marine Hydraulic systems (pumps, power units and storage tanks) | P4 | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B
|  | P4 ¦ Oil Storage & Offloading ¦ Void Tank Gas Detection | P4 | Oil Storage & Offloading | Void Tank Gas Detection | A
|  | P4 ¦ Oil Storage & Offloading ¦ Void Tank Dehumidification systems | P4 | Oil Storage & Offloading | Void Tank Dehumidification systems | B
|  | P4 ¦ Oil Storage & Offloading ¦ Hydrocarbon Tanks | P4 | Oil Storage & Offloading | Hydrocarbon Tanks | A
|  | P4 ¦ Oil Storage & Offloading ¦ Ballast Tanks | P4 | Oil Storage & Offloading | Ballast Tanks | A
|  | P4 ¦ Oil Storage & Offloading ¦ Void Tanks | P4 | Oil Storage & Offloading | Void Tanks | B
|  | P5 ¦ Overpressure Protection ¦ PSV in hazardous or toxic duty | P5 | Overpressure Protection | PSV in hazardous or toxic duty | A
|  | P5 ¦ Overpressure Protection ¦ PSV in non-hazardous, non-toxic service where pressure is above 50 barg | P5 | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A
|  | P5 ¦ Overpressure Protection ¦ PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | P5 | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A
|  | P5 ¦ Overpressure Protection ¦ PSV in non-hazardous, nontoxic service where inlet size 8” or above | P5 | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A
|  | P5 ¦ Overpressure Protection ¦ All other PSVs | P5 | Overpressure Protection | All other PSVs | B
|  | P5 ¦ Overpressure Protection ¦ NRV credited in the sizing case for a PSV | P5 | Overpressure Protection | NRV credited in the sizing case for a PSV | A
|  | P5 ¦ Overpressure Protection ¦ NRV that protects against any E+ severity event. For example, damage to Equipment | P5 | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A
|  | P5 ¦ Overpressure Protection ¦ NRVs where consequence/likelihood of failure combination leads to a turquoise risk | P5 | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B
|  | P5 ¦ Overpressure Protection ¦ All other NRVs | P5 | Overpressure Protection | All other NRVs | C
|  | P5 ¦ Overpressure Protection ¦ ROs (or FOs) that restrict gas flow to flare | P5 | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A
|  | P5 ¦ Overpressure Protection ¦ ROs (or FOs) that restrict flow to a PSV | P5 | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A
|  | P5 ¦ Overpressure Protection ¦ ROs in pump recirculation lines | P5 | Overpressure Protection | ROs in pump recirculation lines | B
|  | P5 ¦ Overpressure Protection ¦ Control valves credited in LOPA | P5 | Overpressure Protection | Control valves credited in LOPA | A
|  | P5 ¦ Overpressure Protection ¦ Bursting disks in hazardous or toxic duty | P5 | Overpressure Protection | Bursting disks in hazardous or toxic duty | A
|  | P5 ¦ Overpressure Protection ¦ Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | P5 | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A
|  | P5 ¦ Overpressure Protection ¦ Bursting disk relieving directly to flare (i.e. no PSV downstream) | P5 | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A
|  | P5 ¦ Overpressure Protection ¦ Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | P5 | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV
|  | P5 ¦ Overpressure Protection ¦ Other bursting disks | P5 | Overpressure Protection | Other bursting disks | B
|  | P5 ¦ Overpressure Protection ¦ Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | P5 | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A
|  | P5 ¦ Overpressure Protection ¦ Vacuum breakers in hazardous or toxic duty | P5 | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A
|  | P5 ¦ Overpressure Protection ¦ Other Vacuum breakers not covered by the descriptions above. | P5 | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C
|  | P5 ¦ Overpressure Protection ¦ Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | P5 | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated.
|  | P5 ¦ Blowdown vent and flare ¦ Blowdown valves in hazardous or toxic duty | P5 | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A
|  | P5 ¦ Blowdown vent and flare ¦ Blowdown valves in non-hazardous, nontoxic duty | P5 | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B
|  | P5 ¦ Blowdown vent and flare ¦ Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | P5 | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A
|  | P5 ¦ Blowdown vent and flare ¦ FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | P5 | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A
|  | P5 ¦ Blowdown vent and flare ¦ All other FOVs | P5 | Blowdown vent and flare | All other FOVs | B
|  | P5 ¦ Blowdown vent and flare ¦ HP Flare KO Drum | P5 | Blowdown vent and flare | HP Flare KO Drum | A
|  | P5 ¦ Blowdown vent and flare ¦ HP Flare KO Drum Pumps (at a component level, align with P4-D) | P5 | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A
|  | P5 ¦ Blowdown vent and flare ¦ HP Flare KO Drum Heaters | P5 | Blowdown vent and flare | HP Flare KO Drum Heaters | A
|  | P5 ¦ Blowdown vent and flare ¦ LP Flare KO Drum | P5 | Blowdown vent and flare | LP Flare KO Drum | A
|  | P5 ¦ Blowdown vent and flare ¦ LP Flare KO Drum Pumps (at a component level, align with P4-D) | P5 | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A
|  | P5 ¦ Blowdown vent and flare ¦ KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | P5 | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B
|  | P5 ¦ Blowdown vent and flare ¦ Flare tip ignition systems | P5 | Blowdown vent and flare | Flare tip ignition systems | A
|  | P5 ¦ Blowdown vent and flare ¦ Flare system XXVs that are not covered under FOVs | P5 | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A
|  | P5 ¦ Blowdown vent and flare ¦ Flare tips | P5 | Blowdown vent and flare | Flare tips | A
|  | P5 ¦ Blowdown vent and flare ¦ Any Equipment that maintains the barrier between wet and dry fluids | P5 | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A
|  | P5 ¦ Blowdown vent and flare ¦ Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | P5 | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A
|  | P5 ¦ Blowdown vent and flare ¦ Other vents | P5 | Blowdown vent and flare | Other vents | C
|  | P5 ¦ Blowdown vent and flare ¦ Equipment providing early indication of blockages within flare header | P5 | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A
|  | P5 ¦ Blowdown vent and flare ¦ Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | P5 | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated.
|  | P5 ¦ Blowdown vent and flare ¦ Flare pipework and headers (align with barrier P4-C) | P5 | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A
|  | P6 ¦ Digital security ¦ Fire walls Remote access servers Architecture Staging servers for Anti-virus and OS patches | P6 | Digital security | Fire walls Remote access servers Architecture Staging servers for Anti-virus and OS patches | A
|  | P6 ¦ Control systems - LoPs ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, p | P6 | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A
|  | P6 ¦ Control systems - non LoPs, LOPA initiating causes ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI sc | P6 | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B
|  | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable | P6 | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B
|  | P7 ¦ SIS - LoP Components ¦ LoP Components: Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial | P7 | SIS - LoP Components | LoP Components: Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. Testing Equipment Shutdown Components: XXV valves, blow down valves, switches/push buttons | A
|  | P7 ¦ SIS - Non LoP Components ¦ LoP Components: Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke | P7 | SIS - Non LoP Components | LoP Components: Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B
|  | P8 ¦ Alarms & operator response ¦ Instruments associated with Safety Related Alarms (credited in LOPA) - transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and po | P8 | Alarms & operator response | Instruments associated with Safety Related Alarms (credited in LOPA) - transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A
|  | P8 ¦ Alarms & operator response ¦ Instruments associated with non-Safety Related Alarms - transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distributio | P8 | Alarms & operator response | Instruments associated with non-Safety Related Alarms - transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | B
|  | P9 ¦ Collision Prevention ¦ Navigation Aids, lights, sounders & UPS systems | P9 | Collision Prevention | Navigation Aids, lights, sounders & UPS systems | A
|  | P9 ¦ Export tanker birthing and position monitoring ¦ Mooring Hawser and Load Monitoring | P9 | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B
|  | P9 ¦ Export tanker birthing and position monitoring ¦ Berthing System (TAOMS) | P9 | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B
|  | M1 ¦ Bunding, Open and Closed Hazardous Drains ¦ Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | M1 | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B
|  | M1 ¦ Bunding, Open and Closed Hazardous Drains ¦ Main Deck Coaming | M1 | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B
|  | M1 ¦ Bunding, Open and Closed Hazardous Drains ¦ Open Hazardous Drains Water seals | M1 | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A
|  | M1 ¦ Bunding, Open and Closed Hazardous Drains ¦ Close drain Drum Alarms | M1 | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A
|  | M1 ¦ Bunding, Open and Closed Hazardous Drains ¦ Close drain Drum heating system (heating Coil, instrumentation, insulation) | M1 | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A
|  | M1 ¦ Bunding, Open and Closed Hazardous Drains ¦ Secondary containments | M1 | Bunding, Open and Closed Hazardous Drains | Secondary containments | B
|  | M1 ¦ Bunding, Open and Closed Hazardous Drains ¦ Helideck Drainage | M1 | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B
|  | M1 ¦ Bunding, Open and Closed Hazardous Drains ¦ Rodding | M1 | Bunding, Open and Closed Hazardous Drains | Rodding | A
|  | M2 ¦ Passive Fire Protection ¦ PFP where applied | M2 | Passive Fire Protection | PFP where applied | A
|  | M2 ¦ Blast Overpressure Protection ¦ Blast Walls | M2 | Blast Overpressure Protection | Blast Walls | A
|  | M2 ¦ Blast Overpressure Protection ¦ Blast Doors | M2 | Blast Overpressure Protection | Blast Doors | A
|  | M2 ¦ Temporary refuge integrity ¦ External Temporary Refuge doors | M2 | Temporary refuge integrity | External Temporary Refuge doors | A
|  | M2 ¦ Temporary refuge integrity ¦ Internal Temporary Fire Refuge doors | M2 | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B
|  | M3 ¦ Alarm Annunciation System: ¦ External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | M3 | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A
|  | M3 ¦ Personnel Address (PA) System ¦ Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | M3 | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A
|  | M3 ¦ Marine, Aircraft and Helicopter Radio System ¦ Antenna Receiver/transmitter Batteries Sat comms | M3 | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A
|  | M3 ¦ Telecommunications ¦ Class A Telecommunication UPS & Shut down | M3 | Telecommunications | Class A Telecommunication UPS & Shut down | A
|  | M3 ¦ Electronic Muster System ¦ Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | M3 | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A
|  | M3 ¦ Facility Emergency Telephone & Hot line systems ¦ Call control - PABX/IPT Ex telephones Designated emergency phones (Control rooms muster points etc.) Interconnecting cable plant and networks | M3 | Facility Emergency Telephone & Hot line systems | Call control - PABX/IPT Ex telephones Designated emergency phones (Control rooms muster points etc.) Interconnecting cable plant and networks | A
|  | M3 ¦ Facility radio system ¦ Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | M3 | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A
|  | M3 ¦ Emergency Power ¦ Emergency Generator | M3 | Emergency Power | Emergency Generator | A
|  | M3 ¦ Emergency Power ¦ Hull Generators | M3 | Emergency Power | Hull Generators | A
|  | M3 ¦ Emergency Power ¦ Hull Generators (2 out of 3) | M3 | Emergency Power | Hull Generators (2 out of 3) | B
|  | M3 ¦ Emergency Power ¦ UPS Systems | M3 | Emergency Power | UPS Systems | A
|  | M3 ¦ Emergency Lighting ¦ Emergency Lighting - battery backed | M3 | Emergency Lighting | Emergency Lighting - battery backed | A
|  | M3 ¦ Emergency Lighting ¦ Emergency Lighting - supplied from Emergency Generator Switchboard | M3 | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B
|  | M3 ¦ Emergency Lighting ¦ Emergency Lighting - Emergency Hand Torches in switchgear rooms | M3 | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B
|  | M4 ¦ Ignition Prevention ¦ For Equipment in Zone 0 and Zone 1 | M4 | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A
|  | M4 ¦ Ignition Prevention ¦ For Equipment in Zone 2 | M4 | Ignition Prevention | For Equipment in Zone 2 | B
|  | M4 ¦ Ignition Prevention ¦ Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | M4 | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A
|  | M4 ¦ Inert Gas Blanketing ¦ IGG Generator | M4 | Inert Gas Blanketing | IGG Generator | A
|  | M4 ¦ Inert Gas Blanketing ¦ IGG Generator Diesel Oil Supply Pumps | M4 | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B
|  | M4 ¦ Inert Gas Blanketing ¦ Isolation valves on locked valve register | M4 | Inert Gas Blanketing | Isolation valves on locked valve register | A
|  | M5 ¦ Lifesaving Equipment ¦ Emergency escape breathing devices | M5 | Lifesaving Equipment | Emergency escape breathing devices | A
|  | M5 ¦ Lifesaving Equipment ¦ Grab bags and smoke hoods | M5 | Lifesaving Equipment | Grab bags and smoke hoods | B
|  | M5 ¦ Lifesaving Equipment ¦ Lifejackets | M5 | Lifesaving Equipment | Lifejackets | A
|  | M5 ¦ Lifesaving Equipment ¦ Lifebuoys | M5 | Lifesaving Equipment | Lifebuoys | B
|  | M5 ¦ Lifesaving Equipment ¦ Line-throwing Device | M5 | Lifesaving Equipment | Line-throwing Device | B
|  | M5 ¦ Lifesaving Equipment ¦ Helicopter Crash Equipment | M5 | Lifesaving Equipment | Helicopter Crash Equipment | B
|  | M5 ¦ Lifesaving Equipment ¦ Fireman Outfits | M5 | Lifesaving Equipment | Fireman Outfits | A
|  | M5 ¦ Lifesaving Equipment ¦ Emergency Breathing Air Compressor | M5 | Lifesaving Equipment | Emergency Breathing Air Compressor | B
|  | M5 ¦ Lifesaving Equipment ¦ Storage Containers | M5 | Lifesaving Equipment | Storage Containers | C
|  | M5 ¦ Muster areas, escape and evacuation routes ¦ Station Bill | M5 | Muster areas, escape and evacuation routes | Station Bill | B
|  | M5 ¦ Muster areas, escape and evacuation routes ¦ Escape Routes | M5 | Muster areas, escape and evacuation routes | Escape Routes | A
|  | M5 ¦ Muster areas, escape and evacuation routes ¦ Escape Route Doors | M5 | Muster areas, escape and evacuation routes | Escape Route Doors | A
|  | M5 ¦ Muster areas, escape and evacuation routes ¦ Primary Muster Area | M5 | Muster areas, escape and evacuation routes | Primary Muster Area | A
|  | M5 ¦ Muster areas, escape and evacuation routes ¦ Egress Routes | M5 | Muster areas, escape and evacuation routes | Egress Routes | A
|  | M5 ¦ Muster areas, escape and evacuation routes ¦ Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | M5 | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A
|  | M5 ¦ Muster areas, escape and evacuation routes ¦ Alternative Muster Areas | M5 | Muster areas, escape and evacuation routes | Alternative Muster Areas | B
|  | M5 ¦ Lifeboats ¦ Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | M5 | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A
|  | M5 ¦ Lifeboats ¦ Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | M5 | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A
|  | M5 ¦ Lifeboats ¦ Release Mechanism | M5 | Lifeboats | Release Mechanism | A
|  | M5 ¦ Lifeboats ¦ Deluge, Engine | M5 | Lifeboats | Deluge, Engine | A
|  | M5 ¦ Lifeboats ¦ VHF Radio | M5 | Lifeboats | VHF Radio | A
|  | M5 ¦ Lifeboats ¦ Emergency Beacons | M5 | Lifeboats | Emergency Beacons | A
|  | M5 ¦ Means of escape to sea ¦ Life-rafts | M5 | Means of escape to sea | Life-rafts | A
|  | M5 ¦ Means of escape to sea ¦ Personal Davit Descent devices | M5 | Means of escape to sea | Personal Davit Descent devices | A
|  | M5 ¦ Means of escape to sea ¦ Embarkation Rope Ladders to Sea | M5 | Means of escape to sea | Embarkation Rope Ladders to Sea | A
|  | M5 ¦ Helideck ¦ Helideck Landing Area Net (as required) | M5 | Helideck | Helideck Landing Area Net (as required) | C
|  | M5 ¦ Helideck ¦ Perimeter Net - (Integrity inspections) | M5 | Helideck | Perimeter Net - (Integrity inspections) | B
|  | M5 ¦ Helideck ¦ Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | M5 | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A
|  | M5 ¦ Helideck ¦ Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | M5 | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A
|  | M5 ¦ Helideck ¦ Firefighting Equipment (System) - including Foam (as required) | M5 | Helideck | Firefighting Equipment (System) - including Foam (as required) | A
|  | M5 ¦ Helideck ¦ Helideck Equipment - Deck crew duties and helicopter Ops support | M5 | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C
|  | M5 ¦ Helideck ¦ Emergency Equipment - Helideck emergency response Equipment | M5 | Helideck | Emergency Equipment - Helideck emergency response Equipment | B
|  | M5 ¦ Helideck ¦ MET System (Meteorological Equipment) - On-board IMMS System | M5 | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C
|  | M5 ¦ Rescue & Recovery Systems ¦ Place of Safety | M5 | Rescue & Recovery Systems | Place of Safety | B
|  | M5 ¦ Rescue & Recovery Systems ¦ Man Overboard Alarm | M5 | Rescue & Recovery Systems | Man Overboard Alarm | B
|  | M5 ¦ Rescue & Recovery Systems ¦ Fast Rescue craft | M5 | Rescue & Recovery Systems | Fast Rescue craft | B
|  | M5 ¦ Cranes ¦ Hoisting system | M5 | Cranes | Hoisting system | A
|  | M5 ¦ Cranes ¦ Boom system | M5 | Cranes | Boom system | A
|  | M5 ¦ Cranes ¦ Warning, recording & measuring systems | M5 | Cranes | Warning, recording & measuring systems | A
|  | M5 ¦ Cranes ¦ Structure | M5 | Cranes | Structure | A
|  | M5 ¦ Cranes ¦ Slewing system | M5 | Cranes | Slewing system | B
|  | M5 ¦ Cranes ¦ Hydraulic system | M5 | Cranes | Hydraulic system | B
|  | M5 ¦ Cranes ¦ Prime mover system | M5 | Cranes | Prime mover system | B
|  | M5 ¦ Cranes ¦ Access & walkways | M5 | Cranes | Access & walkways | A
|  | M5 ¦ Cranes ¦ Maintenance Equipment | M5 | Cranes | Maintenance Equipment | C
|  | M5 ¦ Lifting system ¦ Runway beams | M5 | Lifting system | Runway beams | A
|  | M5 ¦ Lifting system ¦ Gantry crane | M5 | Lifting system | Gantry crane | A
|  | M5 ¦ Lifting system ¦ Lifeboat davit | M5 | Lifting system | Lifeboat davit | A
|  | M5 ¦ Lifting system ¦ Life-raft davit | M5 | Lifting system | Life-raft davit | A
|  | M5 ¦ Lifting system ¦ General purpose/maintenance davit | M5 | Lifting system | General purpose/maintenance davit | B
|  | M5 ¦ Lifting system ¦ Winch (for lifting personnel) | M5 | Lifting system | Winch (for lifting personnel) | A
|  | M5 ¦ Lifting system ¦ Winch (general purpose - not for lifting personnel) | M5 | Lifting system | Winch (general purpose - not for lifting personnel) | B
|  | M6 ¦ Fire & Gas systems ¦ Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | M6 | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A
|  | M6 ¦ Fire & Gas systems ¦ Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | M6 | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A
|  | M6 ¦ Emergency Shutdown Systems ¦ XV/XXVs on emergency shutdown duty | M6 | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A
|  | M6 ¦ Riser ESDVs & EIVs ¦ Export/Import/Injection Riser ESDVs (XXVs) & actuators | M6 | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A
|  | M6 ¦ Riser ESDVs & EIVs ¦ Umbilical emergency ESDVs (XXVs) & actuators | M6 | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A
|  | M6 ¦ Riser ESDVs & EIVs ¦ Injection Flowline EIVs (XV) & actuators | M6 | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A
|  | M7 ¦ Fire protection ¦ Firewater pumps (main and jockey), drivers, their controls and control panels | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A
|  | M7 ¦ Fire protection ¦ Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B
|  | M7 ¦ Fire protection ¦ Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A
|  | M7 ¦ Fire protection ¦ Zone isolation valves | M7 | Fire protection | Zone isolation valves | A
|  | M7 ¦ Fire protection ¦ Sprinkler / Deluge Nozzle (≥10 per zone) | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B
|  | M7 ¦ Fire protection ¦ Sprinkler / Deluge Nozzle (<10 per zone) | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A
|  | M7 ¦ Fire protection ¦ Pressure / level / flow instruments | M7 | Fire protection | Pressure / level / flow instruments | A
|  | M7 ¦ Fire protection ¦ Control Valves | M7 | Fire protection | Control Valves | A
|  | M7 ¦ Fire protection ¦ Logic solvers | M7 | Fire protection | Logic solvers | A
|  | M7 ¦ Fire protection ¦ Accommodation hydrants (main fire-fighting mechanism) | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A
|  | M7 ¦ Fire protection ¦ Accommodation hydrants (if sprinkler system present) | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B
|  | M7 ¦ Fire protection ¦ Fusible plug / fusible loop (≥3 per fire zone) | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B
|  | M7 ¦ Fire protection ¦ Fusible plug / fusible loop (<3 per zone) | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A
|  | M7 ¦ Miscellaneous fire protection systems ¦ Hose reels, nozzles and portable fire monitors | M7 | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B
|  | M7 ¦ Miscellaneous fire protection systems ¦ Mobile (wheeled) fire extinguishers | M7 | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B
|  | M7 ¦ Miscellaneous fire protection systems ¦ Fixed CO2 Fire Extinguishing Systems | M7 | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B
|  | M7 ¦ Miscellaneous fire protection systems ¦ Galley Fire Suppression System | M7 | Miscellaneous fire protection systems | Galley Fire Suppression System | A
|  | M7 ¦ Miscellaneous fire protection systems ¦ Water Mist Systems | M7 | Miscellaneous fire protection systems | Water Mist Systems | B
Note on F1: Author: Truncated to 254 characters due to 255 char limit in VLOOKUP function used to find things in this table

## SystemsUtilities
List from Paul Powney received 3 Aug 2017 to identify process and utility systems.
Functional location | Function Location Description | System No | Tag Abbreviation | Utilities System YorN | Comment
E-SYSTEM-00 | GENERAL / NON SPECIFIC SYSTEM SYS 00 | 00 | SYS | N
E-SYSTEM-01 | RESERVED FOR SUBSEA USE | 01 | SYS | N | System Not in Use
E-SYSTEM-02 | RESERVED FOR SUBSEA USE | 02 | SYS | N | System Not in Use
E-SYSTEM-03 | RESERVED FOR SUBSEA USE | 03 | SYS | N | System Not in Use
E-SYSTEM-04 | RESERVED FOR SUBSEA USE | 04 | SYS | N | System Not in Use
E-SYSTEM-05 | CONTROL UMBILICALS AND HPU SYS 05 | 05 | SYS | N
E-SYSTEM-06 | RESERVED FOR SUBSEA USE | 06 | SYS | N | System Not in Use
E-SYSTEM-07 | RESERVED FOR SUBSEA USE | 07 | SYS | N | System Not in Use
E-SYSTEM-08 | RESERVED FOR SUBSEA USE | 08 | SYS | N | System Not in Use
E-SYSTEM-09 | RESERVED FOR SUBSEA USE | 09 | SYS | N | System Not in Use
E-SYSTEM-10 | RESERVED FOR SUBSEA USE | 10 | SYS | N | System Not in Use
E-SYSTEM-11 | RESERVED FOR SUBSEA USE | 11 | SYS | N | System Not in Use
E-SYSTEM-12 | RESERVED FOR SUBSEA USE | 12 | SYS | N | System Not in Use
E-SYSTEM-13 | SUBSEA - WELLHEAD AND TEST SEPARATOR | 13 | SYS | N
E-SYSTEM-14 | RESERVED FOR SUBSEA USE | 14 | SYS | N | System Not in Use
E-SYSTEM-15 | RESERVED FOR SUBSEA USE | 15 | SYS | N | System Not in Use
E-SYSTEM-16 | RESERVED FOR SUBSEA USE | 16 | SYS | N | System Not in Use
E-SYSTEM-17 | RESERVED FOR SUBSEA USE | 17 | SYS | N | System Not in Use
E-SYSTEM-18 | RESERVED FOR SUBSEA USE | 18 | SYS | N | System Not in Use
E-SYSTEM-19 | RESERVED FOR SUBSEA USE | 19 | SYS | N | System Not in Use
E-SYSTEM-20 | PROCESS SEPARATION SYS 20 | 20 | SYS | N
E-SYSTEM-21 | PROCESS CONDENSATE HANDLING SYS 21 | 21 | SYS | N
E-SYSTEM-22 | PROCESS RECEPTION SYS 22 | 22 | SYS | N
E-SYSTEM-23 | PROCESS COMPRESSION MAIN | 23 | SYS | N
E-SYSTEM-24 | FLASH GAS COMPRESSION SYS 24 | 24 | SYS | N
E-SYSTEM-25 | GAS TREATMENT SYS 25 | 25 | SYS | N
E-SYSTEM-26 | RESERVED FOR ONSHORE USE | 26 | SYS | N | System Not in Use
E-SYSTEM-27 | GAS EXPORT SYS 27 | 27 | SYS | N
E-SYSTEM-28 | RICH MEG SYS 28 | 28 | SYS | N
E-SYSTEM-29 | LEAN MEG SYS 29 | 29 | SYS | N
E-SYSTEM-30 | MEG REGENERATION SYS 30 | 30 | SYS | N
E-SYSTEM-31 | RESERVED FOR ONSHORE USE | 31 | SYS | N | System Not in Use
E-SYSTEM-32 | RESERVED FOR ONSHORE USE | 32 | SYS | N | System Not in Use
E-SYSTEM-33 | RESERVED FOR ONSHORE USE | 33 | SYS | N | System Not in Use
E-SYSTEM-34 | RESERVED FOR ONSHORE USE | 34 | SYS | N | System Not in Use
E-SYSTEM-35 | RESERVED FOR ONSHORE USE | 35 | SYS | N | System Not in Use
E-SYSTEM-36 | RESERVED FOR ONSHORE USE | 36 | SYS | N | System Not in Use
E-SYSTEM-37 | RESERVED FOR ONSHORE USE | 37 | SYS | N | System Not in Use
E-SYSTEM-38 | RESERVED FOR ONSHORE USE | 38 | SYS | N | System Not in Use
E-SYSTEM-39 | RESERVED FOR ONSHORE USE | 39 | SYS | N | System Not in Use
E-SYSTEM-40 | LP FUEL GAS SYS 40 | 40 | SYS | N
E-SYSTEM-41 | PROCESS - HP WET FLARE | 41 | SYS | N
E-SYSTEM-42 | PROCESS - HP FLARE | 42 | SYS | N
E-SYSTEM-43 | PROCESS - VENT AND BLOW DOWN | 43 | SYS | N
E-SYSTEM-44 | PROCESS - LP FLARE | 44 | SYS | N
E-SYSTEM-45 | UTILITIES - FUEL GAS | 45 | SYS | N
E-SYSTEM-46 | UTILITIES - FUEL GAS HP | 46 | SYS | N
E-SYSTEM-47 | CHEMICALS - METHANOL INJECTION | 47 | SYS | N
E-SYSTEM-48 | CHEMICALS - CORROSION INHIBITOR INJECTION | 48 | SYS | N
E-SYSTEM-49 | CHEMICALS - KINETIC INHIBITOR INJECTION | 49 | SYS | N
E-SYSTEM-50 | CHEMICALS - REVERSE EMULSION BREAKER | 50 | SYS | N
E-SYSTEM-51 | CHEMICAL INJECTION SYS 51 | 51 | SYS | N
E-SYSTEM-52 | MEG CHEMICAL INJECTION SYS 52 | 52 | SYS | N
E-SYSTEM-53 | POTABLE WATER SYS 53 | 53 | SYS | Y
E-SYSTEM-54 | UTILITY WATER SYS 54 | 54 | SYS | Y
E-SYSTEM-55 | CHEMICALS - MISCELLANEOUS | 55 | SYS | N
E-SYSTEM-56 | DRAINS - HAZARDOUS OPEN SYS 56 | 56 | SYS | N
E-SYSTEM-57 | CLOSED DRAINS SYS 57 | 57 | SYS | N
E-SYSTEM-58 | NON-HAZARDOUS OPEN DRAINS SYS 58 | 58 | SYS | Y
E-SYSTEM-59 | SANITARY WATER SYS 59 | 59 | SYS | Y
E-SYSTEM-60 | HOT OIL SYS 60 | 60 | SYS | N
E-SYSTEM-61 | OXYGEN SCAVENGER SYS 61 | 61 | SYS | N
E-SYSTEM-62 | DIESEL SYS 62 | 62 | SYS | N
E-SYSTEM-63 | INSTRUMENT AIR SYS 63 | 63 | SYS | Y
E-SYSTEM-64 | INERT GAS SYS 64 | 64 | SYS | Y
E-SYSTEM-65 | PLANT/UTILITY AIR SYS 65 | 65 | SYS | Y
E-SYSTEM-66 | THERMAL OXIDIZER SYS 66 | 66 | SYS | N
E-SYSTEM-67 | PRODUCED WATER SYS 67 | 67 | SYS | N
E-SYSTEM-68 | RESERVED FOR ONSHORE USE | 68 | SYS | N | System Not in Use
E-SYSTEM-69 | RESERVED FOR ONSHORE USE | 69 | SYS | N | System Not in Use
E-SYSTEM-70 | RESERVED FOR ONSHORE USE | 70 | SYS | N | System Not in Use
E-SYSTEM-71 | RESERVED FOR ONSHORE USE | 71 | SYS | N | System Not in Use
E-SYSTEM-72 | RESERVED FOR ONSHORE USE | 72 | SYS | N | System Not in Use
E-SYSTEM-73 | RESERVED FOR ONSHORE USE | 73 | SYS | N | System Not in Use
E-SYSTEM-74 | RESERVED FOR ONSHORE USE | 74 | SYS | N | System Not in Use
E-SYSTEM-75 | RESERVED FOR ONSHORE USE | 75 | SYS | N | System Not in Use
E-SYSTEM-76 | ICSS - PROCESS AUTOMATION SYSTEM | 76 | SYS | N
E-SYSTEM-77 | ICSS - SAFETY INSTRUMENTED SYSTEM ESD | 77 | SYS | N
E-SYSTEM-78 | FIRE AND GAS DETECTION | 78 | SYS | N
E-SYSTEM-79 | SAFETY - FIRE FIGHTING | 79 | SYS | N
E-SYSTEM-80 | NORMAL POWER | 80 | SYS | N
E-SYSTEM-81 | FIRE WATER SYS 81 | 81 | SYS | N
E-SYSTEM-82 | UTILITIES - SEWAGE SYSTEM | 82 | SYS | Y
E-SYSTEM-83 | TELECOMS (GENERAL) | 83 | SYS | N
E-SYSTEM-84 | ESSENTIAL POWER | 84 | SYS | N
E-SYSTEM-85 | ESSENTIAL LIGTING AND SMALL POWER | 85 | SYS | N
E-SYSTEM-86 | TRACE HEATING | 86 | SYS | N
E-SYSTEM-87 | EMERGENCY POWER | 87 | SYS | N
E-SYSTEM-88 | UPS POWER | 88 | SYS | N
E-SYSTEM-89 | NORMAL LIGHTING AND SMALL POWER | 89 | SYS | N
E-SYSTEM-90 | EARTHING AND LIGHTING PROTECTION | 90 | SYS | N
E-SYSTEM-91 | POWER - MAIN GENERATION SYS 91 | 91 | SYS | N
E-SYSTEM-92 | CATHODIC PROTECTION | 92 | SYS | N
E-SYSTEM-93 | POWER MANAGEMENT SYSTEM | 93 | SYS | N
E-SYSTEM-94 | UTILITIES - HVAC | 94 | SYS | Y
E-SYSTEM-95 | ACCESS CONTROL | 95 | SYS | N
E-SYSTEM-96 | CCTV - SECURITY | 96 | SYS | N
E-SYSTEM-97 | LAN - VOIP | 97 | SYS | N
E-SYSTEM-98 | PAGA | 98 | SYS | N
E-SYSTEM-99 | RADIO SYSTEMS (INCLUDING SAT COM) | 99 | SYS | N
R-SYSTEM-00 | GENERAL / NON SPECIFIC SYSTEM SYS 00 | 00 | SYS | N
R-SYSTEM-01 | RESERVED FOR SUBSEA USE | 01 | SYS | N | System Not in Use
R-SYSTEM-02 | RESERVED FOR SUBSEA USE | 02 | SYS | N | System Not in Use
R-SYSTEM-03 | RESERVED FOR SUBSEA USE | 3 | SYS | N | System Not in Use
R-SYSTEM-04 | RESERVED FOR SUBSEA USE | 4 | SYS | N | System Not in Use
R-SYSTEM-05 | CONTROL UMBILICALS AND HPU SYS 05 | 5 | SYS | N
R-SYSTEM-06 | RESERVED FOR SUBSEA USE | 6 | SYS | N | System Not in Use
R-SYSTEM-07 | RESERVED FOR SUBSEA USE | 7 | SYS | N | System Not in Use
R-SYSTEM-08 | RESERVED FOR SUBSEA USE | 8 | SYS | N | System Not in Use
R-SYSTEM-09 | RESERVED FOR SUBSEA USE | 9 | SYS | N | System Not in Use
R-SYSTEM-10 | RESERVED FOR SUBSEA USE | 10 | SYS | N | System Not in Use
R-SYSTEM-11 | RESERVED FOR SUBSEA USE | 11 | SYS | N | System Not in Use
R-SYSTEM-12 | RESERVED FOR SUBSEA USE | 12 | SYS | N | System Not in Use
R-SYSTEM-13 | SUBSEA - WELLHEAD AND TEST SEPARATOR | 13 | SYS | N
R-SYSTEM-14 | RESERVED FOR SUBSEA USE | 14 | SYS | N | System Not in Use
R-SYSTEM-15 | RESERVED FOR SUBSEA USE | 15 | SYS | N | System Not in Use
R-SYSTEM-16 | RESERVED FOR SUBSEA USE | 16 | SYS | N | System Not in Use
R-SYSTEM-17 | RESERVED FOR SUBSEA USE | 17 | SYS | N | System Not in Use
R-SYSTEM-18 | RESERVED FOR SUBSEA USE | 18 | SYS | N | System Not in Use
R-SYSTEM-19 | RESERVED FOR SUBSEA USE | 19 | SYS | N | System Not in Use
R-SYSTEM-20 | PROCESS SEPARATION SYS 20 | 20 | SYS | N
R-SYSTEM-21 | PROCESS CONDENSATE HANDLING SYS 21 | 21 | SYS | N
R-SYSTEM-22 | PROCESS RECEPTION SYS 22 | 22 | SYS | N
R-SYSTEM-23 | PROCESS COMPRESSION MAIN | 23 | SYS | N
R-SYSTEM-24 | FLASH GAS COMPRESSION SYS 24 | 24 | SYS | N
R-SYSTEM-25 | GAS TREATMENT SYS 25 | 25 | SYS | N
R-SYSTEM-26 | RESERVED FOR ONSHORE USE | 26 | SYS | N | System Not in Use
R-SYSTEM-27 | GAS EXPORT SYS 27 | 27 | SYS | N
R-SYSTEM-28 | RICH MEG SYS 28 | 28 | SYS | N
R-SYSTEM-29 | LEAN MEG SYS 29 | 29 | SYS | N
R-SYSTEM-30 | MEG REGENERATION SYS 30 | 30 | SYS | N
R-SYSTEM-31 | RESERVED FOR ONSHORE USE | 31 | SYS | N | System Not in Use
R-SYSTEM-32 | RESERVED FOR ONSHORE USE | 32 | SYS | N | System Not in Use
R-SYSTEM-33 | RESERVED FOR ONSHORE USE | 33 | SYS | N | System Not in Use
R-SYSTEM-34 | RESERVED FOR ONSHORE USE | 34 | SYS | N | System Not in Use
R-SYSTEM-35 | RESERVED FOR ONSHORE USE | 35 | SYS | N | System Not in Use
R-SYSTEM-36 | RESERVED FOR ONSHORE USE | 36 | SYS | N | System Not in Use
R-SYSTEM-37 | RESERVED FOR ONSHORE USE | 37 | SYS | N | System Not in Use
R-SYSTEM-38 | RESERVED FOR ONSHORE USE | 38 | SYS | N | System Not in Use
R-SYSTEM-39 | RESERVED FOR ONSHORE USE | 39 | SYS | N | System Not in Use
R-SYSTEM-40 | LP FUEL GAS SYS 40 | 40 | SYS | N
R-SYSTEM-41 | PROCESS - HP WET FLARE | 41 | SYS | N
R-SYSTEM-42 | PROCESS - HP FLARE | 42 | SYS | N
R-SYSTEM-43 | PROCESS - VENT AND BLOW DOWN | 43 | SYS | N
R-SYSTEM-44 | PROCESS - LP FLARE | 44 | SYS | N
R-SYSTEM-45 | UTILITIES - FUEL GAS | 45 | SYS | N
R-SYSTEM-46 | UTILITIES - FUEL GAS HP | 46 | SYS | N
R-SYSTEM-47 | CHEMICALS - METHANOL INJECTION | 47 | SYS | N
R-SYSTEM-48 | CHEMICALS - CORROSION INHIBITOR INJECTION | 48 | SYS | N
R-SYSTEM-49 | CHEMICALS - KINETIC INHIBITOR INJECTION | 49 | SYS | N
R-SYSTEM-50 | CHEMICALS - REVERSE EMULSION BREAKER | 50 | SYS | N
R-SYSTEM-51 | CHEMICAL INJECTION SYS 51 | 51 | SYS | N
R-SYSTEM-52 | MEG CHEMICAL INJECTION SYS 52 | 52 | SYS | N
R-SYSTEM-53 | POTABLE WATER SYS 53 | 53 | SYS | Y
R-SYSTEM-54 | UTILITY WATER SYS 54 | 54 | SYS | Y
R-SYSTEM-55 | CHEMICALS - MISCELLANEOUS | 55 | SYS | N
R-SYSTEM-56 | DRAINS - HAZARDOUS OPEN SYS 56 | 56 | SYS | N
R-SYSTEM-57 | CLOSED DRAINS SYS 57 | 57 | SYS | N
R-SYSTEM-58 | NON-HAZARDOUS OPEN DRAINS SYS 58 | 58 | SYS | Y
R-SYSTEM-59 | SANITARY WATER SYS 59 | 59 | SYS | Y
R-SYSTEM-60 | HOT OIL SYS 60 | 60 | SYS | N
R-SYSTEM-61 | OXYGEN SCAVENGER SYS 61 | 61 | SYS | N
R-SYSTEM-62 | DIESEL SYS 62 | 62 | SYS | N
R-SYSTEM-63 | INSTRUMENT AIR SYS 63 | 63 | SYS | Y
R-SYSTEM-64 | INERT GAS SYS 64 | 64 | SYS | Y
R-SYSTEM-65 | PLANT/UTILITY AIR SYS 65 | 65 | SYS | Y
R-SYSTEM-66 | THERMAL OXIDIZER SYS 66 | 66 | SYS | N
R-SYSTEM-67 | PRODUCED WATER SYS 67 | 67 | SYS | N
R-SYSTEM-68 | RESERVED FOR ONSHORE USE | 68 | SYS | N | System Not in Use
R-SYSTEM-69 | RESERVED FOR ONSHORE USE | 69 | SYS | N | System Not in Use
R-SYSTEM-70 | RESERVED FOR ONSHORE USE | 70 | SYS | N | System Not in Use
R-SYSTEM-71 | RESERVED FOR ONSHORE USE | 71 | SYS | N | System Not in Use
R-SYSTEM-72 | RESERVED FOR ONSHORE USE | 72 | SYS | N | System Not in Use
R-SYSTEM-73 | RESERVED FOR ONSHORE USE | 73 | SYS | N | System Not in Use
R-SYSTEM-74 | RESERVED FOR ONSHORE USE | 74 | SYS | N | System Not in Use
R-SYSTEM-75 | RESERVED FOR ONSHORE USE | 75 | SYS | N | System Not in Use
R-SYSTEM-76 | ICSS - PROCESS AUTOMATION SYSTEM | 76 | SYS | N
R-SYSTEM-77 | ICSS - SAFETY INSTRUMENTED SYSTEM ESD | 77 | SYS | N
R-SYSTEM-78 | FIRE AND GAS DETECTION | 78 | SYS | N
R-SYSTEM-79 | SAFETY - FIRE FIGHTING | 79 | SYS | N
R-SYSTEM-80 | NORMAL POWER | 80 | SYS | N
R-SYSTEM-81 | FIRE WATER SYS 81 | 81 | SYS | N
R-SYSTEM-82 | UTILITIES - SEWAGE SYSTEM | 82 | SYS | Y
R-SYSTEM-83 | TELECOMS (GENERAL) | 83 | SYS | N
R-SYSTEM-84 | ESSENTIAL POWER | 84 | SYS | N
R-SYSTEM-85 | ESSENTIAL LIGTING AND SMALL POWER | 85 | SYS | N
R-SYSTEM-86 | TRACE HEATING | 86 | SYS | N
R-SYSTEM-87 | EMERGENCY POWER | 87 | SYS | N
R-SYSTEM-88 | UPS POWER | 88 | SYS | N
R-SYSTEM-89 | NORMAL LIGHTING AND SMALL POWER | 89 | SYS | N
R-SYSTEM-90 | EARTHING AND LIGHTING PROTECTION | 90 | SYS | N
R-SYSTEM-91 | POWER - MAIN GENERATION SYS 91 | 91 | SYS | N
R-SYSTEM-92 | CATHODIC PROTECTION | 92 | SYS | N
R-SYSTEM-93 | POWER MANAGEMENT SYSTEM | 93 | SYS | N
R-SYSTEM-94 | UTILITIES - HVAC | 94 | SYS | Y
R-SYSTEM-95 | ACCESS CONTROL | 95 | SYS | N
R-SYSTEM-96 | CCTV - SECURITY | 96 | SYS | N
R-SYSTEM-97 | LAN - VOIP | 97 | SYS | N
R-SYSTEM-98 | PAGA | 98 | SYS | N
R-SYSTEM-99 | RADIO SYSTEMS (INCLUDING SAT COM) | 99 | SYS | N

## Systems(Old)
Table extracted and cleaned from EG001-DM-SPE-00-0012-B14.docx
System # | Proposed Revised System Description For Rosetta & Rosetta East inc Subsea Facilities | Notes | Comment | FluidType | Primary function | LossOfSystemImpact
0 | General / Non specific System | Applicable to Legend sheets, Cause & Effect docs Interconnecting P+IDs between Existing Rosetta & New Rosetta East facilities |  | Not Applicable
1 | Reserved For Subsea Use |  |  | Not Applicable
2 | Reserved For Subsea Use |  |  | Not Applicable
3 | Reserved For Subsea Use |  |  | Not Applicable
4 | Reserved For Subsea Use |  |  | Not Applicable
5 | Subsea - Control Umbilicals | Includes Onshore HPU, Umbilicals & Umbilical Terminatiion Units |  | Hydraulic | Containment Hydraulic Fluid
6 | Reserved For Subsea Use |  |  | Not Applicable
7 | Reserved For Subsea Use |  |  | Not Applicable
8 | Reserved For Subsea Use |  |  | Not Applicable
9 | Reserved For Subsea Use |  |  | Not Applicable
10 | Reserved For Subsea Use |  |  | Not Applicable
11 | Reserved For Subsea Use |  |  | Not Applicable
12 | Reserved For Subsea Use |  |  | Not Applicable
13 | Subsea - Wellhead & test separator | Only applicable to Existing subsea facilities feeding into Existing Rosetta Facility |  | Hydrocarbons | Primary Containment Hydrocarbons
14 | Reserved For Subsea Use |  |  | Not Applicable
15 | Reserved For Subsea Use |  |  | Not Applicable
16 | Reserved For Subsea Use |  |  | Not Applicable
17 | Reserved For Subsea Use |  |  | Not Applicable
18 | Reserved For Subsea Use |  |  | Not Applicable
19 | Reserved For Subsea Use |  |  | Not Applicable
20 | Process - Separation |  |  | Hydrocarbons | Primary Containment Hydrocarbons
21 | Process - Condensate handling | Including Treatment, Metering Storage & Export. |  | Hydrocarbons | Primary Containment Hydrocarbons
22 | Process Reception | Pigging, Slug Catchers & ESD Skids |  | Hydrocarbons | Primary Containment Hydrocarbons
23 | Process - Compression Main |  |  | Hydrocarbons | Primary Containment Hydrocarbons
24 | Process - Compression Flash Gas | Newly Assigned (Bechtel) |  | Hydrocarbons | Primary Containment Hydrocarbons
25 | Process - Gas Treatment |  |  | Hydrocarbons | Primary Containment Hydrocarbons
26 | Reserved For Onshore Use |  |  | Not Applicable
27 | Process - Gas Export | Including Export Metering |  | Hydrocarbons | Primary Containment Hydrocarbons
28 | Chemicals - Rich MEG Injection | Newly Assigned (Bechtel) |  | Process Chemicals
29 | Chemicals - Lean MEG | Newly Assigned (Bechtel) |  | Process Chemicals
30 | MEG Regeneation | Newly Assigned (Bechtel) |  | Process Chemicals
31 | Reserved For Onshore Use |  |  | Not Applicable
32 | Reserved For Onshore Use |  |  | Not Applicable
33 | Reserved For Onshore Use |  |  | Not Applicable
34 | Reserved For Onshore Use |  |  | Not Applicable
35 | Reserved For Onshore Use |  |  | Not Applicable
36 | Reserved For Onshore Use |  |  | Not Applicable
37 | Reserved For Onshore Use |  |  | Not Applicable
38 | Reserved For Onshore Use |  |  | Not Applicable
39 | Reserved For Onshore Use |  |  | Not Applicable
40 | Utilities - Fuel Gas LP |  |  | Hydrocarbons | Primary Containment Hydrocarbons
41 | Process - HP Wet Flare | Only Applicable to EXISTING Rosetta. |  | Hydrocarbons | Primary Containment Hydrocarbons
42 | Process - HP Flare |  |  | Hydrocarbons | Primary Containment Hydrocarbons
43 | Process - Vent and Blow Down |  |  | Hydrocarbons | Primary Containment Hydrocarbons
44 | Process - LP Flare |  |  | Hydrocarbons | Primary Containment Hydrocarbons
45 | Utilities - Fuel Gas |  |  | Hydrocarbons | Primary Containment Hydrocarbons
46 | Utilities - Fuel Gas HP |  |  | Hydrocarbons | Primary Containment Hydrocarbons
47 | Chemicals - Methanol Injection |  |  | Injection Chemicals
48 | Chemicals - Corrosion Inhibitor Injection |  | Suggest this is not renamed from "Corrosion Inhibitor Injection" to "G-F Chemical Injection" per Bechtel proposal. | Injection Chemicals
49 | Chemicals - Kinetic Inhibitor Injection | Only Applicable to EXISTING Rosetta. |  | Injection Chemicals
50 | Chemicals - Reverse Emulsion Breaker | Only Applicable to EXISTING Rosetta. |  | Injection Chemicals
51 | Chemicals - Chemical Injection | Newly Assigned (Bechtel) |  | Injection Chemicals
52 | Chemicals - MEG Injection | Newly Assigned (Bechtel) |  | Injection Chemicals
53 | Utilities - Water - Fresh/ Potable |  |  | Water
54 | Utilities - Water - Utility |  |  | Water
55 | Chemicals - Miscellaneous | Newly Assigned (Bechtel) |  | Injection Chemicals
56 | Drains - Hazardous open |  |  | Hydrocarbons
57 | Drains - Closed |  |  | Hydrocarbons
58 | Drains - Non-Hazardous open |  |  | Drains
59 | Utilities - Water - Sanitary | Newly Assigned (Bechtel) |  | Water
60 | Utilities - Hot Oil | Newly Assigned (Bechtel) |  | Hydrocarbons
61 | Chemicals - Oxygen scavenger | Newly Assigned (Bechtel) - O2 scavenger for MEG see system 52 |  | Injection Chemicals
62 | Utilities - Diesel |  |  | Hydrocarbons
63 | Utilities - Instrument Air |  |  | Compressed Air
64 | Utilities - Inert Gas | Inert Gas = Nitrogen |  | Nitrogen
65 | Utilities - Plant / Utility Air |  |  | Compressed Air
66 | Thermal Oxidizer | Newly Assigned (Bechtel) |  | Injection Chemicals
67 | Water - Produced | Newly Assigned (Bechtel) |  | Water
68 | Reserved For Onshore Use |  |  | Not Applicable
69 | Reserved For Onshore Use |  |  | Not Applicable
70 | Reserved For Onshore Use |  |  | Not Applicable
71 | Reserved For Onshore Use |  |  | Not Applicable
72 | Reserved For Onshore Use |  |  | Not Applicable
73 | Reserved For Onshore Use |  |  | Not Applicable
74 | Reserved For Onshore Use |  |  | Not Applicable
75 | Reserved For Onshore Use |  |  | Not Applicable
76 | ICSS - Process Automation System |  |  | Not Applicable | Process Control
77 | ICSS - Safety Instrumented SystemESD |  |  | Not Applicable | Process Control
78 | Fire & Gas Detection | Includes Control Panels, Field Detection Devices |  | Not Applicable | Fire & Explosion protection
79 | Safety - Fire Fighting | Portable Fire Fighting Equipment |  | Not Applicable | Fire & Explosion protection
80 | Normal Power | Applicable to both EXISTING Rosetta and New Rosetta East Facilities. Note this also includes Main Generation on the existing Rosetta Facility. |  | Not Applicable | Power
81 | Safety - Fire Water System |  | Potential to separate:- Foam system, Deluge system, Inert Gas Suppression System from Fire Water System | Firewater | Fire & Explosion protection
82 | Utilities - Sewage system |  |  | Water
83 | Telecoms (General) | Newly Assigned (Bechtel) |  | Not Applicable | Communications
84 | Essential Power | Applicable to EXISTING Rosetta Facilities Only. |  | Not Applicable | Emergency systems
85 | Essential Lighting & Small Power |  |  | Not Applicable | Emergency systems
86 | Trace Heating |  | Applicable to NEW trace heating on Rosetta and Rosetta East. | Not Applicable | Condensation prevention
87 | Emergency Power | Includes Generation & Distribution | Applicable to Rosetta East Only | Not Applicable | Emergency systems
88 | UPS Power | Includes Generation & Distribution |  | Not Applicable | Emergency systems
89 | Normal Lighting & Small Power | Distribution inc consumers |  | Not Applicable | Power
90 | Earthing & Lightning Protection | Inc Lightning protection, power system earthing, and Inst earth systems | Applicable to Rosetta East Only | Not Applicable | Earthing
91 | Power - Main Generation | Newly Assigned (Bechtel) | Only applicable to Rosetta East | Not Applicable | Power
92 | Cathodic Protection | Newly Assigned (Bechtel) |  | Not Applicable | Fabric Protection
93 | Power Management System |  | Applicable to Rosetta and Rosetta East Facilities | Not Applicable | Power
94 | Utilities - HVAC |  |  | Air | HVAC
95 | Access Control | Newly Assigned (Bechtel) |  | Not Applicable
96 | CCTV - Security | Newly Assigned (Bechtel) |  | Not Applicable
97 | LAN - VoIP | Newly Assigned (Bechtel) |  | Not Applicable
98 | PAGA | Newly Assigned (Bechtel) |  | Not Applicable | Emergency systems
99 | Radio Systems (Including Sat Com) | Newly Assigned (Bechtel) |  | Not Applicable | Emergency systems

## FA_CFBC
Failure Code | FA_CFBC |  |  |  | Number of Locations in failure code when defaults assigned: | 4 |  | Final Criticality Code |  | B
Description | CONTROL ROOM
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 3 | 6 |  | Redundancy applies? | No
Environmental | H | 3 | 3 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | H | 3 | 3 |  |  | 2 |  | Annex D Mappings | S | B
Business | H | 3 | 3 |  |  | 2 |  |  | E | C
[6 empty] | 2 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 3 | 6 | 69 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 3 | 3 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 3 | 3 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 3 | 3 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_CFSGW
Failure Code | FA_CFSGW |  |  |  | Number of Locations in failure code when defaults assigned: | 5 |  | Final Criticality Code |  | B
Description | WALL OR FENCE
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4
Safety | G | 6 | 7 |  | Redundancy applies? | No
Environmental | H | 6 | 6 |  | Elements contributing to CMMS Location Criticality rating | 4 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | H | 6 | 6 |  |  | 2 |  | Annex D Mappings | S | B
Business | H | 6 | 6 |  |  | 2 |  |  | E | C
[6 empty] | 2 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | G | 6 | 7 | 71 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 6 | 6 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 6 | 6 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 6 | 6 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_CFSSE
Failure Code | FA_CFSSE |  |  |  | Number of Locations in failure code when defaults assigned: | 104 |  | Final Criticality Code |  | A
Description | EQUIPMENT SUPPORT STRUCTURE
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 5 | 8 |  | Redundancy applies? | No
Environmental | H | 5 | 5 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | H | 5 | 5 |  |  | 2 |  | Annex D Mappings | S | A
Business | G | 5 | 6 |  |  | 2 |  |  | E | C
[6 empty] | 4 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 5 | 8 | 69 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P4 ¦ Process Containment Integrity ¦ All other supports, paint and bolting |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | Non hazardous system supports, unknown systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 5 | 6 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_CFSSF
Failure Code | FA_CFSSF |  |  |  | Number of Locations in failure code when defaults assigned: | 19 |  | Final Criticality Code |  | B
Description | STRUCTURAL FOUNDATION
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 6
Safety | F | 5 | 7 |  | Redundancy applies? | No
Environmental | H | 5 | 5 |  | Elements contributing to CMMS Location Criticality rating | 6 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | H | 5 | 5 |  |  | 2 |  | Annex D Mappings | S | B
Business | H | 5 | 5 |  |  | 2 |  |  | E | C
[6 empty] | 2 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | F | 5 | 7 | 70 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P2 ¦ Structural Integrity ¦ Secondary Structures - Single component failure has no immediate consequence |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | Support for non-hazardous system, unknown systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_CFSST
Failure Code | FA_CFSST |  |  |  | Number of Locations in failure code when defaults assigned: | 907 |  | Final Criticality Code |  | A
Description | STRUCTURAL BASE
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 7 | 10 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | H | 7 | 7 |  |  | 2 |  | Annex D Mappings | S | A
Business | G | 7 | 8 |  |  | 2 |  |  | E | C
[6 empty] | 4 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 7 | 10 | 69 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P2 ¦ Structural Integrity ¦ Secondary Structures - Single component failure has no immediate consequence |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | Support for non-hazardous system, unknown systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_EECF
Failure Code | FA_EECF |  |  |  | Number of Locations in failure code when defaults assigned: | 398 |  | Final Criticality Code |  | A
Description | LIGHT FITTING
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 7 | 10 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | H | 7 | 7 |  |  | 2 |  | Annex D Mappings | S | A
Business | H | 7 | 7 |  |  | 2 |  |  | E | C
[6 empty] | 2 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 7 | 10 | 69 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_EECH
Failure Code | FA_EECH |  |  |  | Number of Locations in failure code when defaults assigned: | 109 |  | Final Criticality Code |  | A
Description | ELECTRIC HEATER
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 6 | 9 |  | Redundancy applies? | No
Environmental | H | 6 | 6 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | F | 6 | 8 |  |  | 2 |  | Annex D Mappings | S | A
Business | H | 6 | 6 |  |  | 6 |  |  | E | C
[6 empty] | 2 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 6 | 9 | 69 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | system 64
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 6 | 8 | 70 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_EECMD
Failure Code | FA_EECMD |  |  |  | Number of Locations in failure code when defaults assigned: | 7 |  | Final Criticality Code |  | A
Description | DC ELECTRIC MOTOR
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 6 | 9 |  | Redundancy applies? | No
Environmental | H | 6 | 6 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | F | 6 | 8 |  |  | 2 |  | Annex D Mappings | S | A
Business | H | 6 | 6 |  |  | 6 |  |  | E | C
[6 empty] | 2 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 6 | 9 | 69 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 6 | 8 | 70 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_EECMI
Failure Code | FA_EECMI |  |  |  | Number of Locations in failure code when defaults assigned: | 466 |  | Final Criticality Code |  | A
Description | AC INDUCTION ELECTRIC MOTOR
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 6 | 9 |  | Redundancy applies? | No
Environmental | H | 6 | 6 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | F | 6 | 8 |  |  | 2 |  | Annex D Mappings | S | A
Business | H | 6 | 6 |  |  | 6 |  |  | E | C
[6 empty] | 2 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 6 | 9 | 69 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | M4 ¦ Ignition Prevention ¦ For Equipment in Zone 2 |  |  | B
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | Non-priority induction motors
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 6 | 8 | 70 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_EECMS
Failure Code | FA_EECMS |  |  |  | Number of Locations in failure code when defaults assigned: | 1 |  | Final Criticality Code |  | A
Description | AC SYNCHRONOUS ELECTRIC MOTOR
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 6 | 9 |  | Redundancy applies? | No
Environmental | H | 6 | 6 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | F | 6 | 8 |  |  | 2 |  | Annex D Mappings | S | A
Business | H | 6 | 6 |  |  | 6 |  |  | E | C
[6 empty] | 2 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 6 | 9 | 69 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 6 | 8 | 70 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_EECO
Failure Code | FA_EECO |  |  |  | Number of Locations in failure code when defaults assigned: | 21 |  | Final Criticality Code |  | B
Description | ELECTRIC SOCKET OUTLET
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4
Safety | G | 6 | 7 |  | Redundancy applies? | No
Environmental | H | 6 | 6 |  | Elements contributing to CMMS Location Criticality rating | 4 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | H | 6 | 6 |  |  | 2 |  | Annex D Mappings | S | B
Business | H | 6 | 6 |  |  | 2 |  |  | E | C
[6 empty] | 2 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | G | 6 | 7 | 71 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 6 | 6 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 6 | 6 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 6 | 6 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_EECT
Failure Code | FA_EECT |  |  |  | Number of Locations in failure code when defaults assigned: | 2 |  | Final Criticality Code |  | B
Description | TRACE HEATING CIRCUIT
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4
Safety | G | 6 | 7 |  | Redundancy applies? | No
Environmental | H | 6 | 6 |  | Elements contributing to CMMS Location Criticality rating | 4 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | H | 6 | 6 |  |  | 2 |  | Annex D Mappings | S | B
Business | G | 6 | 7 |  |  | 2 |  |  | E | C
[6 empty] | 4 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | G | 6 | 7 | 71 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 6 | 6 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 6 | 6 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 6 | 7 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_EEPBA
Failure Code | FA_EEPBA |  |  |  | Number of Locations in failure code when defaults assigned: | 868 |  | Final Criticality Code |  | A
Description | AIR CIRCUIT BREAKER
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 6 | 9 |  | Redundancy applies? | No
Environmental | H | 6 | 6 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | F | 6 | 8 |  |  | 2 |  | Annex D Mappings | S | A
Business | H | 6 | 6 |  |  | 6 |  |  | E | C
[6 empty] | 2 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 6 | 9 | 69 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 6 | 8 | 70 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_EEPBV
Failure Code | FA_EEPBV |  |  |  | Number of Locations in failure code when defaults assigned: | 48 |  | Final Criticality Code |  | A
Description | VACUUM CIRCUIT BREAKER
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 6 | 9 |  | Redundancy applies? | No
Environmental | H | 6 | 6 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | F | 6 | 8 |  |  | 2 |  | Annex D Mappings | S | A
Business | H | 6 | 6 |  |  | 6 |  |  | E | C
[6 empty] | 2 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 6 | 9 | 69 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 6 | 8 | 70 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_EEPCS
Failure Code | FA_EEPCS |  |  |  | Number of Locations in failure code when defaults assigned: | 109 |  | Final Criticality Code |  | C
Description | SACRIFICIAL ANODE
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4
Safety | H | 5 | 5 |  | Redundancy applies? | No
Environmental | H | 5 | 5 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | C
Production | H | 5 | 5 |  |  | 2 |  | Annex D Mappings | S | C
Business | G | 5 | 6 |  |  | 2 |  |  | E | C
[6 empty] | 4 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 5 | 6 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_EEPNE
Failure Code | FA_EEPNE |  |  |  | Number of Locations in failure code when defaults assigned: | 118 |  | Final Criticality Code |  | B
Description | EARTHING BAR
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 6
Safety | F | 6 | 8 |  | Redundancy applies? | No
Environmental | H | 6 | 6 |  | Elements contributing to CMMS Location Criticality rating | 6 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | G | 6 | 7 |  |  | 2 |  | Annex D Mappings | S | B
Business | G | 6 | 7 |  |  | 4 |  |  | E | C
[6 empty] | 4 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | F | 6 | 8 | 70 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 6 | 6 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 6 | 7 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 6 | 7 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_EEPNN
Failure Code | FA_EEPNN |  |  |  | Number of Locations in failure code when defaults assigned: | 8 |  | Final Criticality Code |  | A
Description | NEUTRAL GROUND RESISTOR
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 6 | 9 |  | Redundancy applies? | No
Environmental | H | 6 | 6 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | F | 6 | 8 |  |  | 2 |  | Annex D Mappings | S | A
Business | G | 6 | 7 |  |  | 6 |  |  | E | C
[6 empty] | 4 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 6 | 9 | 69 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 6 | 6 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 6 | 8 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 6 | 7 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_EEPS
Failure Code | FA_EEPS |  |  |  | Number of Locations in failure code when defaults assigned: | 221 |  | Final Criticality Code |  | A
Description | START / STOP SWITCH
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 6 | 9 |  | Redundancy applies? | No
Environmental | H | 6 | 6 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | F | 6 | 8 |  |  | 2 |  | Annex D Mappings | S | A
Business | H | 6 | 6 |  |  | 6 |  |  | E | C
[6 empty] | 2 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 6 | 9 | 69 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable |  |  | B
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | system 59,65 are utility. Same maintenance schedule all criticalities
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 6 | 8 | 70 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_EEPU
Failure Code | FA_EEPU |  |  |  | Number of Locations in failure code when defaults assigned: | 29 |  | Final Criticality Code |  | A
Description | UNINTERRUPTIBLE POWER SUPPLY
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10
Safety | D | 7 | 11 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | F | 7 | 9 |  |  | 2 |  | Annex D Mappings | S | A
Business | F | 7 | 9 |  |  | 6 |  |  | E | C
[6 empty] | 6 |  |  | P | A
Risk Matrix Population Inputs | [8 empty] | B | A
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | D | 7 | 11 | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 7 | 9 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | F | 7 | 9 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_EETA
Failure Code | FA_EETA |  |  |  | Number of Locations in failure code when defaults assigned: | 6 |  | Final Criticality Code |  | A
Description | REACTOR / INDUCTOR
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 5 | 8 |  | Redundancy applies? | No
Environmental | H | 5 | 5 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | F | 5 | 7 |  |  | 2 |  | Annex D Mappings | S | A
Business | F | 5 | 7 |  |  | 6 |  |  | E | C
[6 empty] | 6 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 5 | 8 | 69 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 5 | 7 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | F | 5 | 7 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_EETB
Failure Code | FA_EETB |  |  |  | Number of Locations in failure code when defaults assigned: | 39 |  | Final Criticality Code |  | A
Description | BATTERY
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 7 | 10 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | F | 7 | 9 |  |  | 2 |  | Annex D Mappings | S | A
Business | F | 7 | 9 |  |  | 6 |  |  | E | C
[6 empty] | 6 |  |  | P | A
Risk Matrix Population Inputs | [8 empty] | B | A
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 7 | 10 | 69 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 7 | 9 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | F | 7 | 9 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_EETC
Failure Code | FA_EETC |  |  |  | Number of Locations in failure code when defaults assigned: | 57 |  | Final Criticality Code |  | A
Description | BATTERY CHARGER
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 7 | 10 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | F | 7 | 9 |  |  | 2 |  | Annex D Mappings | S | A
Business | F | 7 | 9 |  |  | 6 |  |  | E | C
[6 empty] | 6 |  |  | P | A
Risk Matrix Population Inputs | [8 empty] | B | A
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 7 | 10 | 69 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 7 | 9 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | F | 7 | 9 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_EETD
Failure Code | FA_EETD |  |  |  | Number of Locations in failure code when defaults assigned: | 70 |  | Final Criticality Code |  | C
Description | BUS DUCT / BUS BAR
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 6
Safety | F | 3 | 5 |  | Redundancy applies? | No
Environmental | H | 3 | 3 |  | Elements contributing to CMMS Location Criticality rating | 6 |  | Derived SAP A/B/C (highest wins) = |  | C
Production | F | 3 | 5 |  |  | 2 |  | Annex D Mappings | S | C
Business | G | 3 | 4 |  |  | 6 |  |  | E | C
[6 empty] | 4 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | F | 3 | 5 | 70 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 3 | 3 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 3 | 5 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 3 | 4 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_EETFW
Failure Code | FA_EETFW |  |  |  | Number of Locations in failure code when defaults assigned: | 20 |  | Final Criticality Code |  | B
Description | WET TRANSFORMER
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 6
Safety | H | 4 | 4 |  | Redundancy applies? | No
Environmental | H | 4 | 4 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | F | 4 | 6 |  |  | 2 |  | Annex D Mappings | S | C
Business | F | 4 | 6 |  |  | 6 |  |  | E | C
[6 empty] | 6 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 4 | 4 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 4 | 4 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 4 | 6 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | F | 4 | 6 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_EETGA
Failure Code | FA_EETGA |  |  |  | Number of Locations in failure code when defaults assigned: | 10 |  | Final Criticality Code |  | B
Description | AC ELECTRIC GENERATOR
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 6
Safety | G | 5 | 6 |  | Redundancy applies? | No
Environmental | H | 5 | 5 |  | Elements contributing to CMMS Location Criticality rating | 4 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | F | 5 | 7 |  |  | 2 |  | Annex D Mappings | S | C
Business | G | 5 | 6 |  |  | 6 |  |  | E | C
[6 empty] | 4 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | G | 5 | 6 | 71 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 5 | 7 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 5 | 6 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_EETI
Failure Code | FA_EETI |  |  |  | Number of Locations in failure code when defaults assigned: | 25 |  | Final Criticality Code |  | B
Description | ELECTRIC ISOLATOR
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4
Safety | G | 6 | 7 |  | Redundancy applies? | No
Environmental | H | 6 | 6 |  | Elements contributing to CMMS Location Criticality rating | 4 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | H | 6 | 6 |  |  | 2 |  | Annex D Mappings | S | B
Business | H | 6 | 6 |  |  | 2 |  |  | E | C
[6 empty] | 2 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | G | 6 | 7 | 71 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 6 | 6 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 6 | 6 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 6 | 6 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_EETM
Failure Code | FA_EETM |  |  |  | Number of Locations in failure code when defaults assigned: | 910 |  | Final Criticality Code |  | A
Description | MOTOR CONTROL CENTER
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 6 | 9 |  | Redundancy applies? | No
Environmental | H | 6 | 6 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | F | 6 | 8 |  |  | 2 |  | Annex D Mappings | S | A
Business | H | 6 | 6 |  |  | 6 |  |  | E | C
[6 empty] | 2 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 6 | 9 | 69 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 6 | 8 | 70 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_EETO
Failure Code | FA_EETO |  |  |  | Number of Locations in failure code when defaults assigned: | 5 |  | Final Criticality Code |  | A
Description | POWER / CONTROL MODULE
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 6 | 9 |  | Redundancy applies? | No
Environmental | H | 6 | 6 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | F | 6 | 8 |  |  | 2 |  | Annex D Mappings | S | A
Business | H | 6 | 6 |  |  | 6 |  |  | E | C
[6 empty] | 2 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 6 | 9 | 69 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 6 | 8 | 70 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_EETP
Failure Code | FA_EETP |  |  |  | Number of Locations in failure code when defaults assigned: | 3 |  | Final Criticality Code |  | B
Description | ELECTRICAL PANEL
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 4 | 7 |  | Redundancy applies? | No
Environmental | H | 4 | 4 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | F | 4 | 6 |  |  | 2 |  | Annex D Mappings | S | B
Business | F | 4 | 6 |  |  | 6 |  |  | E | C
[6 empty] | 6 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 4 | 7 | 69 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 4 | 4 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 4 | 6 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | F | 4 | 6 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_EETQ
Failure Code | FA_EETQ |  |  |  | Number of Locations in failure code when defaults assigned: | 64 |  | Final Criticality Code |  | A
Description | VARIABLE FREQUENCY DRIVE
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 6 | 9 |  | Redundancy applies? | No
Environmental | H | 6 | 6 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | F | 6 | 8 |  |  | 2 |  | Annex D Mappings | S | A
Business | H | 6 | 6 |  |  | 6 |  |  | E | C
[6 empty] | 2 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 6 | 9 | 69 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 6 | 8 | 70 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_EETR
Failure Code | FA_EETR |  |  |  | Number of Locations in failure code when defaults assigned: | 15 |  | Final Criticality Code |  | B
Description | POWER RECTIFIER
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 6
Safety | H | 4 | 4 |  | Redundancy applies? | No
Environmental | H | 4 | 4 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | F | 4 | 6 |  |  | 2 |  | Annex D Mappings | S | C
Business | F | 4 | 6 |  |  | 6 |  |  | E | C
[6 empty] | 6 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 4 | 4 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 4 | 4 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 4 | 6 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | F | 4 | 6 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_EETW
Failure Code | FA_EETW |  |  |  | Number of Locations in failure code when defaults assigned: | 170 |  | Final Criticality Code |  | A
Description | SWITCHGEAR
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 6 | 9 |  | Redundancy applies? | No
Environmental | H | 6 | 6 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | F | 6 | 8 |  |  | 2 |  | Annex D Mappings | S | A
Business | H | 6 | 6 |  |  | 6 |  |  | E | C
[6 empty] | 2 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 6 | 9 | 69 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable |  |  | B
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | system 94 tags are utility
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 6 | 8 | 70 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_EETY
Failure Code | FA_EETY |  |  |  | Number of Locations in failure code when defaults assigned: | 28 |  | Final Criticality Code |  | B
Description | POWER SUPPLY
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 4 | 7 |  | Redundancy applies? | No
Environmental | H | 4 | 4 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | F | 4 | 6 |  |  | 2 |  | Annex D Mappings | S | B
Business | H | 4 | 4 |  |  | 6 |  |  | E | C
[6 empty] | 2 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 4 | 7 | 69 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 4 | 4 | 72 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 4 | 6 | 70 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 4 | 4 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_INAM
Failure Code | FA_INAM |  |  |  | Number of Locations in failure code when defaults assigned: | 17 |  | Final Criticality Code |  | B
Description | FLOW METER
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4
Safety | H | 6 | 6 |  | Redundancy applies? | No
Environmental | H | 6 | 6 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | G | 6 | 7 |  |  | 2 |  | Annex D Mappings | S | C
Business | H | 6 | 6 |  |  | 4 |  |  | E | C
[6 empty] | 2 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 6 | 7 | 71 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_INAP
Failure Code | FA_INAP |  |  |  | Number of Locations in failure code when defaults assigned: | 10 |  | Final Criticality Code |  | B
Description | SAMPLER
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4
Safety | H | 7 | 7 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | H | 7 | 7 |  |  | 2 |  | Annex D Mappings | S | C
Business | G | 7 | 8 |  |  | 2 |  |  | E | C
[6 empty] | 4 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_INDC
Failure Code | FA_INDC |  |  |  | Number of Locations in failure code when defaults assigned: | 9 |  | Final Criticality Code |  | B
Description | LOCAL CONTROLLER
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 6
Safety | H | 6 | 6 |  | Redundancy applies? | No
Environmental | H | 6 | 6 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | F | 6 | 8 |  |  | 2 |  | Annex D Mappings | S | C
Business | H | 6 | 6 |  |  | 6 |  |  | E | C
[6 empty] | 2 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 6 | 8 | 70 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_INDFD
Failure Code | FA_INDFD |  |  |  | Number of Locations in failure code when defaults assigned: | 20 |  | Final Criticality Code |  | A
Description | DAMPER
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 8 | 11 |  | Redundancy applies? | No
Environmental | H | 8 | 8 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | H | 8 | 8 |  |  | 2 |  | Annex D Mappings | S | A
Business | G | 8 | 9 |  |  | 2 |  |  | E | C
[6 empty] | 4 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 8 | 11 | 69 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 8 | 8 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 8 | 8 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 8 | 9 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_INDFS
Failure Code | FA_INDFS |  |  |  | Number of Locations in failure code when defaults assigned: | 230 |  | Final Criticality Code |  | B
Description | SOLENOID VALVE
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 6
Safety | H | 6 | 6 |  | Redundancy applies? | No
Environmental | H | 6 | 6 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | F | 6 | 8 |  |  | 2 |  | Annex D Mappings | S | C
Business | H | 6 | 6 |  |  | 6 |  |  | E | C
[6 empty] | 2 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable |  |  | B
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | systems 63,64,65
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 6 | 8 | 70 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_INDI
Failure Code | FA_INDI |  |  |  | Number of Locations in failure code when defaults assigned: | 1479 |  | Final Criticality Code |  | C
Description | INDICATOR
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 2
Safety | H | 7 | 7 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | C
Production | H | 7 | 7 |  |  | 2 |  | Annex D Mappings | S | C
Business | H | 7 | 7 |  |  | 2 |  |  | E | C
[6 empty] | 2 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | Escalate SIS, otherwise no MAH allocated
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_INDMS
Failure Code | FA_INDMS |  |  |  | Number of Locations in failure code when defaults assigned: | 1691 |  | Final Criticality Code |  | B
Description | SENSING ELEMENT
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 6
Safety | H | 6 | 6 |  | Redundancy applies? | No
Environmental | H | 6 | 6 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | F | 6 | 8 |  |  | 2 |  | Annex D Mappings | S | C
Business | H | 6 | 6 |  |  | 6 |  |  | E | C
[6 empty] | 2 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable |  |  | B
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 6 | 8 | 70 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_INDMT
Failure Code | FA_INDMT |  |  |  | Number of Locations in failure code when defaults assigned: | 2715 |  | Final Criticality Code |  | B
Description | TRANSMITTER
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 6
Safety | H | 5 | 5 |  | Redundancy applies? | No
Environmental | H | 5 | 5 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | F | 5 | 7 |  |  | 2 |  | Annex D Mappings | S | C
Business | H | 5 | 5 |  |  | 6 |  |  | E | C
[6 empty] | 2 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 5 | 5 | 72 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable |  |  | B
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 5 | 5 | 72 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 5 | 7 | 70 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 5 | 5 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_INDS
Failure Code | FA_INDS |  |  |  | Number of Locations in failure code when defaults assigned: | 1553 |  | Final Criticality Code |  | B
Description | INSTRUMENT SWITCH
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 6
Safety | H | 6 | 6 |  | Redundancy applies? | No
Environmental | H | 6 | 6 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | F | 6 | 8 |  |  | 2 |  | Annex D Mappings | S | C
Business | H | 6 | 6 |  |  | 6 |  |  | E | C
[6 empty] | 2 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable |  |  | B
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 6 | 8 | 70 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_INDT
Failure Code | FA_INDT |  |  |  | Number of Locations in failure code when defaults assigned: | 33 |  | Final Criticality Code |  | B
Description | TRANSDUCER
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 6
Safety | H | 5 | 5 |  | Redundancy applies? | No
Environmental | H | 5 | 5 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | F | 5 | 7 |  |  | 2 |  | Annex D Mappings | S | C
Business | H | 5 | 5 |  |  | 6 |  |  | E | C
[6 empty] | 2 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 5 | 5 | 72 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable |  |  | B
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 5 | 5 | 72 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 5 | 7 | 70 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 5 | 5 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_INSC
Failure Code | FA_INSC |  |  |  | Number of Locations in failure code when defaults assigned: | 13 |  | Final Criticality Code |  | B
Description | PLC PANEL
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4
Safety | G | 7 | 8 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 4 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | H | 7 | 7 |  |  | 2 |  | Annex D Mappings | S | B
Business | H | 7 | 7 |  |  | 2 |  |  | E | C
[6 empty] | 2 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_INSD
Failure Code | FA_INSD |  |  |  | Number of Locations in failure code when defaults assigned: | 9 |  | Final Criticality Code |  | B
Description | DISTRIBUTED CONTROL PANEL
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4
Safety | G | 7 | 8 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 4 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | H | 7 | 7 |  |  | 2 |  | Annex D Mappings | S | B
Business | H | 7 | 7 |  |  | 2 |  |  | E | C
[6 empty] | 2 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_INSJ
Failure Code | FA_INSJ |  |  |  | Number of Locations in failure code when defaults assigned: | 866 |  | Final Criticality Code |  | A
Description | JUNCTION BOX
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 6
Safety | F | 7 | 9 |  | Redundancy applies? | No
Environmental | G | 7 | 8 |  | Elements contributing to CMMS Location Criticality rating | 6 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | G | 7 | 8 |  |  | 4 |  | Annex D Mappings | S | A
Business | G | 7 | 8 |  |  | 4 |  |  | E | B
[6 empty] | 4 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | F | 7 | 9 | 70 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable |  |  | B
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_INSL
Failure Code | FA_INSL |  |  |  | Number of Locations in failure code when defaults assigned: | 218 |  | Final Criticality Code |  | B
Description | LOCAL CONTROL PANEL
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 6
Safety | H | 5 | 5 |  | Redundancy applies? | No
Environmental | H | 5 | 5 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | F | 5 | 7 |  |  | 2 |  | Annex D Mappings | S | C
Business | H | 5 | 5 |  |  | 6 |  |  | E | C
[6 empty] | 2 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 5 | 5 | 72 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 5 | 5 | 72 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 5 | 7 | 70 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 5 | 5 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_INSS
Failure Code | FA_INSS |  |  |  | Number of Locations in failure code when defaults assigned: | 8 |  | Final Criticality Code |  | B
Description | OPERATOR STATION
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4
Safety | G | 7 | 8 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 4 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | H | 7 | 7 |  |  | 2 |  | Annex D Mappings | S | B
Business | H | 7 | 7 |  |  | 2 |  |  | E | C
[6 empty] | 2 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_INST
Failure Code | FA_INST |  |  |  | Number of Locations in failure code when defaults assigned: | 3 |  | Final Criticality Code |  | B
Description | TERMINATION RACK
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4
Safety | G | 7 | 8 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 4 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | H | 7 | 7 |  |  | 2 |  | Annex D Mappings | S | B
Business | H | 7 | 7 |  |  | 2 |  |  | E | C
[6 empty] | 2 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_INSY
Failure Code | FA_INSY |  |  |  | Number of Locations in failure code when defaults assigned: | 19 |  | Final Criticality Code |  | A
Description | SAFETY INSTRUMENT SYSTEM PANEL
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 7 | 10 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | G | 7 | 8 |  |  | 2 |  | Annex D Mappings | S | A
Business | G | 7 | 8 |  |  | 4 |  |  | E | C
[6 empty] | 4 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 7 | 10 | 69 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_PEA
Failure Code | FA_PEA |  |  |  | Number of Locations in failure code when defaults assigned: | 133 |  | Final Criticality Code |  | C
Description | SELF-ACTUATING VALVE
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4
Safety | H | 5 | 5 |  | Redundancy applies? | No
Environmental | H | 5 | 5 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | C
Production | G | 5 | 6 |  |  | 2 |  | Annex D Mappings | S | C
Business | G | 5 | 6 |  |  | 4 |  |  | E | C
[6 empty] | 4 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide, undefined likelihood set at 5 |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide, undefined likelihood set at 5
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 5 | 6 | 71 | Copied From AGT UMCL Criticality Guide, undefined likelihood set at 5 |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 5 | 6 | 71 | Copied From AGT UMCL Criticality Guide, undefined likelihood set at 5 |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_PEG
Failure Code | FA_PEG |  |  |  | Number of Locations in failure code when defaults assigned: | 12600 |  | Final Criticality Code |  | B
Description | PIPING
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 4 | 7 |  | Redundancy applies? | No
Environmental | G | 4 | 5 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | H | 4 | 4 |  |  | 4 |  | Annex D Mappings | S | B
Business | F | 4 | 6 |  |  | 2 |  |  | E | C
[6 empty] | 6 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 4 | 7 | 69 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | G | 4 | 5 | 71 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 4 | 4 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | F | 4 | 6 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_PEL
Failure Code | FA_PEL |  |  |  | Number of Locations in failure code when defaults assigned: | 1 |  | Final Criticality Code |  | B
Description | PIG LAUNCHER / RECEIVER
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 6
Safety | H | 4 | 4 |  | Redundancy applies? | No
Environmental | H | 4 | 4 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | G | 4 | 5 |  |  | 2 |  | Annex D Mappings | S | C
Business | F | 4 | 6 |  |  | 4 |  |  | E | C
[6 empty] | 6 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 4 | 4 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 4 | 4 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 4 | 5 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | F | 4 | 6 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_PEM
Failure Code | FA_PEM |  |  |  | Number of Locations in failure code when defaults assigned: | 134 |  | Final Criticality Code |  | B
Description | MANIFOLD
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 6
Safety | H | 4 | 4 |  | Redundancy applies? | No
Environmental | H | 4 | 4 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | F | 4 | 6 |  |  | 2 |  | Annex D Mappings | S | C
Business | G | 4 | 5 |  |  | 6 |  |  | E | C
[6 empty] | 4 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 4 | 4 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | sys 63 - instrument air manifold
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 4 | 4 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 4 | 6 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 4 | 5 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_PEO
Failure Code | FA_PEO |  |  |  | Number of Locations in failure code when defaults assigned: | 482 |  | Final Criticality Code |  | B
Description | RESTRICTIVE ORIFICE
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 2
Safety | H | 4 | 4 |  | Redundancy applies? | No
Environmental | H | 4 | 4 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | H | 4 | 4 |  |  | 2 |  | Annex D Mappings | S | C
Business | H | 4 | 4 |  |  | 2 |  |  | E | C
[6 empty] | 2 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 4 | 4 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P5 ¦ Overpressure Protection ¦ ROs in pump recirculation lines |  |  | B
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 4 | 4 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 4 | 4 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 4 | 4 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_PESC
Failure Code | FA_PESC |  |  |  | Number of Locations in failure code when defaults assigned: | 550 |  | Final Criticality Code |  | A
Description | CONVENTIONAL PRESSURE SAFETY VALVE
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 5 | 8 |  | Redundancy applies? | No
Environmental | F | 5 | 7 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | F | 5 | 7 |  |  | 6 |  | Annex D Mappings | S | A
Business | H | 5 | 5 |  |  | 6 |  |  | E | B
[6 empty] | 2 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 5 | 8 | 69 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P5 ¦ Overpressure Protection ¦ All other PSVs |  |  | B
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | F | 5 | 7 | 70 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 5 | 7 | 70 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 5 | 5 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_PESR
Failure Code | FA_PESR |  |  |  | Number of Locations in failure code when defaults assigned: | 49 |  | Final Criticality Code |  | A
Description | RUPTURE DISC
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 5 | 8 |  | Redundancy applies? | No
Environmental | F | 5 | 7 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | F | 5 | 7 |  |  | 6 |  | Annex D Mappings | S | A
Business | H | 5 | 5 |  |  | 6 |  |  | E | B
[6 empty] | 2 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 5 | 8 | 69 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | F | 5 | 7 | 70 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 5 | 7 | 70 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 5 | 5 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_PESV
Failure Code | FA_PESV |  |  |  | Number of Locations in failure code when defaults assigned: | 15 |  | Final Criticality Code |  | A
Description | VACUUM RELIEF PRESSURE SAFETY VALVE
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 5 | 8 |  | Redundancy applies? | No
Environmental | F | 5 | 7 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | F | 5 | 7 |  |  | 6 |  | Annex D Mappings | S | A
Business | H | 5 | 5 |  |  | 6 |  |  | E | B
[6 empty] | 2 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 5 | 8 | 69 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | system 64
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | F | 5 | 7 | 70 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 5 | 7 | 70 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 5 | 5 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_PET
Failure Code | FA_PET |  |  |  | Number of Locations in failure code when defaults assigned: | 548 |  | Final Criticality Code |  | B
Description | THERMOWELL
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 2
Safety | H | 4 | 4 |  | Redundancy applies? | No
Environmental | H | 4 | 4 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | H | 4 | 4 |  |  | 2 |  | Annex D Mappings | S | C
Business | H | 4 | 4 |  |  | 2 |  |  | E | C
[6 empty] | 2 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 4 | 4 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P6 ¦ Control systems - all others ¦ Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cable |  |  | B
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 4 | 4 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 4 | 4 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 4 | 4 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_PEVB
Failure Code | FA_PEVB |  |  |  | Number of Locations in failure code when defaults assigned: | 9510 |  | Final Criticality Code |  | C
Description | BALL VALVE
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4
Safety | G | 5 | 6 |  | Redundancy applies? | No
Environmental | G | 5 | 6 |  | Elements contributing to CMMS Location Criticality rating | 4 |  | Derived SAP A/B/C (highest wins) = |  | C
Production | G | 5 | 6 |  |  | 4 |  | Annex D Mappings | S | C
Business | H | 5 | 5 |  |  | 4 |  |  | E | C
[6 empty] | 2 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | G | 5 | 6 | 71 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | G | 5 | 6 | 71 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 5 | 6 | 71 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 5 | 5 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_PEVC
Failure Code | FA_PEVC |  |  |  | Number of Locations in failure code when defaults assigned: | 1564 |  | Final Criticality Code |  | C
Description | CHECK VALVE
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4
Safety | G | 5 | 6 |  | Redundancy applies? | No
Environmental | G | 5 | 6 |  | Elements contributing to CMMS Location Criticality rating | 4 |  | Derived SAP A/B/C (highest wins) = |  | C
Production | G | 5 | 6 |  |  | 4 |  | Annex D Mappings | S | C
Business | H | 5 | 5 |  |  | 4 |  |  | E | C
[6 empty] | 2 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | G | 5 | 6 | 71 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P5 ¦ Overpressure Protection ¦ All other NRVs |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | G | 5 | 6 | 71 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 5 | 6 | 71 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 5 | 5 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_PEVD
Failure Code | FA_PEVD |  |  |  | Number of Locations in failure code when defaults assigned: | 3 |  | Final Criticality Code |  | C
Description | DIAPHRAGM VALVE
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4
Safety | G | 5 | 6 |  | Redundancy applies? | No
Environmental | G | 5 | 6 |  | Elements contributing to CMMS Location Criticality rating | 4 |  | Derived SAP A/B/C (highest wins) = |  | C
Production | G | 5 | 6 |  |  | 4 |  | Annex D Mappings | S | C
Business | H | 5 | 5 |  |  | 4 |  |  | E | C
[6 empty] | 2 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | G | 5 | 6 | 71 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | G | 5 | 6 | 71 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 5 | 6 | 71 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 5 | 5 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_PEVG
Failure Code | FA_PEVG |  |  |  | Number of Locations in failure code when defaults assigned: | 2589 |  | Final Criticality Code |  | C
Description | GATE VALVE
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4
Safety | G | 5 | 6 |  | Redundancy applies? | No
Environmental | G | 5 | 6 |  | Elements contributing to CMMS Location Criticality rating | 4 |  | Derived SAP A/B/C (highest wins) = |  | C
Production | G | 5 | 6 |  |  | 4 |  | Annex D Mappings | S | C
Business | H | 5 | 5 |  |  | 4 |  |  | E | C
[6 empty] | 2 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | G | 5 | 6 | 71 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | G | 5 | 6 | 71 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 5 | 6 | 71 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 5 | 5 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_PEVL
Failure Code | FA_PEVL |  |  |  | Number of Locations in failure code when defaults assigned: | 969 |  | Final Criticality Code |  | C
Description | GLOBE VALVE
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4
Safety | G | 5 | 6 |  | Redundancy applies? | No
Environmental | G | 5 | 6 |  | Elements contributing to CMMS Location Criticality rating | 4 |  | Derived SAP A/B/C (highest wins) = |  | C
Production | G | 5 | 6 |  |  | 4 |  | Annex D Mappings | S | C
Business | H | 5 | 5 |  |  | 4 |  |  | E | C
[6 empty] | 2 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | G | 5 | 6 | 71 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | G | 5 | 6 | 71 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 5 | 6 | 71 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 5 | 5 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_PEVM
Failure Code | FA_PEVM |  |  |  | Number of Locations in failure code when defaults assigned: | 9 |  | Final Criticality Code |  | B
Description | MULTIPLE ORIFICE VALVE
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4
Safety | G | 6 | 7 |  | Redundancy applies? | No
Environmental | G | 6 | 7 |  | Elements contributing to CMMS Location Criticality rating | 4 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | G | 6 | 7 |  |  | 4 |  | Annex D Mappings | S | B
Business | H | 6 | 6 |  |  | 4 |  |  | E | B
[6 empty] | 2 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | G | 6 | 7 | 71 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | G | 6 | 7 | 71 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 6 | 7 | 71 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_PEVN
Failure Code | FA_PEVN |  |  |  | Number of Locations in failure code when defaults assigned: | 79 |  | Final Criticality Code |  | C
Description | NEEDLE VALVE
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 2
Safety | H | 5 | 5 |  | Redundancy applies? | No
Environmental | H | 5 | 5 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | C
Production | H | 5 | 5 |  |  | 2 |  | Annex D Mappings | S | C
Business | H | 5 | 5 |  |  | 2 |  |  | E | C
[6 empty] | 2 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide, undefined likelihood set at 5 |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | system 64
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide, undefined likelihood set at 5
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide, undefined likelihood set at 5 |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide, undefined likelihood set at 5 |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_PEVX
Failure Code | FA_PEVX |  |  |  | Number of Locations in failure code when defaults assigned: | 4 |  | Final Criticality Code |  | A
Description | DIVERTER VALVE
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10
Safety | D | 5 | 9 |  | Redundancy applies? | No
Environmental | F | 5 | 7 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | F | 5 | 7 |  |  | 6 |  | Annex D Mappings | S | A
Business | E | 5 | 8 |  |  | 6 |  |  | E | B
[6 empty] | 8 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | A
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | D | 5 | 9 | 68 | Copied From AGT UMCL Criticality Guide, undefined likelihood set at 5 |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | F | 5 | 7 | 70 | Copied From AGT UMCL Criticality Guide, undefined likelihood set at 5
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 5 | 7 | 70 | Copied From AGT UMCL Criticality Guide, undefined likelihood set at 5 |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | E | 5 | 8 | 69 | Copied From AGT UMCL Criticality Guide, undefined likelihood set at 5 |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_PEVY
Failure Code | FA_PEVY |  |  |  | Number of Locations in failure code when defaults assigned: | 65 |  | Final Criticality Code |  | B
Description | BUTTERFLY VALVE
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4
Safety | G | 6 | 7 |  | Redundancy applies? | No
Environmental | G | 6 | 7 |  | Elements contributing to CMMS Location Criticality rating | 4 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | G | 6 | 7 |  |  | 4 |  | Annex D Mappings | S | B
Business | H | 6 | 6 |  |  | 4 |  |  | E | B
[6 empty] | 2 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | G | 6 | 7 | 71 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | sys 63,34,35
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | G | 6 | 7 | 71 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 6 | 7 | 71 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_REBC
Failure Code | FA_REBC |  |  |  | Number of Locations in failure code when defaults assigned: | 4 |  | Final Criticality Code |  | A
Description | BLOWER, CENTRIFUGAL
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10
Safety | D | 7 | 11 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | G | 7 | 8 |  |  | 2 |  | Annex D Mappings | S | A
Business | G | 7 | 8 |  |  | 4 |  |  | E | C
[6 empty] | 4 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | D | 7 | 11 | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P4 ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) |  |  | B
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | sys 82
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_REC
Failure Code | FA_REC |  |  |  | Number of Locations in failure code when defaults assigned: | 4 |  | Final Criticality Code |  | B
Description | CENTRIFUGE
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4
Safety | G | 7 | 8 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 4 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | G | 7 | 8 |  |  | 2 |  | Annex D Mappings | S | B
Business | G | 7 | 8 |  |  | 4 |  |  | E | C
[6 empty] | 4 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_REDH
Failure Code | FA_REDH |  |  |  | Number of Locations in failure code when defaults assigned: | 6 |  | Final Criticality Code |  | B
Description | HYDRAULIC MOTOR
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4
Safety | G | 7 | 8 |  | Redundancy applies? | No
Environmental | G | 7 | 8 |  | Elements contributing to CMMS Location Criticality rating | 4 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | G | 7 | 8 |  |  | 4 |  | Annex D Mappings | S | B
Business | H | 7 | 7 |  |  | 4 |  |  | E | B
[6 empty] | 2 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | G | 7 | 8 | 71 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | G | 7 | 8 | 71 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 7 | 8 | 71 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 7 | 7 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_REDP
Failure Code | FA_REDP |  |  |  | Number of Locations in failure code when defaults assigned: | 26 |  | Final Criticality Code |  | B
Description | PNEUMATIC MOTOR
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4
Safety | G | 7 | 8 |  | Redundancy applies? | No
Environmental | G | 7 | 8 |  | Elements contributing to CMMS Location Criticality rating | 4 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | G | 7 | 8 |  |  | 4 |  | Annex D Mappings | S | B
Business | H | 7 | 7 |  |  | 4 |  |  | E | B
[6 empty] | 2 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | G | 7 | 8 | 71 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | G | 7 | 8 | 71 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 7 | 8 | 71 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 7 | 7 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_REEL
Failure Code | FA_REEL |  |  |  | Number of Locations in failure code when defaults assigned: | 4 |  | Final Criticality Code |  | A
Description | LIQUID FUEL COMBUSTION ENGINE
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10
Safety | D | 7 | 11 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | H | 7 | 7 |  |  | 2 |  | Annex D Mappings | S | A
Business | F | 7 | 9 |  |  | 2 |  |  | E | C
[6 empty] | 6 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | A
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | D | 7 | 11 | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | F | 7 | 9 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_REFA
Failure Code | FA_REFA |  |  |  | Number of Locations in failure code when defaults assigned: | 24 |  | Final Criticality Code |  | A
Description | AXIAL FAN
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 6
Safety | G | 7 | 8 |  | Redundancy applies? | No
Environmental | G | 7 | 8 |  | Elements contributing to CMMS Location Criticality rating | 4 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | F | 7 | 9 |  |  | 4 |  | Annex D Mappings | S | B
Business | F | 7 | 9 |  |  | 6 |  |  | E | B
[6 empty] | 6 |  |  | P | A
Risk Matrix Population Inputs | [8 empty] | B | A
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | G | 7 | 8 | 71 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | G | 7 | 8 | 71 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 7 | 9 | 70 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | F | 7 | 9 | 70 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_REFC
Failure Code | FA_REFC |  |  |  | Number of Locations in failure code when defaults assigned: | 131 |  | Final Criticality Code |  | A
Description | CENTRIFUGAL FAN
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 7 | 10 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | G | 7 | 8 |  |  | 2 |  | Annex D Mappings | S | A
Business | G | 7 | 8 |  |  | 4 |  |  | E | C
[6 empty] | 4 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 7 | 10 | 69 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | sys 65
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_REMC
Failure Code | FA_REMC |  |  |  | Number of Locations in failure code when defaults assigned: | 3 |  | Final Criticality Code |  | A
Description | CENTRIFUGAL COMPRESSOR
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | G | 6 | 7 |  | Redundancy applies? | No
Environmental | G | 6 | 7 |  | Elements contributing to CMMS Location Criticality rating | 4 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | E | 6 | 9 |  |  | 4 |  | Annex D Mappings | S | B
Business | F | 6 | 8 |  |  | 8 |  |  | E | B
[6 empty] | 6 |  |  | P | A
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | G | 6 | 7 | 71 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no valid tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | G | 6 | 7 | 71 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | E | 6 | 9 | 69 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | No | A
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | F | 6 | 8 | 70 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_REMR
Failure Code | FA_REMR |  |  |  | Number of Locations in failure code when defaults assigned: | 6 |  | Final Criticality Code |  | A
Description | RECIPROCATING COMPRESSOR
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | G | 6 | 7 |  | Redundancy applies? | No
Environmental | G | 6 | 7 |  | Elements contributing to CMMS Location Criticality rating | 4 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | E | 6 | 9 |  |  | 4 |  | Annex D Mappings | S | B
Business | F | 6 | 8 |  |  | 8 |  |  | E | B
[6 empty] | 6 |  |  | P | A
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | G | 6 | 7 | 71 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | G | 6 | 7 | 71 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | E | 6 | 9 | 69 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | No | A
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | F | 6 | 8 | 70 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_REMT
Failure Code | FA_REMT |  |  |  | Number of Locations in failure code when defaults assigned: | 11 |  | Final Criticality Code |  | B
Description | ROTARY COMPRESSOR
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 6
Safety | G | 6 | 7 |  | Redundancy applies? | No
Environmental | G | 6 | 7 |  | Elements contributing to CMMS Location Criticality rating | 4 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | F | 6 | 8 |  |  | 4 |  | Annex D Mappings | S | B
Business | F | 6 | 8 |  |  | 6 |  |  | E | B
[6 empty] | 6 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | G | 6 | 7 | 71 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P4 ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) |  |  | B
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | air compressors, sys 65
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | G | 6 | 7 | 71 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 6 | 8 | 70 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | F | 6 | 8 | 70 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_RENG
Failure Code | FA_RENG |  |  |  | Number of Locations in failure code when defaults assigned: | 10 |  | Final Criticality Code |  | A
Description | GAS TURBINE
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | F | 7 | 9 |  | Redundancy applies? | No
Environmental | G | 7 | 8 |  | Elements contributing to CMMS Location Criticality rating | 6 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | E | 7 | 10 |  |  | 4 |  | Annex D Mappings | S | A
Business | F | 7 | 9 |  |  | 8 |  |  | E | B
[6 empty] | 6 |  |  | P | A
Risk Matrix Population Inputs | [8 empty] | B | A
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | F | 7 | 9 | 70 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | E | 7 | 10 | 69 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | No | A
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | F | 7 | 9 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_REPC
Failure Code | FA_REPC |  |  |  | Number of Locations in failure code when defaults assigned: | 275 |  | Final Criticality Code |  | A
Description | CENTRIFUGAL PUMP
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | H | 7 | 7 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | E | 7 | 10 |  |  | 2 |  | Annex D Mappings | S | C
Business | G | 7 | 8 |  |  | 8 |  |  | E | C
[6 empty] | 4 |  |  | P | A
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P4 ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) |  |  | B
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | E | 7 | 10 | 69 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | No | A
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_REPD
Failure Code | FA_REPD |  |  |  | Number of Locations in failure code when defaults assigned: | 39 |  | Final Criticality Code |  | B
Description | POSITIVE DISPLACEMENT PUMP
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 6
Safety | G | 6 | 7 |  | Redundancy applies? | No
Environmental | G | 6 | 7 |  | Elements contributing to CMMS Location Criticality rating | 4 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | F | 6 | 8 |  |  | 4 |  | Annex D Mappings | S | B
Business | F | 6 | 8 |  |  | 6 |  |  | E | B
[6 empty] | 6 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | G | 6 | 7 | 71 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | G | 6 | 7 | 71 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 6 | 8 | 70 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | F | 6 | 8 | 70 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_RER
Failure Code | FA_RER |  |  |  | Number of Locations in failure code when defaults assigned: | 2 |  | Final Criticality Code |  | B
Description | RAKE / SCRAPER
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4
Safety | G | 6 | 7 |  | Redundancy applies? | No
Environmental | G | 6 | 7 |  | Elements contributing to CMMS Location Criticality rating | 4 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | G | 6 | 7 |  |  | 4 |  | Annex D Mappings | S | B
Business | G | 6 | 7 |  |  | 4 |  |  | E | B
[6 empty] | 4 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | G | 6 | 7 | 71 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | G | 6 | 7 | 71 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 6 | 7 | 71 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 6 | 7 | 71 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_RETG
Failure Code | FA_RETG |  |  |  | Number of Locations in failure code when defaults assigned: | 5 |  | Final Criticality Code |  | B
Description | GEARBOX
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 6
Safety | H | 6 | 6 |  | Redundancy applies? | No
Environmental | H | 6 | 6 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | F | 6 | 8 |  |  | 2 |  | Annex D Mappings | S | C
Business | H | 6 | 6 |  |  | 6 |  |  | E | C
[6 empty] | 2 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in MEL
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 6 | 8 | 70 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_RETP
Failure Code | FA_RETP |  |  |  | Number of Locations in failure code when defaults assigned: | 5 |  | Final Criticality Code |  | B
Description | COUPLING
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 6
Safety | F | 6 | 8 |  | Redundancy applies? | No
Environmental | H | 6 | 6 |  | Elements contributing to CMMS Location Criticality rating | 6 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | F | 6 | 8 |  |  | 2 |  | Annex D Mappings | S | B
Business | H | 6 | 6 |  |  | 6 |  |  | E | C
[6 empty] | 2 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | F | 6 | 8 | 70 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P4 ¦ Non Hydrocarbon RE (air compressors, water and hydraulic pumps) ¦ Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) |  |  | B
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | sys 65 only - no tags in process systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 6 | 8 | 70 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 6 | 6 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_REUC
Failure Code | FA_REUC |  |  |  | Number of Locations in failure code when defaults assigned: | 1 |  | Final Criticality Code |  | B
Description | CHEMICAL INJECTION SYSTEM
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4
Safety | H | 7 | 7 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | G | 7 | 8 |  |  | 2 |  | Annex D Mappings | S | C
Business | G | 7 | 8 |  |  | 4 |  |  | E | C
[6 empty] | 4 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SEC
Failure Code | FA_SEC |  |  |  | Number of Locations in failure code when defaults assigned: | 6 |  | Final Criticality Code |  | C
Description | CYCLONE
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4
Safety | H | 5 | 5 |  | Redundancy applies? | No
Environmental | G | 5 | 6 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | C
Production | G | 5 | 6 |  |  | 4 |  | Annex D Mappings | S | C
Business | G | 5 | 6 |  |  | 4 |  |  | E | C
[6 empty] | 4 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 5 | 5 | 72 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | sys 65 only - no tags in process systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | G | 5 | 6 | 71 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 5 | 6 | 71 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 5 | 6 | 71 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SEE
Failure Code | FA_SEE |  |  |  | Number of Locations in failure code when defaults assigned: | 3 |  | Final Criticality Code |  | B
Description | EJECTOR / EDUCTOR
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 6
Safety | F | 5 | 7 |  | Redundancy applies? | No
Environmental | H | 5 | 5 |  | Elements contributing to CMMS Location Criticality rating | 6 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | F | 5 | 7 |  |  | 2 |  | Annex D Mappings | S | B
Business | H | 5 | 5 |  |  | 6 |  |  | E | C
[6 empty] | 2 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | F | 5 | 7 | 70 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 5 | 5 | 72 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 5 | 7 | 70 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 5 | 5 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SEFB
Failure Code | FA_SEFB |  |  |  | Number of Locations in failure code when defaults assigned: | 310 |  | Final Criticality Code |  | B
Description | BASKET STRAINER FILTER
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4
Safety | H | 7 | 7 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | G | 7 | 8 |  |  | 2 |  | Annex D Mappings | S | C
Business | H | 7 | 7 |  |  | 4 |  |  | E | C
[6 empty] | 2 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 7 | 7 | 72 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | sys 53,65 utilities
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 7 | 8 | 71 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 7 | 7 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SEFE
Failure Code | FA_SEFE |  |  |  | Number of Locations in failure code when defaults assigned: | 194 |  | Final Criticality Code |  | B
Description | ELEMENT FILTER
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4
Safety | H | 7 | 7 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | G | 7 | 8 |  |  | 2 |  | Annex D Mappings | S | C
Business | H | 7 | 7 |  |  | 4 |  |  | E | C
[6 empty] | 2 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 7 | 7 | 72 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | Generally for equipment reliability, rather than MAH, None allocated - sys 63,64,65;
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 7 | 8 | 71 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 7 | 7 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SEFS
Failure Code | FA_SEFS |  |  |  | Number of Locations in failure code when defaults assigned: | 18 |  | Final Criticality Code |  | C
Description | SCREEN FILTER
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 2
Safety | H | 7 | 7 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | C
Production | H | 7 | 7 |  |  | 2 |  | Annex D Mappings | S | C
Business | H | 7 | 7 |  |  | 2 |  |  | E | C
[6 empty] | 2 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | Generally for equipment reliability, rather than MAH, None allocated - sys 64
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SEHF
Failure Code | FA_SEHF |  |  |  | Number of Locations in failure code when defaults assigned: | 70 |  | Final Criticality Code |  | A
Description | FINNED COIL HEAT EXCHANGER
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | #N/A
Safety | H | 5 | 5 |  | Redundancy applies? | No
Environmental | H | 5 | 5 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | - | 5 | #N/A |  |  | 2 |  | Annex D Mappings | S | C
Business | H | 5 | 5 |  |  | #N/A |  |  | E | C
[6 empty] | 2 |  |  | P | A
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | sys 63,65
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | - | 5 | #N/A | 45 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SEHS
Failure Code | FA_SEHS |  |  |  | Number of Locations in failure code when defaults assigned: | 48 |  | Final Criticality Code |  | A
Description | SPIRAL HEAT EXCHANGER
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | #N/A
Safety | H | 5 | 5 |  | Redundancy applies? | No
Environmental | H | 5 | 5 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | - | 5 | #N/A |  |  | 2 |  | Annex D Mappings | S | C
Business | H | 5 | 5 |  |  | #N/A |  |  | E | C
[6 empty] | 2 |  |  | P | A
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | - | 5 | #N/A | 45 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SEHT
Failure Code | FA_SEHT |  |  |  | Number of Locations in failure code when defaults assigned: | 51 |  | Final Criticality Code |  | A
Description | SHELL & TUBE HEAT EXCHANGER
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | #N/A
Safety | G | 5 | 6 |  | Redundancy applies? | No
Environmental | H | 5 | 5 |  | Elements contributing to CMMS Location Criticality rating | 4 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | - | 5 | #N/A |  |  | 2 |  | Annex D Mappings | S | C
Business | G | 5 | 6 |  |  | #N/A |  |  | E | C
[6 empty] | 4 |  |  | P | A
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | G | 5 | 6 | 71 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | - | 5 | #N/A | 45 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 5 | 6 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SEL
Failure Code | FA_SEL |  |  |  | Number of Locations in failure code when defaults assigned: | 53 |  | Final Criticality Code |  | A
Description | FLAME ARRESTOR
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 5 | 8 |  | Redundancy applies? | No
Environmental | H | 5 | 5 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | H | 5 | 5 |  |  | 2 |  | Annex D Mappings | S | A
Business | H | 5 | 5 |  |  | 2 |  |  | E | C
[6 empty] | 2 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 5 | 8 | 69 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | M4 ¦ Ignition Prevention ¦ For Equipment in Zone 2 |  |  | B
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | system 58
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SEM
Failure Code | FA_SEM |  |  |  | Number of Locations in failure code when defaults assigned: | 5 |  | Final Criticality Code |  | A
Description | FLARE
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 5 | 8 |  | Redundancy applies? | No
Environmental | G | 5 | 6 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | E | 5 | 8 |  |  | 4 |  | Annex D Mappings | S | A
Business | F | 5 | 7 |  |  | 8 |  |  | E | C
[6 empty] | 6 |  |  | P | A
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 5 | 8 | 69 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | G | 5 | 6 | 71 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | E | 5 | 8 | 69 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | F | 5 | 7 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SENF
Failure Code | FA_SENF |  |  |  | Number of Locations in failure code when defaults assigned: | 4 |  | Final Criticality Code |  | A
Description | FIRED HEATER FURNACE
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | #N/A
Safety | H | 5 | 5 |  | Redundancy applies? | No
Environmental | G | 5 | 6 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | - | 5 | #N/A |  |  | 4 |  | Annex D Mappings | S | C
Business | G | 5 | 6 |  |  | #N/A |  |  | E | C
[6 empty] | 4 |  |  | P | A
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | G | 5 | 6 | 71 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | - | 5 | #N/A | 45 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 5 | 6 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SEPA
Failure Code | FA_SEPA |  |  |  | Number of Locations in failure code when defaults assigned: | 192 |  | Final Criticality Code |  | A
Description | ACCUMULATOR
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 5 | 8 |  | Redundancy applies? | No
Environmental | H | 5 | 5 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | H | 5 | 5 |  |  | 2 |  | Annex D Mappings | S | A
Business | G | 5 | 6 |  |  | 2 |  |  | E | C
[6 empty] | 4 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 5 | 8 | 69 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 5 | 6 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SEPC
Failure Code | FA_SEPC |  |  |  | Number of Locations in failure code when defaults assigned: | 59 |  | Final Criticality Code |  | C
Description | CYLINDER
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4
Safety | H | 5 | 5 |  | Redundancy applies? | No
Environmental | H | 5 | 5 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | C
Production | H | 5 | 5 |  |  | 2 |  | Annex D Mappings | S | C
Business | G | 5 | 6 |  |  | 2 |  |  | E | C
[6 empty] | 4 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | sys 64
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 5 | 6 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SEPHC
Failure Code | FA_SEPHC |  |  |  | Number of Locations in failure code when defaults assigned: | 2 |  | Final Criticality Code |  | A
Description | CONDENSER VESSEL
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | #N/A
Safety | H | 5 | 5 |  | Redundancy applies? | No
Environmental | H | 5 | 5 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | - | 5 | #N/A |  |  | 2 |  | Annex D Mappings | S | C
Business | G | 5 | 6 |  |  | #N/A |  |  | E | C
[6 empty] | 4 |  |  | P | A
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | - | 5 | #N/A | 45 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 5 | 6 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SEPHS
Failure Code | FA_SEPHS |  |  |  | Number of Locations in failure code when defaults assigned: | 190 |  | Final Criticality Code |  | A
Description | SEPARATOR VESSEL
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | #N/A
Safety | H | 5 | 5 |  | Redundancy applies? | No
Environmental | H | 5 | 5 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | - | 5 | #N/A |  |  | 2 |  | Annex D Mappings | S | C
Business | G | 5 | 6 |  |  | #N/A |  |  | E | C
[6 empty] | 4 |  |  | P | A
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | sys 53,64,65
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | - | 5 | #N/A | 45 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 5 | 6 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SES
Failure Code | FA_SES |  |  |  | Number of Locations in failure code when defaults assigned: | 72 |  | Final Criticality Code |  | C
Description | PULSATION DAMPENER
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4
Safety | G | 5 | 6 |  | Redundancy applies? | No
Environmental | H | 5 | 5 |  | Elements contributing to CMMS Location Criticality rating | 4 |  | Derived SAP A/B/C (highest wins) = |  | C
Production | G | 5 | 6 |  |  | 2 |  | Annex D Mappings | S | C
Business | H | 5 | 5 |  |  | 4 |  |  | E | C
[6 empty] | 2 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | G | 5 | 6 | 71 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 5 | 6 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SETAC
Failure Code | FA_SETAC |  |  |  | Number of Locations in failure code when defaults assigned: | 60 |  | Final Criticality Code |  | A
Description | CLOSED ROOF ATMOSPHERIC TANK
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | #N/A
Safety | H | 5 | 5 |  | Redundancy applies? | No
Environmental | H | 5 | 5 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | - | 5 | #N/A |  |  | 2 |  | Annex D Mappings | S | C
Business | G | 5 | 6 |  |  | #N/A |  |  | E | C
[6 empty] | 4 |  |  | P | A
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | sys 53,63; no MAH barrier for non-HC tank
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | - | 5 | #N/A | 45 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 5 | 6 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SETAP
Failure Code | FA_SETAP |  |  |  | Number of Locations in failure code when defaults assigned: | 40 |  | Final Criticality Code |  | A
Description | PIT / SUMP
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | #N/A
Safety | H | 5 | 5 |  | Redundancy applies? | No
Environmental | G | 5 | 6 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | - | 5 | #N/A |  |  | 4 |  | Annex D Mappings | S | C
Business | G | 5 | 6 |  |  | #N/A |  |  | E | C
[6 empty] | 4 |  |  | P | A
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P2 ¦ Structural Integrity ¦ Tertiary Structures - Failure may result in fall 1 - 3m |  |  | B
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | sys 58,59,65,82
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | G | 5 | 6 | 71 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | - | 5 | #N/A | 45 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 5 | 6 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SETPC
Failure Code | FA_SETPC |  |  |  | Number of Locations in failure code when defaults assigned: | 11 |  | Final Criticality Code |  | A
Description | CYLINDRICAL PRESSURISED TANK
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10
Safety | D | 5 | 9 |  | Redundancy applies? | No
Environmental | H | 5 | 5 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | G | 5 | 6 |  |  | 2 |  | Annex D Mappings | S | A
Business | F | 5 | 7 |  |  | 4 |  |  | E | C
[6 empty] | 6 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | D | 5 | 9 | 68 | Copied From AGT UMCL Criticality Guide (Likelihood mnaully corrected due to lookup error) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide (Likelihood mnaully corrected due to lookup error)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 5 | 6 | 71 | Copied From AGT UMCL Criticality Guide (Likelihood mnaully corrected due to lookup error) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | F | 5 | 7 | 70 | Copied From AGT UMCL Criticality Guide (Likelihood mnaully corrected due to lookup error) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SEZ
Failure Code | FA_SEZ |  |  |  | Number of Locations in failure code when defaults assigned: | 64 |  | Final Criticality Code |  | C
Description | SILENCER / MUFFLER
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4
Safety | H | 5 | 5 |  | Redundancy applies? | No
Environmental | G | 5 | 6 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | C
Production | H | 5 | 5 |  |  | 4 |  | Annex D Mappings | S | C
Business | H | 5 | 5 |  |  | 2 |  |  | E | C
[6 empty] | 2 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | sys 63,64,65
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | G | 5 | 6 | 71 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SQFC
Failure Code | FA_SQFC |  |  |  | Number of Locations in failure code when defaults assigned: | 21 |  | Final Criticality Code |  | B
Description | EQUIPMENT CABINET
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 4 | 7 |  | Redundancy applies? | No
Environmental | H | 4 | 4 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | H | 4 | 4 |  |  | 2 |  | Annex D Mappings | S | B
Business | H | 4 | 4 |  |  | 2 |  |  | E | C
[6 empty] | 2 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 4 | 7 | 69 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 4 | 4 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 4 | 4 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 4 | 4 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SQFDF
Failure Code | FA_SQFDF |  |  |  | Number of Locations in failure code when defaults assigned: | 420 |  | Final Criticality Code |  | A
Description | FLAME DETECTOR
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10
Safety | D | 7 | 11 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | H | 7 | 7 |  |  | 2 |  | Annex D Mappings | S | A
Business | H | 7 | 7 |  |  | 2 |  |  | E | C
[6 empty] | 2 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | D | 7 | 11 | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SQFDG
Failure Code | FA_SQFDG |  |  |  | Number of Locations in failure code when defaults assigned: | 739 |  | Final Criticality Code |  | A
Description | FIXED GAS DETECTOR
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10
Safety | D | 7 | 11 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | H | 7 | 7 |  |  | 2 |  | Annex D Mappings | S | A
Business | H | 7 | 7 |  |  | 2 |  |  | E | C
[6 empty] | 2 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | D | 7 | 11 | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SQFDS
Failure Code | FA_SQFDS |  |  |  | Number of Locations in failure code when defaults assigned: | 140 |  | Final Criticality Code |  | A
Description | SMOKE DETECTOR
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10
Safety | D | 7 | 11 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | H | 7 | 7 |  |  | 2 |  | Annex D Mappings | S | A
Business | H | 7 | 7 |  |  | 2 |  |  | E | C
[6 empty] | 2 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | D | 7 | 11 | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SQFFD
Failure Code | FA_SQFFD |  |  |  | Number of Locations in failure code when defaults assigned: | 26 |  | Final Criticality Code |  | A
Description | FIREWATER DELUGE SYSTEM
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10
Safety | D | 7 | 11 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | F | 7 | 9 |  |  | 2 |  | Annex D Mappings | S | A
Business | F | 7 | 9 |  |  | 6 |  |  | E | C
[6 empty] | 6 |  |  | P | A
Risk Matrix Population Inputs | [8 empty] | B | A
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | D | 7 | 11 | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | F | 7 | 9 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | F | 7 | 9 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SQFFH
Failure Code | FA_SQFFH |  |  |  | Number of Locations in failure code when defaults assigned: | 3 |  | Final Criticality Code |  | A
Description | FIRE HOSE
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10
Safety | D | 7 | 11 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | H | 7 | 7 |  |  | 2 |  | Annex D Mappings | S | A
Business | F | 7 | 9 |  |  | 2 |  |  | E | C
[6 empty] | 6 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | A
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | D | 7 | 11 | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | F | 7 | 9 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SQFFM
Failure Code | FA_SQFFM |  |  |  | Number of Locations in failure code when defaults assigned: | 23 |  | Final Criticality Code |  | A
Description | FIRE WATER/FOAM MONITOR
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10
Safety | D | 6 | 10 |  | Redundancy applies? | No
Environmental | H | 6 | 6 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | H | 6 | 6 |  |  | 2 |  | Annex D Mappings | S | A
Business | H | 6 | 6 |  |  | 2 |  |  | E | C
[6 empty] | 2 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | D | 6 | 10 | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 6 | 6 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 6 | 6 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 6 | 6 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SQFFY
Failure Code | FA_SQFFY |  |  |  | Number of Locations in failure code when defaults assigned: | 118 |  | Final Criticality Code |  | A
Description | FIRE HYDRANT
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10
Safety | D | 5 | 9 |  | Redundancy applies? | No
Environmental | H | 5 | 5 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | H | 5 | 5 |  |  | 2 |  | Annex D Mappings | S | A
Business | F | 5 | 7 |  |  | 2 |  |  | E | C
[6 empty] | 6 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | D | 5 | 9 | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | F | 5 | 7 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SQFRA
Failure Code | FA_SQFRA |  |  |  | Number of Locations in failure code when defaults assigned: | 244 |  | Final Criticality Code |  | A
Description | EMERGENCY ALARM DEVICE
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10
Safety | D | 7 | 11 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | H | 7 | 7 |  |  | 2 |  | Annex D Mappings | S | A
Business | H | 7 | 7 |  |  | 2 |  |  | E | C
[6 empty] | 2 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | D | 7 | 11 | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | M3 ¦ Alarm Annunciation System: ¦ External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers |  |  | A
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | system 82 utility
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SQFRE
Failure Code | FA_SQFRE |  |  |  | Number of Locations in failure code when defaults assigned: | 20 |  | Final Criticality Code |  | A
Description | SAFETY SHOWER OR EYE BATH
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 5 | 8 |  | Redundancy applies? | No
Environmental | H | 5 | 5 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | H | 5 | 5 |  |  | 2 |  | Annex D Mappings | S | A
Business | H | 5 | 5 |  |  | 2 |  |  | E | C
[6 empty] | 2 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 5 | 8 | 69 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | P4 ¦ Process Containment Integrity ¦ All other pressure Equipment and pipework |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | system 53 only - no process system tags
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 5 | 5 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SQMT
Failure Code | FA_SQMT |  |  |  | Number of Locations in failure code when defaults assigned: | 2 |  | Final Criticality Code |  | C
Description | MAINTENANCE TOOL
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 2
Safety | H | 7 | 7 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | C
Production | H | 7 | 7 |  |  | 2 |  | Annex D Mappings | S | C
Business | H | 7 | 7 |  |  | 2 |  |  | E | C
[6 empty] | 2 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SQTA
Failure Code | FA_SQTA |  |  |  | Number of Locations in failure code when defaults assigned: | 60 |  | Final Criticality Code |  | A
Description | PUBLIC ADDRESS AND ALARM SYSTEM
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10
Safety | D | 7 | 11 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | H | 7 | 7 |  |  | 2 |  | Annex D Mappings | S | A
Business | G | 7 | 8 |  |  | 2 |  |  | E | C
[6 empty] | 4 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | D | 7 | 11 | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SQTB
Failure Code | FA_SQTB |  |  |  | Number of Locations in failure code when defaults assigned: | 169 |  | Final Criticality Code |  | A
Description | NON DIRECTIONAL BEACON
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10
Safety | D | 7 | 11 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | H | 7 | 7 |  |  | 2 |  | Annex D Mappings | S | A
Business | G | 7 | 8 |  |  | 2 |  |  | E | C
[6 empty] | 4 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | D | 7 | 11 | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SQTE
Failure Code | FA_SQTE |  |  |  | Number of Locations in failure code when defaults assigned: | 33 |  | Final Criticality Code |  | A
Description | TELECOMMUNICATION CABINET
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 7 | 10 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | G | 7 | 8 |  |  | 2 |  | Annex D Mappings | S | A
Business | G | 7 | 8 |  |  | 4 |  |  | E | C
[6 empty] | 4 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 7 | 10 | 69 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SQTH
Failure Code | FA_SQTH |  |  |  | Number of Locations in failure code when defaults assigned: | 95 |  | Final Criticality Code |  | A
Description | PATCH PANEL
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 7 | 10 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | G | 7 | 8 |  |  | 2 |  | Annex D Mappings | S | A
Business | G | 7 | 8 |  |  | 4 |  |  | E | C
[6 empty] | 4 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 7 | 10 | 69 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SQTL
Failure Code | FA_SQTL |  |  |  | Number of Locations in failure code when defaults assigned: | 487 |  | Final Criticality Code |  | A
Description | LOUDSPEAKER
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10
Safety | D | 7 | 11 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | H | 7 | 7 |  |  | 2 |  | Annex D Mappings | S | A
Business | G | 7 | 8 |  |  | 2 |  |  | E | C
[6 empty] | 4 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | D | 7 | 11 | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SQTN
Failure Code | FA_SQTN |  |  |  | Number of Locations in failure code when defaults assigned: | 3 |  | Final Criticality Code |  | A
Description | ANTENNA
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10
Safety | D | 8 | 12 |  | Redundancy applies? | No
Environmental | H | 8 | 8 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | G | 8 | 9 |  |  | 2 |  | Annex D Mappings | S | A
Business | G | 8 | 9 |  |  | 4 |  |  | E | C
[6 empty] | 4 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | D | 8 | 12 | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 8 | 8 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 8 | 9 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 8 | 9 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SQTOF
Failure Code | FA_SQTOF |  |  |  | Number of Locations in failure code when defaults assigned: | 6 |  | Final Criticality Code |  | A
Description | FIXED RADIO
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10
Safety | D | 7 | 11 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | G | 7 | 8 |  |  | 2 |  | Annex D Mappings | S | A
Business | G | 7 | 8 |  |  | 4 |  |  | E | C
[6 empty] | 4 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | D | 7 | 11 | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SQTP
Failure Code | FA_SQTP |  |  |  | Number of Locations in failure code when defaults assigned: | 104 |  | Final Criticality Code |  | C
Description | COMPUTER PERIPHERAL
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 2
Safety | H | 7 | 7 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | C
Production | H | 7 | 7 |  |  | 2 |  | Annex D Mappings | S | C
Business | H | 7 | 7 |  |  | 2 |  |  | E | C
[6 empty] | 2 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SQTS
Failure Code | FA_SQTS |  |  |  | Number of Locations in failure code when defaults assigned: | 101 |  | Final Criticality Code |  | A
Description | TELEPHONE OR MULTIMEDIA EQUIPMENT
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10
Safety | D | 7 | 11 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | G | 7 | 8 |  |  | 2 |  | Annex D Mappings | S | A
Business | G | 7 | 8 |  |  | 4 |  |  | E | C
[6 empty] | 4 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | D | 7 | 11 | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SQTV
Failure Code | FA_SQTV |  |  |  | Number of Locations in failure code when defaults assigned: | 167 |  | Final Criticality Code |  | A
Description | CCTV CAMERA UNIT
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10
Safety | D | 7 | 11 |  | Redundancy applies? | No
Environmental | G | 7 | 8 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | G | 7 | 8 |  |  | 4 |  | Annex D Mappings | S | A
Business | G | 7 | 8 |  |  | 4 |  |  | E | B
[6 empty] | 4 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | D | 7 | 11 | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SQTW
Failure Code | FA_SQTW |  |  |  | Number of Locations in failure code when defaults assigned: | 17 |  | Final Criticality Code |  | A
Description | WIRELESS COMMUNICATION OR CONTROL EQUIPMENT
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 7 | 10 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | G | 7 | 8 |  |  | 2 |  | Annex D Mappings | S | A
Business | H | 7 | 7 |  |  | 4 |  |  | E | C
[6 empty] | 2 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | C
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 7 | 10 | 69 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 7 | 8 | 71 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | H | 7 | 7 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SQTY
Failure Code | FA_SQTY |  |  |  | Number of Locations in failure code when defaults assigned: | 4 |  | Final Criticality Code |  | A
Description | RECEIVER / TRANSMITTER
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 8 | 11 |  | Redundancy applies? | No
Environmental | H | 8 | 8 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | G | 8 | 9 |  |  | 2 |  | Annex D Mappings | S | A
Business | G | 8 | 9 |  |  | 4 |  |  | E | C
[6 empty] | 4 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 8 | 11 | 69 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 8 | 8 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 8 | 9 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 8 | 9 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_SYLH
Failure Code | FA_SYLH |  |  |  | Number of Locations in failure code when defaults assigned: | 316 |  | Final Criticality Code |  | A
Description | SYSTEM LEVEL HIERARCHY
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8
Safety | E | 7 | 10 |  | Redundancy applies? | No
Environmental | E | 7 | 10 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | E | 7 | 10 |  |  | 8 |  | Annex D Mappings | S | A
Business | E | 7 | 10 |  |  | 8 |  |  | E | A
[6 empty] | 8 |  |  | P | A
Risk Matrix Population Inputs | [8 empty] | B | A
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | E | 7 | 10 | 69 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | Not equipment tags, no criticality assignment required
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | E | 7 | 10 | 69 | Initial Estimate based quick judegment (not in AGT)
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | E | 7 | 10 | 69 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | No | A
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | E | 7 | 10 | 69 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_WECO
Failure Code | FA_WECO |  |  |  | Number of Locations in failure code when defaults assigned: | 11 |  | Final Criticality Code |  | A
Description | OVERHEAD CRANE
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 6
Safety | H | 7 | 7 |  | Redundancy applies? | No
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | A
Production | G | 7 | 8 |  |  | 2 |  | Annex D Mappings | S | C
Business | F | 7 | 9 |  |  | 4 |  |  | E | C
[6 empty] | 6 |  |  | P | B
Risk Matrix Population Inputs | [8 empty] | B | A
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | M5 ¦ Cranes ¦ Maintenance Equipment |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | system 65 gantry crane
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 7 | 7 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | G | 7 | 8 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | F | 7 | 9 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C

## FA_WEHY
Failure Code | FA_WEHY |  |  |  | Number of Locations in failure code when defaults assigned: | 2 |  | Final Criticality Code |  | B
Description | CONVEYOR
Reviewed
Agreed
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  | Calculation has been overriden? Overwrite K10 to override |  | FALSE
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code in K1 is changed from the derived value below
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4
Safety | H | 6 | 6 |  | Redundancy applies? | No
Environmental | H | 6 | 6 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C (highest wins) = |  | B
Production | H | 6 | 6 |  |  | 2 |  | Annex D Mappings | S | C
Business | G | 6 | 7 |  |  | 2 |  |  | E | C
[6 empty] | 4 |  |  | P | C
Risk Matrix Population Inputs | [8 empty] | B | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041
Loss of Function | H | 6 | 6 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family / Component |  |  | ABC
|  |  | #N/A |  |  |  | #N/A ¦ #N/A ¦ #N/A |  |  | C
#N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | no tags in utility systems
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2
Loss of Function | H | 6 | 6 | 72 | Copied From AGT UMCL Criticality Guide
#N/A
#N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart
Loss of Function | H | 6 | 6 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart
Loss of Function | G | 6 | 7 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C
[7 empty] | Regulatory Requirement overrides? | No | No | C