[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | #N/A | 153 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | #N/A | 154 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | #N/A | 155 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | #N/A | 156 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | #N/A | 157 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | #N/A | 158 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | #N/A | 159 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | #N/A | 160 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | #N/A | 161 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | #N/A | 162 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | #N/A | 163 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | #N/A | 164 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | #N/A | 165 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | #N/A | 166 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | #N/A | 167 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | #N/A | 168 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | #N/A | 169 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | #N/A | 170 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | #N/A | 171 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | #N/A | 172 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | #N/A | 173 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | #N/A | 174 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | #N/A | 175 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | #N/A | 176 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | #N/A | 177 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | #N/A | 178 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | #N/A | 179 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | #N/A | 180 |  | #N/A | #N/A
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | #N/A | 181 |  | #N/A | #N/A
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | #N/A | 182 |  | #N/A | #N/A
[11 empty] | P6-A | Digital security | Architecture | A | 18 | #N/A | 183 |  | #N/A | #N/A
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | #N/A | 184 |  | #N/A | #N/A
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | #N/A | 185 |  | #N/A | #N/A
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | #N/A | 186 |  | #N/A | #N/A
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | #N/A | 187 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | #N/A | 188 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | #N/A | 189 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | #N/A | 190 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | #N/A | 191 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | #N/A | 192 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | #N/A | 193 |  | #N/A | #N/A
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | #N/A | 194 |  | #N/A | #N/A
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | #N/A | 195 |  | #N/A | #N/A
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | #N/A | 196 |  | #N/A | #N/A
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | #N/A | 197 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | #N/A | 198 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | #N/A | 199 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | #N/A | 200 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | #N/A | 201 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | #N/A | 202 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | #N/A | 203 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | #N/A | 204 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | #N/A | 205 |  | #N/A | #N/A
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | #N/A | 206 |  | #N/A | #N/A
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | #N/A | 207 |  | #N/A | #N/A
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | #N/A | 208 |  | #N/A | #N/A
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | #N/A | 209 |  | #N/A | #N/A
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | #N/A | 210 |  | #N/A | #N/A
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | #N/A | 211 |  | #N/A | #N/A
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | #N/A | 212 |  | #N/A | #N/A
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | #N/A | 213 |  | #N/A | #N/A
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | #N/A | 214 |  | #N/A | #N/A
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | #N/A | 215 |  | #N/A | #N/A
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | #N/A | 216 |  | #N/A | #N/A
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | #N/A | 217 |  | #N/A | #N/A
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | #N/A | 218 |  | #N/A | #N/A
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | #N/A | 219 |  | #N/A | #N/A
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | #N/A | 220 |  | #N/A | #N/A
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | #N/A | 221 |  | #N/A | #N/A
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | #N/A | 222 |  | #N/A | #N/A
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | #N/A | 223 |  | #N/A | #N/A
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | #N/A | 224 |  | #N/A | #N/A
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | #N/A | 225 |  | #N/A | #N/A
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | #N/A | 226 |  | #N/A | #N/A
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | #N/A | 227 |  | #N/A | #N/A
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | #N/A | 228 |  | #N/A | #N/A
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | #N/A | 229 |  | #N/A | #N/A
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | #N/A | 230 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | #N/A | 231 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | #N/A | 232 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | #N/A | 233 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | #N/A | 234 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | #N/A | 235 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | #N/A | 236 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | #N/A | 237 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | #N/A | 238 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | #N/A | 239 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | #N/A | 240 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | #N/A | 241 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | #N/A | 242 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | #N/A | 243 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | #N/A | 244 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | #N/A | 245 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | #N/A | 246 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | #N/A | 247 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | #N/A | 248 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | #N/A | 249 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | #N/A | 250 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | #N/A | 251 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | #N/A | 252 |  | #N/A | #N/A
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | #N/A | 253 |  | #N/A | #N/A
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | #N/A | 254 |  | #N/A | #N/A
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | #N/A | 255 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | #N/A | 256 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | #N/A | 257 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | #N/A | 258 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | #N/A | 259 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | #N/A | 260 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | #N/A | 261 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | #N/A | 262 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | #N/A | 263 |  | #N/A | #N/A
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | #N/A | 264 |  | #N/A | #N/A
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | #N/A | 265 |  | #N/A | #N/A
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | #N/A | 266 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | #N/A | 267 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Boom system | A | 48 | #N/A | 268 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | #N/A | 269 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Structure | A | 48 | #N/A | 270 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | #N/A | 271 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | #N/A | 272 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | #N/A | 273 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | #N/A | 274 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | #N/A | 275 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | #N/A | 276 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | #N/A | 277 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | #N/A | 278 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | #N/A | 279 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | #N/A | 280 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | #N/A | 281 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | #N/A | 282 |  | #N/A | #N/A
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | #N/A | 283 |  | #N/A | #N/A
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | #N/A | 284 |  | #N/A | #N/A
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | #N/A | 285 |  | #N/A | #N/A
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | #N/A | 286 |  | #N/A | #N/A
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | #N/A | 287 |  | #N/A | #N/A
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | #N/A | 288 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | #N/A | 289 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | #N/A | 290 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | #N/A | 291 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | #N/A | 292 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | #N/A | 293 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | #N/A | 294 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | #N/A | 295 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | #N/A | 296 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | #N/A | 297 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | #N/A | 298 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | #N/A | 299 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | #N/A | 300 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | #N/A | 301 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | #N/A | 302 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | #N/A | 303 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | #N/A | 304 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | #N/A | 305 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | #N/A | 306 |  | #N/A | #N/A

## FA_SEHF
Failure Code | FA_SEHF |  |  |  | Number of Locations in failure code when defaults assigned: | 70 |  | Final Criticality Code |  | B | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | FINNED COIL HEAT EXCHANGER
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | Count | 54 | 13
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | Selected ID | 11 | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly | All pressure retaining Equipment and pipework for highly toxic substances | A
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | #N/A |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System | All pressure retaining Equipment and pipework with corrosion resistant linings | A |  | 54 | 13
Safety | H | 2 | 2 |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework | All pressure retaining Equipment and pipework associated with fire water delivery systems | A
Environmental | H | 2 | 2 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C = |  | B | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table | Bilge and ballast pipework | A
Production | - | 0 | #N/A |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing | All other pressure Equipment and pipework | C
Business | H | 2 | 2 |  |  | #N/A |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity | Supports for criticality A pressure systems | A
[6 empty] | 2 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity | Insulation installed on criticality A pressure systems | A
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity | Painting on criticality A pressure systems | A
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE | Bolting on criticality A pressure systems | A
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | All other supports, paint and bolting | C
|  |  | #N/A |  |  |  | Process Containment Integrity | All other pressure Equipment and pipework |  | C | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection | Mix of process and equipment coolers, modify for system |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | - | - | #N/A | 45 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | No | B | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No |  | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 1 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 2 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 3 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 4 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 5 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 6 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 7 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 8 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 9 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 10 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 11 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 12 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 13 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 13 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 13 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 13 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 13 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 13 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 13 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 13 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 13 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 13 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 13 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 13 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 13 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 13 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 13 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 13 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 13 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 13 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 13 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 13 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 13 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 13 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 13 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 13 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 13 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 13 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 13 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 13 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 13 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 13 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 13 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 13 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 13 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 13 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 13 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 13 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 13 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 13 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 13 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 13 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 13 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 13 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 13 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 13 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 13 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 13 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 13 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 13 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 13 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 13 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 13 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 13 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 13 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 13 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 13 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 13 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 13 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 13 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 13 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 13 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 13 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 13 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 13 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 13 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 13 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 13 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 13 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 13 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 13 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 13 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 13 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 13 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 13 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 13 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 13 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 13 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 13 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 13 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 13 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 13 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 13 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 13 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 13 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 13 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 13 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 13 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 13 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 13 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 13 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 13 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 13 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 13 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 13 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 13 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 13 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 13 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 13 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 13 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 13 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 13 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 13 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 13 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 13 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 13 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 13 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 13 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 13 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 13 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 13 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 13 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 13 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 13 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 13 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 13 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 13 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 13 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 13 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 13 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 13 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 13 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 13 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 13 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 13 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 13 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 13 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 13 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 13 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 13 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 13 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 13 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 13 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 13 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 13 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 13 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 13 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 13 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 13 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 13 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 13 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 13 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 13 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 13 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 13 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 13 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 13 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 13 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 13 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 13 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 13 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 13 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 13 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 13 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 13 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 13 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 13 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 13 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 13 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 13 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 13 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 13 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 13 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 13 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 13 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 13 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 13 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 13 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 13 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 13 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 13 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 13 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 13 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 13 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 13 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 13 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 13 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 13 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 13 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 13 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 13 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 13 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 13 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 13 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 13 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 13 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 13 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 13 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 13 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 13 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 13 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 13 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 13 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 13 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 13 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 13 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 13 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 13 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 13 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 13 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 13 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 13 | 306

## FA_SEHS
Failure Code | FA_SEHS |  |  |  | Number of Locations in failure code when defaults assigned: | 48 |  | Final Criticality Code |  | B | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | SPIRAL HEAT EXCHANGER
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | Count | 54 | 13
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | Selected ID | 11 | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly | All pressure retaining Equipment and pipework for highly toxic substances | A
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | #N/A |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System | All pressure retaining Equipment and pipework with corrosion resistant linings | A |  | 54 | 13
Safety | H | 2 | 2 |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework | All pressure retaining Equipment and pipework associated with fire water delivery systems | A
Environmental | H | 2 | 2 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C = |  | B | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table | Bilge and ballast pipework | A
Production | - | 0 | #N/A |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing | All other pressure Equipment and pipework | C
Business | H | 2 | 2 |  |  | #N/A |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity | Supports for criticality A pressure systems | A
[6 empty] | 2 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity | Insulation installed on criticality A pressure systems | A
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity | Painting on criticality A pressure systems | A
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE | Bolting on criticality A pressure systems | A
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | All other supports, paint and bolting | C
|  |  | #N/A |  |  |  | Process Containment Integrity | All other pressure Equipment and pipework |  | C | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection | Mix from seal plan coolers ro process |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | - | - | #N/A | 45 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | No | B | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No |  | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 1 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 2 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 3 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 4 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 5 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 6 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 7 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 8 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 9 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 10 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 11 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 12 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 13 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 13 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 13 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 13 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 13 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 13 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 13 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 13 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 13 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 13 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 13 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 13 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 13 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 13 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 13 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 13 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 13 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 13 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 13 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 13 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 13 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 13 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 13 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 13 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 13 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 13 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 13 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 13 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 13 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 13 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 13 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 13 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 13 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 13 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 13 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 13 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 13 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 13 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 13 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 13 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 13 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 13 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 13 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 13 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 13 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 13 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 13 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 13 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 13 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 13 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 13 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 13 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 13 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 13 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 13 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 13 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 13 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 13 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 13 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 13 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 13 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 13 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 13 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 13 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 13 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 13 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 13 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 13 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 13 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 13 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 13 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 13 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 13 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 13 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 13 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 13 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 13 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 13 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 13 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 13 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 13 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 13 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 13 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 13 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 13 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 13 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 13 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 13 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 13 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 13 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 13 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 13 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 13 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 13 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 13 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 13 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 13 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 13 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 13 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 13 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 13 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 13 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 13 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 13 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 13 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 13 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 13 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 13 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 13 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 13 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 13 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 13 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 13 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 13 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 13 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 13 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 13 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 13 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 13 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 13 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 13 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 13 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 13 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 13 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 13 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 13 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 13 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 13 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 13 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 13 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 13 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 13 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 13 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 13 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 13 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 13 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 13 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 13 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 13 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 13 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 13 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 13 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 13 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 13 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 13 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 13 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 13 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 13 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 13 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 13 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 13 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 13 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 13 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 13 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 13 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 13 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 13 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 13 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 13 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 13 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 13 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 13 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 13 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 13 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 13 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 13 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 13 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 13 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 13 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 13 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 13 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 13 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 13 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 13 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 13 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 13 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 13 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 13 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 13 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 13 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 13 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 13 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 13 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 13 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 13 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 13 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 13 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 13 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 13 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 13 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 13 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 13 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 13 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 13 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 13 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 13 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 13 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 13 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 13 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 13 | 306

## FA_SEHT
Failure Code | FA_SEHT |  |  |  | Number of Locations in failure code when defaults assigned: | 51 |  | Final Criticality Code |  | B | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | SHELL & TUBE HEAT EXCHANGER
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | Count | 54 | 13
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | Selected ID | 11 | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly | All pressure retaining Equipment and pipework for highly toxic substances | A
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | #N/A |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System | All pressure retaining Equipment and pipework with corrosion resistant linings | A |  | 54 | 13
Safety | G | 4 | 5 |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework | All pressure retaining Equipment and pipework associated with fire water delivery systems | A
Environmental | H | 2 | 2 |  | Elements contributing to CMMS Location Criticality rating | 4 |  | Derived SAP A/B/C = |  | B | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table | Bilge and ballast pipework | A
Production | - | 0 | #N/A |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing | All other pressure Equipment and pipework | C
Business | G | 4 | 5 |  |  | #N/A |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity | Supports for criticality A pressure systems | A
[6 empty] | 4 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity | Insulation installed on criticality A pressure systems | A
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity | Painting on criticality A pressure systems | A
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE | Bolting on criticality A pressure systems | A
Loss of Function | G | 4 | 5 | 71 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | All other supports, paint and bolting | C
|  |  | #N/A |  |  |  | Process Containment Integrity | All other pressure Equipment and pipework |  | C | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection | Mixed duty, may need to escalate based on system |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | - | - | #N/A | 45 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | No | B | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No |  | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | G | 4 | 5 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 1 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 2 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 3 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 4 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 5 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 6 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 7 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 8 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 9 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 10 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 11 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 12 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 13 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 13 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 13 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 13 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 13 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 13 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 13 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 13 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 13 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 13 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 13 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 13 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 13 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 13 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 13 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 13 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 13 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 13 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 13 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 13 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 13 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 13 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 13 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 13 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 13 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 13 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 13 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 13 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 13 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 13 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 13 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 13 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 13 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 13 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 13 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 13 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 13 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 13 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 13 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 13 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 13 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 13 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 13 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 13 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 13 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 13 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 13 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 13 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 13 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 13 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 13 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 13 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 13 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 13 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 13 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 13 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 13 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 13 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 13 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 13 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 13 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 13 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 13 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 13 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 13 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 13 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 13 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 13 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 13 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 13 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 13 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 13 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 13 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 13 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 13 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 13 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 13 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 13 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 13 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 13 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 13 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 13 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 13 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 13 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 13 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 13 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 13 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 13 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 13 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 13 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 13 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 13 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 13 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 13 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 13 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 13 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 13 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 13 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 13 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 13 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 13 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 13 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 13 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 13 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 13 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 13 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 13 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 13 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 13 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 13 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 13 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 13 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 13 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 13 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 13 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 13 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 13 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 13 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 13 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 13 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 13 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 13 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 13 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 13 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 13 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 13 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 13 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 13 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 13 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 13 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 13 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 13 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 13 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 13 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 13 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 13 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 13 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 13 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 13 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 13 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 13 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 13 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 13 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 13 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 13 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 13 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 13 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 13 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 13 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 13 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 13 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 13 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 13 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 13 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 13 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 13 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 13 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 13 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 13 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 13 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 13 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 13 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 13 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 13 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 13 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 13 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 13 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 13 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 13 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 13 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 13 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 13 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 13 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 13 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 13 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 13 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 13 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 13 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 13 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 13 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 13 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 13 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 13 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 13 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 13 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 13 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 13 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 13 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 13 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 13 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 13 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 13 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 13 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 13 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 13 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 13 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 13 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 13 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 13 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 13 | 306

## FA_SEL
Failure Code | FA_SEL |  |  |  | Number of Locations in failure code when defaults assigned: | 53 |  | Final Criticality Code |  | B | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | FLAME ARRESTOR
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | For Equipment in Zone 0 and Zone 1 | A | Count | 54 | 3
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity | For Equipment in Zone 2 | B | Selected ID | 40 | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8 |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System |  |  |  | 54 | 3
Safety | E | 8 | 11 |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework
Environmental | H | 2 | 2 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C = |  | B | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table
Production | H | 2 | 2 |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing
Business | H | 2 | 2 |  |  | 2 |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity
[6 empty] | 2 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE
Loss of Function | E | 8 | 11 | 69 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps)
|  |  | #N/A |  |  |  | Ignition Prevention | For Equipment in Zone 2 |  | B | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection | May be able to downgrade if not in hazardous zone, argument is if its not zone 2 why have a flame arrestor? Hazardous zone schedule may help with parent tags for pieces of equipment |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 0 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 0 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 0 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 0 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 0 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 0 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 0 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 0 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 0 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 0 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 0 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 0 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 0 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 0 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 0 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 0 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 0 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 0 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 0 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 0 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 0 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 0 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 0 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 0 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 0 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 0 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 0 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 0 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 0 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 0 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 0 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 0 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 0 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 0 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 0 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 0 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 0 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 0 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 0 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 0 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 0 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 0 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 0 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 0 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 0 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 0 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 0 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 0 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 0 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 0 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 0 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 0 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 0 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 0 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 0 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 0 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 0 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 0 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 0 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 0 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 0 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 0 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 0 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 0 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 0 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 0 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 0 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 0 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 0 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 0 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 0 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 0 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 0 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 0 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 0 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 0 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 0 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 0 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 0 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 0 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 0 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 0 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 0 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 0 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 0 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 0 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 0 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 0 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 0 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 0 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 0 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 0 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 0 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 0 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 0 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 0 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 0 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 0 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 0 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 0 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 0 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 0 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 0 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 0 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 0 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 0 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 0 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 0 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 0 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 0 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 0 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 0 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 0 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 0 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 0 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 0 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 0 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 0 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 0 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 0 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 0 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 0 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 0 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 0 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 0 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 0 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 0 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 0 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 1 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 2 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 3 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 3 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 3 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 3 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 3 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 3 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 3 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 3 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 3 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 3 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 3 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 3 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 3 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 3 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 3 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 3 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 3 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 3 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 3 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 3 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 3 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 3 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 3 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 3 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 3 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 3 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 3 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 3 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 3 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 3 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 3 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 3 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 3 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 3 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 3 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 3 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 3 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 3 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 3 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 3 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 3 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 3 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 3 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 3 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 3 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 3 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 3 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 3 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 3 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 3 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 3 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 3 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 3 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 3 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 3 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 3 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 3 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 3 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 3 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 3 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 3 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 3 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 3 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 3 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 3 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 3 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 3 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 3 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 3 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 3 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 3 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 3 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 3 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 3 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 3 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 3 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 3 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 3 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 3 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 3 | 306

## FA_SEM
Failure Code | FA_SEM |  |  |  | Number of Locations in failure code when defaults assigned: | 5 |  | Final Criticality Code |  | A | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | FLARE
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | Blowdown valves in hazardous or toxic duty | A | Count | 54 | 20
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity | Blowdown valves in non-hazardous, nontoxic duty | B | Selected ID | 17 | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8 |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System | All other FOVs | B |  | 54 | 20
Safety | E | 8 | 11 |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework | HP Flare KO Drum | A
Environmental | G | 4 | 5 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C = |  | A | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A
Production | E | 8 | 11 |  |  | 4 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing | HP Flare KO Drum Heaters | A
Business | F | 6 | 8 |  |  | 8 |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity | LP Flare KO Drum | A
[6 empty] | 6 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE | Flare tip ignition systems | A
Loss of Function | E | 8 | 11 | 69 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Flare system XXVs that are not covered under FOVs | A
|  |  | #N/A |  |  |  | Blowdown vent and flare | Flare tips |  | A | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages | Flare tips | A
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading | Any Equipment that maintains the barrier between wet and dry fluids | A
|  |  | #N/A |  |  |  | Comment on barrier selection | Flare tips defined as A, flare stack assumed to be A as P4-C support to crit A pressure systems |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare | Other vents | C
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security | Equipment providing early indication of blockages within flare header | A
Loss of Function | G | 4 | 5 | 71 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated.
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes | Flare pipework and headers (align with barrier P4-C) | A
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | E | 8 | 11 | 69 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | No | B | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No |  | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | F | 6 | 8 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 0 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 0 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 0 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 0 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 0 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 0 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 0 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 0 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 0 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 0 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 0 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 0 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 0 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 0 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 0 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 0 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 0 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 0 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 0 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 0 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 0 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 0 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 0 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 0 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 0 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 0 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 0 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 0 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 0 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 0 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 0 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 0 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 0 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 0 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 0 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 0 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 0 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 0 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 0 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 0 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 0 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 0 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 0 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 0 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 0 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 0 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 0 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 0 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 0 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 0 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 0 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 0 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 0 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 0 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 0 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 0 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 0 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 0 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 0 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 0 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 0 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 0 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 0 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 0 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 0 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 0 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 1 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 2 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 3 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 4 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 5 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 6 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 7 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 8 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 9 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 10 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 11 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 12 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 13 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 14 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 15 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 16 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 17 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 18 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 19 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 20 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 20 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 20 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 20 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 20 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 20 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 20 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 20 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 20 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 20 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 20 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 20 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 20 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 20 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 20 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 20 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 20 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 20 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 20 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 20 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 20 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 20 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 20 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 20 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 20 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 20 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 20 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 20 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 20 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 20 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 20 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 20 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 20 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 20 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 20 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 20 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 20 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 20 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 20 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 20 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 20 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 20 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 20 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 20 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 20 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 20 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 20 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 20 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 20 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 20 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 20 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 20 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 20 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 20 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 20 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 20 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 20 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 20 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 20 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 20 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 20 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 20 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 20 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 20 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 20 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 20 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 20 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 20 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 20 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 20 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 20 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 20 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 20 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 20 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 20 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 20 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 20 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 20 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 20 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 20 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 20 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 20 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 20 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 20 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 20 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 20 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 20 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 20 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 20 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 20 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 20 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 20 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 20 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 20 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 20 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 20 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 20 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 20 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 20 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 20 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 20 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 20 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 20 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 20 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 20 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 20 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 20 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 20 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 20 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 20 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 20 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 20 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 20 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 20 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 20 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 20 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 20 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 20 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 20 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 20 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 20 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 20 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 20 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 20 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 20 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 20 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 20 | 306

## FA_SENF
Failure Code | FA_SENF |  |  |  | Number of Locations in failure code when defaults assigned: | 4 |  | Final Criticality Code |  | B | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | FIRED HEATER FURNACE
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | For Equipment in Zone 0 and Zone 1 | A | Count | 54 | 3
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity | For Equipment in Zone 2 | B | Selected ID | 40 | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | #N/A |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System |  |  |  | 54 | 3
Safety | H | 2 | 2 |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework
Environmental | G | 4 | 5 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C = |  | B | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table
Production | - | 0 | #N/A |  |  | 4 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing
Business | G | 4 | 5 |  |  | #N/A |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity
[6 empty] | 4 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps)
|  |  | #N/A |  |  |  | Ignition Prevention | For Equipment in Zone 2 |  | B | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection | Assuming hot surface potential, but otherwise might not be classified as MAH |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security
Loss of Function | G | 4 | 5 | 71 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | - | - | #N/A | 45 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | No | B | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No |  | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | G | 4 | 5 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 0 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 0 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 0 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 0 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 0 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 0 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 0 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 0 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 0 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 0 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 0 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 0 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 0 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 0 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 0 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 0 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 0 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 0 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 0 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 0 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 0 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 0 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 0 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 0 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 0 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 0 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 0 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 0 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 0 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 0 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 0 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 0 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 0 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 0 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 0 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 0 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 0 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 0 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 0 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 0 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 0 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 0 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 0 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 0 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 0 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 0 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 0 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 0 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 0 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 0 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 0 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 0 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 0 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 0 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 0 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 0 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 0 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 0 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 0 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 0 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 0 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 0 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 0 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 0 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 0 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 0 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 0 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 0 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 0 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 0 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 0 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 0 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 0 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 0 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 0 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 0 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 0 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 0 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 0 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 0 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 0 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 0 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 0 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 0 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 0 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 0 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 0 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 0 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 0 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 0 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 0 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 0 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 0 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 0 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 0 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 0 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 0 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 0 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 0 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 0 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 0 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 0 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 0 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 0 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 0 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 0 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 0 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 0 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 0 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 0 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 0 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 0 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 0 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 0 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 0 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 0 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 0 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 0 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 0 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 0 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 0 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 0 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 0 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 0 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 0 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 0 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 0 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 0 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 1 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 2 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 3 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 3 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 3 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 3 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 3 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 3 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 3 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 3 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 3 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 3 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 3 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 3 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 3 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 3 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 3 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 3 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 3 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 3 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 3 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 3 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 3 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 3 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 3 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 3 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 3 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 3 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 3 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 3 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 3 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 3 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 3 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 3 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 3 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 3 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 3 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 3 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 3 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 3 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 3 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 3 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 3 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 3 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 3 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 3 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 3 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 3 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 3 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 3 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 3 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 3 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 3 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 3 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 3 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 3 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 3 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 3 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 3 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 3 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 3 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 3 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 3 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 3 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 3 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 3 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 3 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 3 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 3 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 3 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 3 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 3 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 3 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 3 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 3 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 3 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 3 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 3 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 3 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 3 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 3 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 3 | 306

## FA_SEPA
Failure Code | FA_SEPA |  |  |  | Number of Locations in failure code when defaults assigned: | 192 |  | Final Criticality Code |  | C | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | ACCUMULATOR
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | Count | 54 | 13
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | Selected ID | 11 | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly | All pressure retaining Equipment and pipework for highly toxic substances | A
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8 |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System | All pressure retaining Equipment and pipework with corrosion resistant linings | A |  | 54 | 13
Safety | E | 8 | 11 |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework | All pressure retaining Equipment and pipework associated with fire water delivery systems | A
Environmental | H | 2 | 2 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C = |  | C | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table | Bilge and ballast pipework | A
Production | H | 2 | 2 |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing | All other pressure Equipment and pipework | C
Business | G | 4 | 5 |  |  | 2 |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity | Supports for criticality A pressure systems | A
[6 empty] | 4 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity | Insulation installed on criticality A pressure systems | A
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity | Painting on criticality A pressure systems | A
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE | Bolting on criticality A pressure systems | A
Loss of Function | E | 8 | 11 | 69 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | All other supports, paint and bolting | C
|  |  | #N/A |  |  |  | Process Containment Integrity | All other pressure Equipment and pipework |  | C | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection | Escalate for hazardous fluids |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | G | 4 | 5 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 1 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 2 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 3 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 4 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 5 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 6 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 7 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 8 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 9 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 10 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 11 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 12 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 13 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 13 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 13 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 13 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 13 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 13 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 13 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 13 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 13 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 13 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 13 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 13 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 13 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 13 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 13 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 13 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 13 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 13 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 13 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 13 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 13 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 13 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 13 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 13 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 13 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 13 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 13 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 13 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 13 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 13 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 13 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 13 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 13 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 13 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 13 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 13 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 13 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 13 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 13 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 13 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 13 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 13 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 13 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 13 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 13 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 13 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 13 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 13 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 13 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 13 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 13 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 13 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 13 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 13 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 13 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 13 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 13 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 13 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 13 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 13 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 13 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 13 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 13 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 13 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 13 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 13 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 13 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 13 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 13 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 13 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 13 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 13 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 13 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 13 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 13 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 13 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 13 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 13 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 13 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 13 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 13 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 13 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 13 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 13 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 13 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 13 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 13 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 13 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 13 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 13 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 13 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 13 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 13 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 13 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 13 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 13 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 13 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 13 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 13 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 13 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 13 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 13 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 13 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 13 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 13 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 13 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 13 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 13 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 13 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 13 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 13 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 13 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 13 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 13 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 13 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 13 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 13 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 13 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 13 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 13 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 13 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 13 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 13 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 13 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 13 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 13 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 13 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 13 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 13 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 13 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 13 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 13 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 13 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 13 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 13 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 13 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 13 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 13 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 13 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 13 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 13 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 13 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 13 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 13 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 13 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 13 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 13 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 13 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 13 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 13 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 13 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 13 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 13 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 13 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 13 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 13 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 13 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 13 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 13 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 13 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 13 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 13 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 13 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 13 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 13 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 13 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 13 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 13 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 13 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 13 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 13 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 13 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 13 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 13 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 13 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 13 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 13 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 13 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 13 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 13 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 13 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 13 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 13 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 13 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 13 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 13 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 13 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 13 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 13 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 13 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 13 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 13 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 13 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 13 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 13 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 13 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 13 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 13 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 13 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 13 | 306

## FA_SEPC
Failure Code | FA_SEPC |  |  |  | Number of Locations in failure code when defaults assigned: | 59 |  | Final Criticality Code |  | C | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | CYLINDER
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | Count | 54 | 13
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | Selected ID | 11 | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly | All pressure retaining Equipment and pipework for highly toxic substances | A
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4 |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System | All pressure retaining Equipment and pipework with corrosion resistant linings | A |  | 54 | 13
Safety | H | 1 | 1 |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework | All pressure retaining Equipment and pipework associated with fire water delivery systems | A
Environmental | H | 1 | 1 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C = |  | C | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table | Bilge and ballast pipework | A
Production | H | 1 | 1 |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing | All other pressure Equipment and pipework | C
Business | G | 3 | 4 |  |  | 2 |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity | Supports for criticality A pressure systems | A
[6 empty] | 4 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity | Insulation installed on criticality A pressure systems | A
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity | Painting on criticality A pressure systems | A
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE | Bolting on criticality A pressure systems | A
Loss of Function | H | 1 | 1 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | All other supports, paint and bolting | C
|  |  | #N/A |  |  |  | Process Containment Integrity | All other pressure Equipment and pipework |  | C | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection | Escalate for hazardous fluids? |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security
Loss of Function | H | 1 | 1 | 72 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | H | 1 | 1 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | G | 3 | 4 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 1 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 2 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 3 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 4 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 5 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 6 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 7 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 8 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 9 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 10 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 11 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 12 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 13 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 13 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 13 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 13 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 13 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 13 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 13 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 13 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 13 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 13 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 13 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 13 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 13 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 13 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 13 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 13 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 13 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 13 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 13 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 13 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 13 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 13 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 13 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 13 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 13 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 13 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 13 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 13 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 13 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 13 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 13 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 13 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 13 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 13 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 13 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 13 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 13 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 13 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 13 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 13 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 13 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 13 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 13 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 13 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 13 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 13 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 13 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 13 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 13 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 13 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 13 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 13 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 13 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 13 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 13 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 13 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 13 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 13 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 13 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 13 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 13 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 13 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 13 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 13 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 13 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 13 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 13 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 13 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 13 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 13 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 13 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 13 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 13 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 13 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 13 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 13 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 13 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 13 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 13 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 13 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 13 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 13 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 13 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 13 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 13 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 13 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 13 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 13 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 13 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 13 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 13 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 13 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 13 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 13 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 13 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 13 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 13 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 13 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 13 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 13 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 13 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 13 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 13 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 13 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 13 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 13 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 13 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 13 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 13 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 13 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 13 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 13 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 13 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 13 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 13 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 13 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 13 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 13 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 13 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 13 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 13 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 13 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 13 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 13 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 13 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 13 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 13 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 13 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 13 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 13 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 13 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 13 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 13 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 13 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 13 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 13 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 13 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 13 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 13 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 13 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 13 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 13 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 13 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 13 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 13 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 13 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 13 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 13 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 13 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 13 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 13 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 13 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 13 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 13 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 13 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 13 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 13 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 13 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 13 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 13 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 13 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 13 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 13 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 13 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 13 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 13 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 13 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 13 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 13 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 13 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 13 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 13 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 13 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 13 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 13 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 13 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 13 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 13 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 13 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 13 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 13 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 13 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 13 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 13 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 13 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 13 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 13 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 13 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 13 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 13 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 13 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 13 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 13 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 13 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 13 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 13 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 13 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 13 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 13 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 13 | 306

## FA_SEPHC
Failure Code | FA_SEPHC |  |  |  | Number of Locations in failure code when defaults assigned: | 2 |  | Final Criticality Code |  | B | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | CONDENSER VESSEL
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | Count | 54 | 13
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | Selected ID | 11 | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly | All pressure retaining Equipment and pipework for highly toxic substances | A
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | #N/A |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System | All pressure retaining Equipment and pipework with corrosion resistant linings | A |  | 54 | 13
Safety | H | 2 | 2 |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework | All pressure retaining Equipment and pipework associated with fire water delivery systems | A
Environmental | H | 2 | 2 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C = |  | B | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table | Bilge and ballast pipework | A
Production | - | 0 | #N/A |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing | All other pressure Equipment and pipework | C
Business | G | 4 | 5 |  |  | #N/A |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity | Supports for criticality A pressure systems | A
[6 empty] | 4 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity | Insulation installed on criticality A pressure systems | A
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity | Painting on criticality A pressure systems | A
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE | Bolting on criticality A pressure systems | A
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | All other supports, paint and bolting | C
|  |  | #N/A |  |  |  | Process Containment Integrity | All other pressure Equipment and pipework |  | C | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection | Escalate for hazardous fluids? |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | - | - | #N/A | 45 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | No | B | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No |  | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | G | 4 | 5 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 1 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 2 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 3 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 4 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 5 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 6 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 7 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 8 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 9 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 10 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 11 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 12 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 13 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 13 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 13 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 13 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 13 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 13 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 13 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 13 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 13 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 13 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 13 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 13 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 13 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 13 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 13 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 13 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 13 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 13 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 13 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 13 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 13 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 13 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 13 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 13 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 13 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 13 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 13 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 13 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 13 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 13 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 13 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 13 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 13 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 13 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 13 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 13 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 13 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 13 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 13 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 13 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 13 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 13 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 13 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 13 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 13 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 13 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 13 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 13 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 13 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 13 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 13 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 13 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 13 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 13 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 13 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 13 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 13 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 13 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 13 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 13 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 13 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 13 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 13 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 13 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 13 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 13 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 13 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 13 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 13 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 13 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 13 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 13 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 13 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 13 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 13 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 13 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 13 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 13 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 13 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 13 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 13 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 13 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 13 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 13 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 13 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 13 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 13 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 13 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 13 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 13 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 13 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 13 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 13 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 13 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 13 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 13 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 13 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 13 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 13 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 13 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 13 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 13 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 13 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 13 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 13 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 13 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 13 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 13 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 13 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 13 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 13 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 13 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 13 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 13 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 13 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 13 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 13 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 13 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 13 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 13 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 13 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 13 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 13 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 13 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 13 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 13 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 13 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 13 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 13 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 13 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 13 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 13 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 13 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 13 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 13 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 13 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 13 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 13 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 13 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 13 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 13 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 13 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 13 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 13 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 13 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 13 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 13 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 13 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 13 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 13 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 13 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 13 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 13 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 13 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 13 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 13 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 13 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 13 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 13 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 13 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 13 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 13 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 13 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 13 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 13 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 13 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 13 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 13 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 13 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 13 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 13 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 13 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 13 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 13 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 13 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 13 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 13 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 13 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 13 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 13 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 13 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 13 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 13 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 13 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 13 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 13 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 13 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 13 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 13 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 13 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 13 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 13 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 13 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 13 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 13 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 13 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 13 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 13 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 13 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 13 | 306

## FA_SEPHS
Failure Code | FA_SEPHS |  |  |  | Number of Locations in failure code when defaults assigned: | 190 |  | Final Criticality Code |  | B | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | SEPARATOR VESSEL
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | Count | 54 | 13
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | Selected ID | 11 | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly | All pressure retaining Equipment and pipework for highly toxic substances | A
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | #N/A |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System | All pressure retaining Equipment and pipework with corrosion resistant linings | A |  | 54 | 13
Safety | H | 2 | 2 |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework | All pressure retaining Equipment and pipework associated with fire water delivery systems | A
Environmental | H | 2 | 2 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C = |  | B | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table | Bilge and ballast pipework | A
Production | - | 0 | #N/A |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing | All other pressure Equipment and pipework | C
Business | G | 4 | 5 |  |  | #N/A |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity | Supports for criticality A pressure systems | A
[6 empty] | 4 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity | Insulation installed on criticality A pressure systems | A
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity | Painting on criticality A pressure systems | A
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE | Bolting on criticality A pressure systems | A
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | All other supports, paint and bolting | C
|  |  | #N/A |  |  |  | Process Containment Integrity | All other pressure Equipment and pipework |  | C | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection | Compressor suction seps to air dryer vessels in compressors, so escalate by system |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | - | - | #N/A | 45 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | No | B | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No |  | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | G | 4 | 5 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 1 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 2 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 3 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 4 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 5 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 6 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 7 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 8 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 9 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 10 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 11 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 12 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 13 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 13 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 13 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 13 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 13 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 13 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 13 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 13 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 13 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 13 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 13 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 13 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 13 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 13 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 13 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 13 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 13 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 13 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 13 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 13 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 13 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 13 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 13 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 13 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 13 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 13 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 13 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 13 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 13 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 13 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 13 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 13 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 13 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 13 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 13 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 13 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 13 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 13 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 13 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 13 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 13 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 13 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 13 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 13 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 13 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 13 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 13 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 13 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 13 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 13 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 13 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 13 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 13 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 13 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 13 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 13 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 13 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 13 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 13 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 13 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 13 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 13 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 13 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 13 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 13 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 13 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 13 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 13 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 13 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 13 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 13 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 13 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 13 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 13 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 13 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 13 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 13 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 13 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 13 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 13 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 13 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 13 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 13 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 13 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 13 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 13 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 13 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 13 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 13 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 13 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 13 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 13 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 13 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 13 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 13 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 13 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 13 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 13 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 13 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 13 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 13 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 13 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 13 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 13 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 13 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 13 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 13 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 13 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 13 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 13 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 13 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 13 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 13 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 13 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 13 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 13 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 13 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 13 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 13 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 13 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 13 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 13 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 13 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 13 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 13 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 13 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 13 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 13 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 13 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 13 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 13 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 13 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 13 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 13 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 13 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 13 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 13 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 13 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 13 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 13 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 13 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 13 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 13 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 13 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 13 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 13 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 13 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 13 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 13 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 13 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 13 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 13 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 13 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 13 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 13 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 13 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 13 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 13 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 13 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 13 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 13 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 13 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 13 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 13 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 13 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 13 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 13 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 13 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 13 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 13 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 13 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 13 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 13 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 13 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 13 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 13 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 13 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 13 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 13 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 13 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 13 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 13 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 13 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 13 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 13 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 13 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 13 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 13 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 13 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 13 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 13 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 13 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 13 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 13 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 13 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 13 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 13 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 13 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 13 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 13 | 306

## FA_SES
Failure Code | FA_SES |  |  |  | Number of Locations in failure code when defaults assigned: | 72 |  | Final Criticality Code |  | A | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | PULSATION DAMPENER
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | Count | 54 | 13
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | Selected ID | 11 | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly | All pressure retaining Equipment and pipework for highly toxic substances | A
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4 |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System | All pressure retaining Equipment and pipework with corrosion resistant linings | A |  | 54 | 13
Safety | G | 4 | 5 |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework | All pressure retaining Equipment and pipework associated with fire water delivery systems | A
Environmental | H | 2 | 2 |  | Elements contributing to CMMS Location Criticality rating | 4 |  | Derived SAP A/B/C = |  | A | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table | Bilge and ballast pipework | A
Production | G | 4 | 5 |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing | All other pressure Equipment and pipework | C
Business | H | 2 | 2 |  |  | 4 |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity | Supports for criticality A pressure systems | A
[6 empty] | 2 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity | Insulation installed on criticality A pressure systems | A
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity | Painting on criticality A pressure systems | A
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE | Bolting on criticality A pressure systems | A
Loss of Function | G | 4 | 5 | 71 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | All other supports, paint and bolting | C
|  |  | #N/A |  |  |  | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C |  | A | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection | Mainly chemical with some process |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | G | 4 | 5 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 1 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 2 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 3 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 4 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 5 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 6 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 7 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 8 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 9 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 10 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 11 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 12 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 13 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 13 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 13 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 13 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 13 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 13 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 13 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 13 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 13 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 13 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 13 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 13 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 13 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 13 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 13 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 13 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 13 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 13 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 13 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 13 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 13 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 13 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 13 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 13 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 13 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 13 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 13 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 13 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 13 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 13 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 13 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 13 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 13 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 13 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 13 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 13 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 13 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 13 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 13 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 13 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 13 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 13 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 13 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 13 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 13 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 13 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 13 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 13 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 13 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 13 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 13 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 13 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 13 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 13 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 13 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 13 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 13 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 13 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 13 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 13 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 13 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 13 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 13 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 13 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 13 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 13 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 13 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 13 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 13 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 13 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 13 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 13 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 13 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 13 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 13 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 13 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 13 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 13 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 13 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 13 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 13 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 13 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 13 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 13 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 13 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 13 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 13 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 13 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 13 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 13 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 13 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 13 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 13 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 13 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 13 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 13 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 13 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 13 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 13 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 13 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 13 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 13 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 13 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 13 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 13 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 13 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 13 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 13 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 13 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 13 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 13 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 13 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 13 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 13 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 13 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 13 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 13 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 13 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 13 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 13 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 13 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 13 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 13 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 13 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 13 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 13 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 13 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 13 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 13 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 13 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 13 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 13 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 13 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 13 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 13 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 13 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 13 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 13 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 13 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 13 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 13 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 13 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 13 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 13 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 13 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 13 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 13 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 13 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 13 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 13 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 13 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 13 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 13 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 13 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 13 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 13 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 13 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 13 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 13 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 13 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 13 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 13 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 13 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 13 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 13 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 13 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 13 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 13 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 13 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 13 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 13 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 13 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 13 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 13 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 13 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 13 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 13 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 13 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 13 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 13 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 13 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 13 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 13 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 13 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 13 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 13 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 13 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 13 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 13 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 13 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 13 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 13 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 13 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 13 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 13 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 13 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 13 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 13 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 13 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 13 | 306

## FA_SETAC
Failure Code | FA_SETAC |  |  |  | Number of Locations in failure code when defaults assigned: | 60 |  | Final Criticality Code |  | A | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | CLOSED ROOF ATMOSPHERIC TANK
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | Export Booster Pumps | A | Count | 54 | 11
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity | Export Hose | A | Selected ID | 15 | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping | Marine Growth Prevention Equipment | B
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly | Cargo Tank Cleaning Systems | B
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | #N/A |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System | Cargo & Ballast Hydraulic Valve Control | A |  | 54 | 11
Safety | H | 2 | 2 |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework | Marine Hydraulic systems (pumps, power units and storage tanks) | B
Environmental | H | 2 | 2 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C = |  | A | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table | Void Tank Gas Detection | A
Production | - | 0 | #N/A |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing | Void Tank Dehumidification systems | B
Business | G | 4 | 5 |  |  | #N/A |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity | Hydrocarbon Tanks | A
[6 empty] | 4 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity | Ballast Tanks | A
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity | Void Tanks | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps)
|  |  | #N/A |  |  |  | Oil Storage & Offloading | Hydrocarbon Tanks |  | A | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection | Fuel, MEG, Condensate, lube oil, reservoirs included, demote if non-hazardous? |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | - | - | #N/A | 45 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | No | B | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No |  | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | G | 4 | 5 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 0 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 0 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 0 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 0 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 0 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 0 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 0 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 0 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 0 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 0 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 0 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 0 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 0 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 0 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 0 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 0 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 0 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 0 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 0 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 0 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 0 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 0 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 0 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 0 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 0 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 0 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 0 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 0 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 0 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 0 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 0 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 0 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 0 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 1 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 2 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 3 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 4 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 5 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 6 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 7 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 8 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 9 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 10 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 11 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 11 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 11 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 11 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 11 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 11 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 11 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 11 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 11 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 11 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 11 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 11 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 11 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 11 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 11 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 11 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 11 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 11 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 11 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 11 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 11 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 11 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 11 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 11 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 11 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 11 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 11 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 11 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 11 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 11 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 11 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 11 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 11 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 11 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 11 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 11 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 11 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 11 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 11 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 11 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 11 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 11 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 11 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 11 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 11 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 11 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 11 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 11 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 11 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 11 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 11 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 11 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 11 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 11 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 11 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 11 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 11 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 11 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 11 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 11 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 11 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 11 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 11 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 11 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 11 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 11 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 11 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 11 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 11 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 11 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 11 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 11 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 11 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 11 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 11 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 11 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 11 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 11 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 11 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 11 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 11 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 11 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 11 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 11 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 11 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 11 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 11 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 11 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 11 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 11 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 11 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 11 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 11 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 11 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 11 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 11 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 11 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 11 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 11 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 11 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 11 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 11 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 11 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 11 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 11 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 11 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 11 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 11 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 11 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 11 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 11 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 11 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 11 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 11 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 11 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 11 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 11 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 11 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 11 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 11 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 11 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 11 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 11 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 11 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 11 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 11 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 11 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 11 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 11 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 11 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 11 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 11 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 11 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 11 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 11 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 11 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 11 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 11 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 11 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 11 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 11 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 11 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 11 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 11 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 11 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 11 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 11 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 11 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 11 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 11 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 11 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 11 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 11 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 11 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 11 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 11 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 11 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 11 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 11 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 11 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 11 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 11 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 11 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 11 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 11 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 11 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 11 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 11 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 11 | 306

## FA_SETAP
Failure Code | FA_SETAP |  |  |  | Number of Locations in failure code when defaults assigned: | 40 |  | Final Criticality Code |  | B | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | PIT / SUMP
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | Count | 54 | 6
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 1 | 2 | Stability loading control & watertight integrity | Secondary Structures - Single component failure results in object dropping >3m | A | Selected ID | 1 | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 2 | 3 | Station Keeping | Secondary Structures - Single component failure has no immediate consequence | C
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 3 | 4 | Swivel Stack Assembly | Tertiary Structures - Failure may result in fall >3m | A
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | #N/A |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 4 | 5 | Swivel Fluid Barrier System | Tertiary Structures - Failure may result in fall 1 - 3m | B |  | 54 | 6
Safety | H | 2 | 2 |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 5 | 6 | Swivel/Turret Pipework | Tertiary Structures - Failure may result in fall <1m | C
Environmental | G | 4 | 5 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C = |  | B | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 6 | 7 | Turret Chain Table
Production | - | 0 | #N/A |  |  | 4 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 6 | 8 | Main Turret Bearing
Business | G | 4 | 5 |  |  | #N/A |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 6 | 9 | Wellhead integrity
[6 empty] | 4 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 6 | 10 | Subsea Integrity
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 6 | 11 | Process Containment Integrity
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 6 | 12 | Gas Turbine Packages & Hydrocarbon RE
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 6 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps)
|  |  | #N/A |  |  |  | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m |  | B | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 6 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 6 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection | Air comp oil sump to sewage pits |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 6 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 6 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 6 | 18 | Digital security
Loss of Function | G | 4 | 5 | 71 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 6 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 6 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 6 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 6 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 6 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 6 | 24 | Alarms & operator response
Loss of Function | - | - | #N/A | 45 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 6 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | No | B | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 6 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 6 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No |  | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 6 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 6 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 6 | 30 | Temporary refuge integrity
Loss of Function | G | 4 | 5 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 6 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 6 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 6 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 6 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 6 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 6 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 6 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 6 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 6 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 6 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 6 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 6 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 6 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 6 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 6 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 6 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 6 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 6 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 6 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 6 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 6 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 6 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 6 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 6 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 6 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 6 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 6 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 6 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 6 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 6 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 6 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 6 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 6 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 6 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 6 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 6 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 6 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 6 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 6 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 6 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 6 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 6 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 6 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 6 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 6 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 6 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 6 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 6 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 6 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 6 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 6 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 6 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 6 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 6 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 6 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 6 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 6 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 6 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 6 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 6 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 6 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 6 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 6 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 6 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 6 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 6 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 6 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 6 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 6 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 6 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 6 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 6 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 6 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 6 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 6 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 6 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 6 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 6 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 6 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 6 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 6 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 6 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 6 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 6 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 6 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 6 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 6 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 6 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 6 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 6 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 6 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 6 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 6 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 6 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 6 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 6 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 6 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 6 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 6 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 6 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 6 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 6 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 6 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 6 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 6 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 6 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 6 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 6 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 6 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 6 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 6 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 6 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 6 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 6 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 6 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 6 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 6 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 6 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 6 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 6 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 6 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 6 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 6 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 6 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 6 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 6 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 6 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 6 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 6 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 6 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 6 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 6 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 6 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 6 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 6 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 6 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 6 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 6 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 6 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 6 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 6 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 6 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 6 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 6 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 6 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 6 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 6 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 6 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 6 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 6 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 6 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 6 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 6 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 6 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 6 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 6 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 6 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 6 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 6 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 6 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 6 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 6 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 6 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 6 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 6 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 6 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 6 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 6 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 6 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 6 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 6 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 6 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 6 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 6 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 6 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 6 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 6 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 6 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 6 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 6 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 6 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 6 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 6 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 6 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 6 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 6 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 6 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 6 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 6 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 6 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 6 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 6 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 6 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 6 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 6 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 6 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 6 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 6 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 6 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 6 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 6 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 6 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 6 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 6 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 6 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 6 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 6 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 6 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 6 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 6 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 6 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 6 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 6 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 6 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 6 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 6 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 6 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 6 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 6 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 6 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 6 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 6 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 6 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 6 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 6 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 6 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 6 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 6 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 6 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 6 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 6 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 6 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 6 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 6 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 6 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 6 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 6 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 6 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 6 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 6 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 6 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 6 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 6 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 6 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 6 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 6 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 6 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 6 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 6 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 6 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 6 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 6 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 6 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 6 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 6 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 6 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 6 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 6 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 6 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 6 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 6 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 6 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 6 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 6 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 6 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 6 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 6 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 6 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 6 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 6 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 6 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 6 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 6 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 6 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 6 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 6 | 306

## FA_SETPC
Failure Code | FA_SETPC |  |  |  | Number of Locations in failure code when defaults assigned: | 11 |  | Final Criticality Code |  | A | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | CYLINDRICAL PRESSURISED TANK
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | Count | 54 | 13
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | Selected ID | 11 | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly | All pressure retaining Equipment and pipework for highly toxic substances | A
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10 |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System | All pressure retaining Equipment and pipework with corrosion resistant linings | A |  | 54 | 13
Safety | D | 10 | #N/A |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework | All pressure retaining Equipment and pipework associated with fire water delivery systems | A
Environmental | H | 2 | 2 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C = |  | A | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table | Bilge and ballast pipework | A
Production | G | 4 | 5 |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing | All other pressure Equipment and pipework | C
Business | F | 6 | 8 |  |  | 4 |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity | Supports for criticality A pressure systems | A
[6 empty] | 6 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity | Insulation installed on criticality A pressure systems | A
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity | Painting on criticality A pressure systems | A
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE | Bolting on criticality A pressure systems | A
Loss of Function | D | 10 | #N/A | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | All other supports, paint and bolting | C
|  |  | #N/A |  |  |  | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 |  | A | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection | Air receiver, water, air, seal oil, N2 tanks. Assume high pressure system until reviewed at detail level. |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | G | 4 | 5 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | F | 6 | 8 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 1 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 2 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 3 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 4 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 5 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 6 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 7 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 8 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 9 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 10 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 11 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 12 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 13 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 13 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 13 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 13 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 13 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 13 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 13 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 13 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 13 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 13 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 13 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 13 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 13 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 13 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 13 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 13 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 13 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 13 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 13 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 13 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 13 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 13 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 13 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 13 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 13 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 13 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 13 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 13 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 13 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 13 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 13 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 13 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 13 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 13 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 13 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 13 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 13 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 13 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 13 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 13 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 13 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 13 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 13 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 13 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 13 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 13 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 13 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 13 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 13 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 13 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 13 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 13 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 13 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 13 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 13 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 13 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 13 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 13 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 13 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 13 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 13 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 13 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 13 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 13 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 13 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 13 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 13 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 13 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 13 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 13 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 13 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 13 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 13 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 13 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 13 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 13 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 13 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 13 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 13 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 13 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 13 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 13 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 13 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 13 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 13 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 13 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 13 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 13 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 13 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 13 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 13 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 13 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 13 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 13 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 13 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 13 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 13 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 13 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 13 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 13 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 13 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 13 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 13 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 13 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 13 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 13 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 13 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 13 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 13 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 13 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 13 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 13 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 13 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 13 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 13 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 13 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 13 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 13 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 13 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 13 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 13 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 13 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 13 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 13 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 13 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 13 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 13 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 13 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 13 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 13 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 13 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 13 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 13 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 13 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 13 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 13 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 13 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 13 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 13 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 13 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 13 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 13 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 13 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 13 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 13 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 13 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 13 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 13 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 13 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 13 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 13 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 13 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 13 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 13 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 13 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 13 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 13 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 13 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 13 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 13 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 13 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 13 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 13 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 13 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 13 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 13 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 13 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 13 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 13 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 13 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 13 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 13 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 13 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 13 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 13 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 13 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 13 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 13 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 13 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 13 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 13 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 13 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 13 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 13 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 13 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 13 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 13 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 13 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 13 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 13 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 13 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 13 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 13 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 13 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 13 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 13 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 13 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 13 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 13 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 13 | 306

## FA_SEZ
Failure Code | FA_SEZ |  |  |  | Number of Locations in failure code when defaults assigned: | 64 |  | Final Criticality Code |  | C | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | SILENCER / MUFFLER
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | Count | 54 | 13
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | Selected ID | 11 | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly | All pressure retaining Equipment and pipework for highly toxic substances | A
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4 |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System | All pressure retaining Equipment and pipework with corrosion resistant linings | A |  | 54 | 13
Safety | H | 2 | 2 |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework | All pressure retaining Equipment and pipework associated with fire water delivery systems | A
Environmental | G | 4 | 5 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C = |  | C | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table | Bilge and ballast pipework | A
Production | H | 2 | 2 |  |  | 4 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing | All other pressure Equipment and pipework | C
Business | H | 2 | 2 |  |  | 2 |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity | Supports for criticality A pressure systems | A
[6 empty] | 2 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity | Insulation installed on criticality A pressure systems | A
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity | Painting on criticality A pressure systems | A
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE | Bolting on criticality A pressure systems | A
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | All other supports, paint and bolting | C
|  |  | #N/A |  |  |  | Process Containment Integrity | All other pressure Equipment and pipework |  | C | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection | Exhaust / vent systems (some intakes),loss of function has level F or below impact |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security
Loss of Function | G | 4 | 5 | 71 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 1 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 2 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 3 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 4 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 5 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 6 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 7 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 8 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 9 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 10 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 11 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 12 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 13 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 13 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 13 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 13 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 13 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 13 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 13 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 13 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 13 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 13 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 13 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 13 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 13 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 13 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 13 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 13 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 13 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 13 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 13 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 13 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 13 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 13 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 13 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 13 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 13 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 13 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 13 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 13 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 13 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 13 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 13 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 13 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 13 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 13 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 13 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 13 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 13 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 13 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 13 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 13 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 13 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 13 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 13 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 13 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 13 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 13 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 13 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 13 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 13 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 13 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 13 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 13 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 13 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 13 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 13 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 13 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 13 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 13 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 13 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 13 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 13 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 13 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 13 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 13 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 13 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 13 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 13 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 13 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 13 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 13 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 13 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 13 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 13 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 13 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 13 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 13 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 13 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 13 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 13 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 13 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 13 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 13 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 13 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 13 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 13 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 13 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 13 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 13 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 13 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 13 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 13 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 13 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 13 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 13 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 13 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 13 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 13 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 13 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 13 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 13 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 13 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 13 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 13 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 13 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 13 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 13 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 13 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 13 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 13 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 13 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 13 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 13 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 13 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 13 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 13 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 13 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 13 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 13 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 13 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 13 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 13 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 13 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 13 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 13 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 13 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 13 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 13 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 13 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 13 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 13 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 13 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 13 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 13 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 13 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 13 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 13 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 13 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 13 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 13 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 13 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 13 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 13 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 13 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 13 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 13 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 13 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 13 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 13 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 13 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 13 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 13 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 13 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 13 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 13 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 13 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 13 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 13 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 13 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 13 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 13 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 13 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 13 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 13 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 13 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 13 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 13 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 13 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 13 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 13 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 13 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 13 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 13 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 13 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 13 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 13 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 13 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 13 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 13 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 13 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 13 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 13 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 13 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 13 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 13 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 13 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 13 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 13 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 13 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 13 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 13 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 13 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 13 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 13 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 13 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 13 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 13 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 13 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 13 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 13 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 13 | 306

## FA_SQFC
Failure Code | FAILURE_CODE |  |  |  | Number of Locations in failure code when defaults assigned: |  |  | Final Criticality Code |  | A | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | FAILURE_CODE_DESCRIPTION
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | #N/A | #N/A | Count | 54 | #N/A
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | #N/A | 2 | Stability loading control & watertight integrity | #N/A | #N/A | Selected ID | #N/A | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | #N/A | 3 | Station Keeping | #N/A | #N/A
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | #N/A | 4 | Swivel Stack Assembly | #N/A | #N/A
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10 |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | #N/A | 5 | Swivel Fluid Barrier System | #N/A | #N/A |  | 54 | #N/A
Safety | A | 8 | 15 |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | #N/A | 6 | Swivel/Turret Pipework | #N/A | #N/A
Environmental | A | 8 | 15 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C = |  | A | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | #N/A | 7 | Turret Chain Table | #N/A | #N/A
Production | A | 8 | 15 |  |  | 10 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | #N/A | 8 | Main Turret Bearing | #N/A | #N/A
Business | A | 8 | 15 |  |  | 10 |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | #N/A | 9 | Wellhead integrity | #N/A | #N/A
[6 empty] | 10 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | #N/A | 10 | Subsea Integrity | #N/A | #N/A
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | #N/A | 11 | Process Containment Integrity | #N/A | #N/A
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | #N/A | 12 | Gas Turbine Packages & Hydrocarbon RE | #N/A | #N/A
Loss of Function | A | 8 | 15 | 65 | DEFAULT |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | #N/A | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | #N/A | #N/A
|  |  | #N/A | [6 empty] | C | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | #N/A | 14 | Diesel Driven Packages | #N/A | #N/A
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | #N/A | 15 | Oil Storage & Offloading | #N/A | #N/A
|  |  | #N/A |  |  |  | Comment on barrier selection |  |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | #N/A | 16 | Overpressure Protection | #N/A | #N/A
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | #N/A | 17 | Blowdown vent and flare | #N/A | #N/A
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | #N/A | 18 | Digital security | #N/A | #N/A
Loss of Function | A | 8 | 15 | 65 | DEFAULT | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | #N/A | 19 | Control systems - LoPs | #N/A | #N/A
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | #N/A | 20 | Control systems - non LoPs, LOPA initiating causes | #N/A | #N/A
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | #N/A | 21 | Control systems - all others | #N/A | #N/A
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | #N/A | 22 | SIS - LoP Components | #N/A | #N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | #N/A | 23 | SIS - Non LoP Components | #N/A | #N/A
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | #N/A | 24 | Alarms & operator response | #N/A | #N/A
Loss of Function | A | 8 | 15 | 65 | DEFAULT |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | #N/A | 25 | Collision Prevention | #N/A | #N/A
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | No | A | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | #N/A | 26 | Export tanker birthing and position monitoring | #N/A | #N/A
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | #N/A | 27 | Bunding, Open and Closed Hazardous Drains | #N/A | #N/A
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No |  | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | #N/A | 28 | Passive Fire Protection | #N/A | #N/A
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | #N/A | 29 | Blast Overpressure Protection | #N/A | #N/A
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | #N/A | 30 | Temporary refuge integrity | #N/A | #N/A
Loss of Function | A | 8 | 15 | 65 | DEFAULT |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | #N/A | 31 | Alarm Annunciation System: | #N/A | #N/A
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | #N/A | 32 | Personnel Address (PA) System | #N/A | #N/A
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | Yes | A | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | #N/A | 33 | Marine, Aircraft and Helicopter Radio System | #N/A | #N/A
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | #N/A | 34 | Telecommunications | #N/A | #N/A
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | #N/A | 35 | Electronic Muster System | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | #N/A | 36 | Facility Emergency Telephone & Hot line systems | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | #N/A | 37 | Facility radio system | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | #N/A | 38 | Emergency Power | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | #N/A | 39 | Emergency Lighting | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | #N/A | 40 | Ignition Prevention | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | #N/A | 41 | Inert Gas Blanketing | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | #N/A | 42 | Lifesaving Equipment | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | #N/A | 43 | Muster areas, escape and evacuation routes | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | #N/A | 44 | Lifeboats | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | #N/A | 45 | Means of escape to sea | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | #N/A | 46 | Helideck | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | #N/A | 47 | Rescue & Recovery Systems | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | #N/A | 48 | Cranes | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | #N/A | 49 | Lifting system | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | #N/A | 50 | Fire & Gas systems | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | #N/A | 51 | Emergency Shutdown Systems | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | #N/A | 52 | Riser ESDVs & EIVs | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | #N/A | 53 | Fire protection | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | #N/A | 54 | Miscellaneous fire protection systems | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | #N/A | 55 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | #N/A | 56 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | #N/A | 57 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | #N/A | 58 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | #N/A | 59 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | #N/A | 60 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | #N/A | 61 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | #N/A | 62 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | #N/A | 63 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | #N/A | 64 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | #N/A | 65 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | #N/A | 66 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | #N/A | 67 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | #N/A | 68 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | #N/A | 69 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | #N/A | 70 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | #N/A | 71 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | #N/A | 72 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | #N/A | 73 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | #N/A | 74 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | #N/A | 75 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | #N/A | 76 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | #N/A | 77 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | #N/A | 78 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | #N/A | 79 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | #N/A | 80 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | #N/A | 81 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | #N/A | 82 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | #N/A | 83 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | #N/A | 84 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | #N/A | 85 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | #N/A | 86 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | #N/A | 87 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | #N/A | 88 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | #N/A | 89 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | #N/A | 90 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | #N/A | 91 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | #N/A | 92 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | #N/A | 93 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | #N/A | 94 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | #N/A | 95 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | #N/A | 96 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | #N/A | 97 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | #N/A | 98 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | #N/A | 99 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | #N/A | 100 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | #N/A | 101 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | #N/A | 102 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | #N/A | 103 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | #N/A | 104 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | #N/A | 105 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | #N/A | 106 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | #N/A | 107 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | #N/A | 108 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | #N/A | 109 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | #N/A | 110 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | #N/A | 111 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | #N/A | 112 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | #N/A | 113 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | #N/A | 114 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | #N/A | 115 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | #N/A | 116 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | #N/A | 117 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | #N/A | 118 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | #N/A | 119 |  | #N/A | #N/A
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | #N/A | 120 |  | #N/A | #N/A
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | #N/A | 121 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | #N/A | 122 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | #N/A | 123 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | #N/A | 124 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | #N/A | 125 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | #N/A | 126 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | #N/A | 127 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | #N/A | 128 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | #N/A | 129 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | #N/A | 130 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | #N/A | 131 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | #N/A | 132 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | #N/A | 133 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | #N/A | 134 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | #N/A | 135 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | #N/A | 136 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | #N/A | 137 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | #N/A | 138 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | #N/A | 139 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | #N/A | 140 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | #N/A | 141 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | #N/A | 142 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | #N/A | 143 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | #N/A | 144 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | #N/A | 145 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | #N/A | 146 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | #N/A | 147 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | #N/A | 148 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | #N/A | 149 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | #N/A | 150 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | #N/A | 151 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | #N/A | 152 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | #N/A | 153 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | #N/A | 154 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | #N/A | 155 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | #N/A | 156 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | #N/A | 157 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | #N/A | 158 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | #N/A | 159 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | #N/A | 160 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | #N/A | 161 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | #N/A | 162 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | #N/A | 163 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | #N/A | 164 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | #N/A | 165 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | #N/A | 166 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | #N/A | 167 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | #N/A | 168 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | #N/A | 169 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | #N/A | 170 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | #N/A | 171 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | #N/A | 172 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | #N/A | 173 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | #N/A | 174 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | #N/A | 175 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | #N/A | 176 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | #N/A | 177 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | #N/A | 178 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | #N/A | 179 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | #N/A | 180 |  | #N/A | #N/A
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | #N/A | 181 |  | #N/A | #N/A
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | #N/A | 182 |  | #N/A | #N/A
[11 empty] | P6-A | Digital security | Architecture | A | 18 | #N/A | 183 |  | #N/A | #N/A
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | #N/A | 184 |  | #N/A | #N/A
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | #N/A | 185 |  | #N/A | #N/A
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | #N/A | 186 |  | #N/A | #N/A
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | #N/A | 187 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | #N/A | 188 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | #N/A | 189 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | #N/A | 190 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | #N/A | 191 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | #N/A | 192 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | #N/A | 193 |  | #N/A | #N/A
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | #N/A | 194 |  | #N/A | #N/A
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | #N/A | 195 |  | #N/A | #N/A
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | #N/A | 196 |  | #N/A | #N/A
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | #N/A | 197 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | #N/A | 198 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | #N/A | 199 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | #N/A | 200 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | #N/A | 201 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | #N/A | 202 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | #N/A | 203 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | #N/A | 204 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | #N/A | 205 |  | #N/A | #N/A
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | #N/A | 206 |  | #N/A | #N/A
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | #N/A | 207 |  | #N/A | #N/A
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | #N/A | 208 |  | #N/A | #N/A
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | #N/A | 209 |  | #N/A | #N/A
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | #N/A | 210 |  | #N/A | #N/A
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | #N/A | 211 |  | #N/A | #N/A
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | #N/A | 212 |  | #N/A | #N/A
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | #N/A | 213 |  | #N/A | #N/A
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | #N/A | 214 |  | #N/A | #N/A
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | #N/A | 215 |  | #N/A | #N/A
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | #N/A | 216 |  | #N/A | #N/A
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | #N/A | 217 |  | #N/A | #N/A
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | #N/A | 218 |  | #N/A | #N/A
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | #N/A | 219 |  | #N/A | #N/A
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | #N/A | 220 |  | #N/A | #N/A
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | #N/A | 221 |  | #N/A | #N/A
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | #N/A | 222 |  | #N/A | #N/A
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | #N/A | 223 |  | #N/A | #N/A
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | #N/A | 224 |  | #N/A | #N/A
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | #N/A | 225 |  | #N/A | #N/A
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | #N/A | 226 |  | #N/A | #N/A
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | #N/A | 227 |  | #N/A | #N/A
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | #N/A | 228 |  | #N/A | #N/A
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | #N/A | 229 |  | #N/A | #N/A
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | #N/A | 230 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | #N/A | 231 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | #N/A | 232 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | #N/A | 233 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | #N/A | 234 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | #N/A | 235 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | #N/A | 236 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | #N/A | 237 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | #N/A | 238 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | #N/A | 239 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | #N/A | 240 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | #N/A | 241 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | #N/A | 242 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | #N/A | 243 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | #N/A | 244 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | #N/A | 245 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | #N/A | 246 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | #N/A | 247 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | #N/A | 248 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | #N/A | 249 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | #N/A | 250 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | #N/A | 251 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | #N/A | 252 |  | #N/A | #N/A
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | #N/A | 253 |  | #N/A | #N/A
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | #N/A | 254 |  | #N/A | #N/A
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | #N/A | 255 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | #N/A | 256 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | #N/A | 257 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | #N/A | 258 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | #N/A | 259 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | #N/A | 260 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | #N/A | 261 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | #N/A | 262 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | #N/A | 263 |  | #N/A | #N/A
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | #N/A | 264 |  | #N/A | #N/A
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | #N/A | 265 |  | #N/A | #N/A
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | #N/A | 266 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | #N/A | 267 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Boom system | A | 48 | #N/A | 268 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | #N/A | 269 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Structure | A | 48 | #N/A | 270 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | #N/A | 271 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | #N/A | 272 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | #N/A | 273 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | #N/A | 274 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | #N/A | 275 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | #N/A | 276 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | #N/A | 277 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | #N/A | 278 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | #N/A | 279 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | #N/A | 280 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | #N/A | 281 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | #N/A | 282 |  | #N/A | #N/A
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | #N/A | 283 |  | #N/A | #N/A
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | #N/A | 284 |  | #N/A | #N/A
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | #N/A | 285 |  | #N/A | #N/A
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | #N/A | 286 |  | #N/A | #N/A
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | #N/A | 287 |  | #N/A | #N/A
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | #N/A | 288 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | #N/A | 289 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | #N/A | 290 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | #N/A | 291 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | #N/A | 292 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | #N/A | 293 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | #N/A | 294 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | #N/A | 295 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | #N/A | 296 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | #N/A | 297 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | #N/A | 298 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | #N/A | 299 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | #N/A | 300 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | #N/A | 301 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | #N/A | 302 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | #N/A | 303 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | #N/A | 304 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | #N/A | 305 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | #N/A | 306 |  | #N/A | #N/A

## FA_SQFDF
Failure Code | FA_SQFDF |  |  |  | Number of Locations in failure code when defaults assigned: | 420 |  | Final Criticality Code |  | A | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | FLAME DETECTOR
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | Count | 54 | 2
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | Selected ID | 50 | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10 |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System |  |  |  | 54 | 2
Safety | D | 10 | #N/A |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework
Environmental | H | 2 | 2 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C = |  | A | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table
Production | H | 2 | 2 |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing
Business | H | 2 | 2 |  |  | 2 |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity
[6 empty] | 2 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE
Loss of Function | D | 10 | #N/A | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps)
|  |  | #N/A |  |  |  | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel |  | A | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection | Gonna be an A… |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 0 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 0 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 0 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 0 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 0 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 0 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 0 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 0 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 0 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 0 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 0 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 0 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 0 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 0 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 0 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 0 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 0 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 0 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 0 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 0 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 0 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 0 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 0 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 0 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 0 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 0 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 0 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 0 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 0 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 0 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 0 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 0 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 0 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 0 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 0 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 0 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 0 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 0 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 0 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 0 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 0 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 0 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 0 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 0 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 0 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 0 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 0 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 0 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 0 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 0 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 0 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 0 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 0 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 0 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 0 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 0 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 0 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 0 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 0 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 0 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 0 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 0 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 0 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 0 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 0 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 0 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 0 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 0 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 0 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 0 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 0 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 0 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 0 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 0 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 0 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 0 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 0 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 0 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 0 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 0 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 0 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 0 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 0 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 0 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 0 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 0 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 0 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 0 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 0 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 0 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 0 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 0 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 0 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 0 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 0 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 0 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 0 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 0 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 0 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 0 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 0 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 0 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 0 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 0 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 0 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 0 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 0 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 0 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 0 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 0 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 0 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 0 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 0 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 0 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 0 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 0 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 0 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 0 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 0 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 0 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 0 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 0 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 0 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 0 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 0 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 0 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 0 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 0 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 0 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 0 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 0 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 0 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 0 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 0 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 0 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 0 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 0 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 0 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 0 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 0 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 0 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 0 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 0 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 0 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 0 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 0 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 0 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 0 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 0 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 0 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 0 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 0 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 0 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 0 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 0 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 0 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 0 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 0 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 0 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 0 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 0 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 0 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 0 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 0 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 0 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 0 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 0 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 0 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 0 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 0 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 0 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 0 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 0 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 0 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 0 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 0 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 0 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 0 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 0 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 0 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 0 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 0 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 0 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 0 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 0 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 0 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 1 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 2 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 2 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 2 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 2 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 2 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 2 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 2 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 2 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 2 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 2 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 2 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 2 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 2 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 2 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 2 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 2 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 2 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 2 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 2 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 2 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 2 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 2 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 2 | 306

## FA_SQFDG
Failure Code | FA_SQFDG |  |  |  | Number of Locations in failure code when defaults assigned: | 739 |  | Final Criticality Code |  | A | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | FIXED GAS DETECTOR
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | Count | 54 | 2
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | Selected ID | 50 | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10 |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System |  |  |  | 54 | 2
Safety | D | 10 | #N/A |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework
Environmental | H | 2 | 2 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C = |  | A | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table
Production | H | 2 | 2 |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing
Business | H | 2 | 2 |  |  | 2 |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity
[6 empty] | 2 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE
Loss of Function | D | 10 | #N/A | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps)
|  |  | #N/A |  |  |  | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel |  | A | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection | Gonna be an A… |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 0 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 0 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 0 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 0 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 0 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 0 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 0 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 0 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 0 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 0 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 0 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 0 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 0 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 0 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 0 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 0 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 0 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 0 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 0 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 0 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 0 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 0 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 0 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 0 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 0 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 0 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 0 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 0 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 0 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 0 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 0 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 0 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 0 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 0 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 0 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 0 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 0 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 0 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 0 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 0 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 0 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 0 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 0 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 0 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 0 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 0 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 0 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 0 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 0 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 0 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 0 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 0 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 0 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 0 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 0 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 0 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 0 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 0 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 0 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 0 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 0 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 0 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 0 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 0 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 0 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 0 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 0 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 0 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 0 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 0 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 0 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 0 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 0 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 0 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 0 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 0 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 0 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 0 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 0 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 0 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 0 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 0 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 0 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 0 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 0 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 0 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 0 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 0 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 0 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 0 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 0 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 0 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 0 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 0 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 0 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 0 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 0 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 0 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 0 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 0 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 0 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 0 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 0 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 0 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 0 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 0 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 0 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 0 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 0 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 0 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 0 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 0 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 0 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 0 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 0 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 0 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 0 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 0 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 0 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 0 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 0 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 0 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 0 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 0 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 0 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 0 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 0 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 0 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 0 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 0 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 0 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 0 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 0 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 0 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 0 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 0 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 0 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 0 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 0 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 0 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 0 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 0 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 0 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 0 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 0 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 0 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 0 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 0 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 0 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 0 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 0 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 0 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 0 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 0 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 0 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 0 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 0 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 0 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 0 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 0 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 0 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 0 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 0 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 0 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 0 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 0 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 0 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 0 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 0 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 0 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 0 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 0 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 0 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 0 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 0 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 0 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 0 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 0 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 0 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 0 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 0 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 0 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 0 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 0 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 0 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 0 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 1 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 2 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 2 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 2 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 2 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 2 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 2 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 2 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 2 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 2 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 2 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 2 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 2 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 2 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 2 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 2 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 2 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 2 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 2 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 2 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 2 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 2 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 2 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 2 | 306

## FA_SQFDS
Failure Code | FA_SQFDS |  |  |  | Number of Locations in failure code when defaults assigned: | 140 |  | Final Criticality Code |  | A | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | SMOKE DETECTOR
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | Count | 54 | 2
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | Selected ID | 50 | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10 |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System |  |  |  | 54 | 2
Safety | D | 10 | #N/A |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework
Environmental | H | 2 | 2 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C = |  | A | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table
Production | H | 2 | 2 |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing
Business | H | 2 | 2 |  |  | 2 |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity
[6 empty] | 2 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE
Loss of Function | D | 10 | #N/A | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps)
|  |  | #N/A |  |  |  | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel |  | A | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection | Gonna be an A… |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 0 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 0 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 0 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 0 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 0 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 0 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 0 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 0 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 0 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 0 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 0 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 0 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 0 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 0 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 0 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 0 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 0 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 0 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 0 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 0 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 0 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 0 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 0 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 0 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 0 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 0 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 0 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 0 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 0 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 0 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 0 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 0 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 0 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 0 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 0 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 0 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 0 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 0 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 0 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 0 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 0 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 0 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 0 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 0 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 0 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 0 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 0 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 0 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 0 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 0 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 0 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 0 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 0 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 0 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 0 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 0 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 0 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 0 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 0 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 0 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 0 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 0 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 0 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 0 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 0 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 0 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 0 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 0 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 0 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 0 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 0 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 0 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 0 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 0 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 0 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 0 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 0 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 0 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 0 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 0 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 0 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 0 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 0 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 0 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 0 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 0 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 0 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 0 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 0 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 0 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 0 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 0 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 0 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 0 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 0 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 0 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 0 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 0 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 0 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 0 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 0 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 0 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 0 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 0 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 0 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 0 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 0 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 0 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 0 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 0 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 0 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 0 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 0 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 0 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 0 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 0 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 0 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 0 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 0 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 0 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 0 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 0 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 0 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 0 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 0 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 0 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 0 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 0 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 0 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 0 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 0 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 0 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 0 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 0 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 0 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 0 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 0 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 0 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 0 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 0 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 0 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 0 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 0 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 0 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 0 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 0 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 0 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 0 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 0 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 0 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 0 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 0 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 0 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 0 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 0 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 0 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 0 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 0 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 0 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 0 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 0 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 0 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 0 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 0 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 0 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 0 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 0 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 0 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 0 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 0 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 0 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 0 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 0 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 0 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 0 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 0 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 0 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 0 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 0 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 0 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 0 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 0 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 0 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 0 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 0 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 0 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 1 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 2 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 2 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 2 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 2 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 2 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 2 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 2 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 2 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 2 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 2 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 2 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 2 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 2 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 2 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 2 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 2 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 2 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 2 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 2 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 2 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 2 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 2 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 2 | 306

## FA_SQFFD
Failure Code | FA_SQFFD |  |  |  | Number of Locations in failure code when defaults assigned: | 26 |  | Final Criticality Code |  | A | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | FIREWATER DELUGE SYSTEM
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | Firewater pumps (main and jockey), drivers, their controls and control panels | A | Count | 54 | 13
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | Selected ID | 53 | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly | Zone isolation valves | A
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10 |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System | Sprinkler / Deluge Nozzle (≥10 per zone) | B |  | 54 | 13
Safety | D | 10 | #N/A |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework | Sprinkler / Deluge Nozzle (<10 per zone) | A
Environmental | H | 2 | 2 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C = |  | A | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table | Pressure / level / flow instruments | A
Production | F | 6 | 8 |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing | Control Valves | A
Business | F | 6 | 8 |  |  | 6 |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity | Logic solvers | A
[6 empty] | 6 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity | Accommodation hydrants (main fire-fighting mechanism) | A
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity | Accommodation hydrants (if sprinkler system present) | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE | Fusible plug / fusible loop (≥3 per fire zone) | B
Loss of Function | D | 10 | #N/A | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Fusible plug / fusible loop (<3 per zone) | A
|  |  | #N/A |  |  |  | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) |  | A | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection | Code Applied to gas turbine deluge nozzles, othe deluge skids. Treat as primary fire fighting system |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | F | 6 | 8 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No |  | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | F | 6 | 8 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 0 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 0 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 0 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 0 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 0 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 0 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 0 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 0 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 0 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 0 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 0 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 0 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 0 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 0 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 0 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 0 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 0 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 0 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 0 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 0 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 0 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 0 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 0 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 0 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 0 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 0 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 0 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 0 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 0 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 0 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 0 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 0 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 0 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 0 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 0 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 0 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 0 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 0 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 0 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 0 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 0 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 0 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 0 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 0 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 0 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 0 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 0 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 0 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 0 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 0 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 0 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 0 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 0 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 0 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 0 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 0 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 0 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 0 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 0 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 0 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 0 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 0 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 0 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 0 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 0 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 0 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 0 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 0 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 0 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 0 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 0 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 0 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 0 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 0 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 0 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 0 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 0 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 0 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 0 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 0 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 0 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 0 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 0 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 0 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 0 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 0 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 0 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 0 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 0 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 0 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 0 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 0 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 0 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 0 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 0 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 0 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 0 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 0 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 0 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 0 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 0 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 0 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 0 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 0 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 0 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 0 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 0 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 0 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 0 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 0 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 0 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 0 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 0 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 0 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 0 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 0 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 0 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 0 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 0 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 0 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 0 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 0 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 0 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 0 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 0 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 0 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 0 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 0 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 0 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 0 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 0 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 0 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 0 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 0 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 0 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 0 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 0 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 0 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 0 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 0 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 0 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 0 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 0 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 0 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 0 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 0 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 0 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 0 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 0 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 0 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 0 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 0 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 0 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 0 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 0 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 0 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 0 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 0 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 0 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 0 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 0 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 0 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 0 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 0 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 0 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 0 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 0 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 0 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 0 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 0 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 0 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 0 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 0 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 0 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 0 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 0 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 0 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 0 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 0 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 0 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 0 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 0 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 0 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 0 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 0 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 0 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 0 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 0 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 0 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 0 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 0 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 0 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 1 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 2 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 3 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 4 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 5 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 6 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 7 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 8 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 9 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 10 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 11 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 12 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 13 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 13 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 13 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 13 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 13 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 13 | 306

## FA_SQFFH
Failure Code | FA_SQFFH |  |  |  | Number of Locations in failure code when defaults assigned: | 3 |  | Final Criticality Code |  | B | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | FIRE HOSE
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | Firewater pumps (main and jockey), drivers, their controls and control panels | A | Count | 54 | 13
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | Selected ID | 53 | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly | Zone isolation valves | A
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10 |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System | Sprinkler / Deluge Nozzle (≥10 per zone) | B |  | 54 | 13
Safety | D | 10 | #N/A |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework | Sprinkler / Deluge Nozzle (<10 per zone) | A
Environmental | H | 2 | 2 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C = |  | B | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table | Pressure / level / flow instruments | A
Production | H | 2 | 2 |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing | Control Valves | A
Business | F | 6 | 8 |  |  | 2 |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity | Logic solvers | A
[6 empty] | 6 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity | Accommodation hydrants (main fire-fighting mechanism) | A
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity | Accommodation hydrants (if sprinkler system present) | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE | Fusible plug / fusible loop (≥3 per fire zone) | B
Loss of Function | D | 10 | #N/A | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Fusible plug / fusible loop (<3 per zone) | A
|  |  | #N/A |  |  |  | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) |  | B | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection | Fire hydrant cabinets set with this code, could escalate for 'primary' fire fighting systems |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | F | 6 | 8 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 0 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 0 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 0 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 0 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 0 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 0 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 0 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 0 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 0 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 0 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 0 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 0 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 0 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 0 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 0 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 0 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 0 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 0 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 0 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 0 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 0 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 0 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 0 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 0 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 0 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 0 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 0 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 0 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 0 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 0 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 0 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 0 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 0 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 0 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 0 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 0 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 0 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 0 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 0 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 0 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 0 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 0 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 0 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 0 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 0 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 0 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 0 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 0 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 0 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 0 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 0 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 0 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 0 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 0 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 0 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 0 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 0 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 0 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 0 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 0 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 0 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 0 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 0 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 0 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 0 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 0 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 0 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 0 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 0 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 0 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 0 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 0 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 0 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 0 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 0 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 0 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 0 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 0 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 0 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 0 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 0 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 0 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 0 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 0 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 0 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 0 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 0 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 0 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 0 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 0 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 0 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 0 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 0 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 0 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 0 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 0 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 0 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 0 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 0 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 0 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 0 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 0 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 0 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 0 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 0 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 0 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 0 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 0 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 0 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 0 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 0 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 0 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 0 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 0 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 0 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 0 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 0 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 0 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 0 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 0 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 0 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 0 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 0 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 0 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 0 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 0 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 0 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 0 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 0 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 0 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 0 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 0 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 0 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 0 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 0 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 0 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 0 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 0 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 0 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 0 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 0 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 0 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 0 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 0 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 0 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 0 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 0 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 0 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 0 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 0 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 0 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 0 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 0 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 0 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 0 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 0 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 0 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 0 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 0 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 0 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 0 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 0 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 0 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 0 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 0 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 0 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 0 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 0 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 0 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 0 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 0 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 0 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 0 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 0 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 0 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 0 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 0 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 0 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 0 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 0 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 0 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 0 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 0 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 0 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 0 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 0 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 0 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 0 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 0 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 0 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 0 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 0 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 1 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 2 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 3 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 4 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 5 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 6 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 7 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 8 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 9 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 10 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 11 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 12 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 13 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 13 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 13 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 13 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 13 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 13 | 306

## FA_SQFFM
Failure Code | FA_SQFFM |  |  |  | Number of Locations in failure code when defaults assigned: | 23 |  | Final Criticality Code |  | B | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | FIRE WATER/FOAM MONITOR
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | Firewater pumps (main and jockey), drivers, their controls and control panels | A | Count | 54 | 13
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | Selected ID | 53 | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly | Zone isolation valves | A
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10 |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System | Sprinkler / Deluge Nozzle (≥10 per zone) | B |  | 54 | 13
Safety | D | 10 | #N/A |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework | Sprinkler / Deluge Nozzle (<10 per zone) | A
Environmental | H | 2 | 2 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C = |  | B | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table | Pressure / level / flow instruments | A
Production | H | 2 | 2 |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing | Control Valves | A
Business | H | 2 | 2 |  |  | 2 |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity | Logic solvers | A
[6 empty] | 2 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity | Accommodation hydrants (main fire-fighting mechanism) | A
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity | Accommodation hydrants (if sprinkler system present) | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE | Fusible plug / fusible loop (≥3 per fire zone) | B
Loss of Function | D | 10 | #N/A | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Fusible plug / fusible loop (<3 per zone) | A
|  |  | #N/A |  |  |  | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) |  | B | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection | Fire hydrant cabinets set with this code, could escalate for 'primary' fire fighting systems |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 0 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 0 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 0 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 0 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 0 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 0 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 0 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 0 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 0 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 0 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 0 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 0 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 0 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 0 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 0 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 0 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 0 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 0 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 0 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 0 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 0 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 0 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 0 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 0 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 0 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 0 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 0 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 0 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 0 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 0 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 0 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 0 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 0 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 0 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 0 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 0 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 0 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 0 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 0 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 0 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 0 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 0 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 0 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 0 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 0 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 0 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 0 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 0 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 0 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 0 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 0 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 0 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 0 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 0 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 0 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 0 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 0 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 0 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 0 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 0 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 0 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 0 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 0 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 0 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 0 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 0 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 0 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 0 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 0 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 0 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 0 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 0 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 0 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 0 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 0 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 0 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 0 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 0 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 0 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 0 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 0 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 0 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 0 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 0 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 0 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 0 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 0 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 0 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 0 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 0 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 0 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 0 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 0 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 0 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 0 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 0 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 0 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 0 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 0 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 0 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 0 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 0 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 0 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 0 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 0 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 0 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 0 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 0 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 0 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 0 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 0 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 0 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 0 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 0 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 0 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 0 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 0 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 0 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 0 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 0 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 0 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 0 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 0 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 0 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 0 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 0 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 0 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 0 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 0 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 0 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 0 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 0 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 0 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 0 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 0 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 0 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 0 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 0 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 0 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 0 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 0 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 0 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 0 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 0 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 0 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 0 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 0 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 0 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 0 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 0 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 0 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 0 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 0 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 0 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 0 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 0 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 0 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 0 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 0 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 0 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 0 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 0 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 0 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 0 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 0 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 0 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 0 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 0 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 0 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 0 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 0 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 0 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 0 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 0 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 0 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 0 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 0 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 0 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 0 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 0 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 0 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 0 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 0 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 0 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 0 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 0 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 0 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 0 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 0 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 0 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 0 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 0 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 1 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 2 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 3 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 4 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 5 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 6 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 7 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 8 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 9 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 10 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 11 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 12 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 13 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 13 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 13 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 13 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 13 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 13 | 306

## FA_SQFFY
Failure Code | FA_SQFFY |  |  |  | Number of Locations in failure code when defaults assigned: | 118 |  | Final Criticality Code |  | B | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | FIRE HYDRANT
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | Firewater pumps (main and jockey), drivers, their controls and control panels | A | Count | 54 | 13
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | Selected ID | 53 | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly | Zone isolation valves | A
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10 |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System | Sprinkler / Deluge Nozzle (≥10 per zone) | B |  | 54 | 13
Safety | D | 10 | #N/A |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework | Sprinkler / Deluge Nozzle (<10 per zone) | A
Environmental | H | 1 | 1 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C = |  | B | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table | Pressure / level / flow instruments | A
Production | H | 1 | 1 |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing | Control Valves | A
Business | F | 5 | 7 |  |  | 2 |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity | Logic solvers | A
[6 empty] | 6 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity | Accommodation hydrants (main fire-fighting mechanism) | A
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity | Accommodation hydrants (if sprinkler system present) | B
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE | Fusible plug / fusible loop (≥3 per fire zone) | B
Loss of Function | D | 10 | #N/A | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Fusible plug / fusible loop (<3 per zone) | A
|  |  | #N/A |  |  |  | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) |  | B | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection | Treat as supplementary until told otherwise |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security
Loss of Function | H | 1 | 1 | 72 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | H | 1 | 1 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | F | 5 | 7 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 0 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 0 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 0 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 0 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 0 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 0 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 0 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 0 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 0 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 0 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 0 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 0 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 0 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 0 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 0 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 0 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 0 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 0 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 0 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 0 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 0 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 0 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 0 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 0 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 0 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 0 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 0 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 0 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 0 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 0 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 0 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 0 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 0 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 0 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 0 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 0 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 0 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 0 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 0 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 0 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 0 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 0 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 0 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 0 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 0 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 0 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 0 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 0 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 0 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 0 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 0 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 0 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 0 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 0 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 0 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 0 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 0 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 0 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 0 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 0 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 0 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 0 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 0 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 0 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 0 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 0 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 0 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 0 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 0 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 0 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 0 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 0 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 0 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 0 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 0 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 0 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 0 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 0 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 0 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 0 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 0 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 0 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 0 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 0 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 0 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 0 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 0 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 0 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 0 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 0 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 0 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 0 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 0 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 0 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 0 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 0 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 0 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 0 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 0 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 0 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 0 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 0 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 0 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 0 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 0 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 0 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 0 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 0 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 0 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 0 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 0 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 0 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 0 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 0 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 0 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 0 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 0 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 0 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 0 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 0 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 0 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 0 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 0 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 0 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 0 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 0 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 0 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 0 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 0 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 0 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 0 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 0 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 0 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 0 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 0 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 0 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 0 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 0 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 0 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 0 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 0 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 0 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 0 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 0 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 0 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 0 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 0 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 0 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 0 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 0 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 0 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 0 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 0 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 0 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 0 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 0 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 0 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 0 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 0 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 0 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 0 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 0 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 0 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 0 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 0 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 0 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 0 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 0 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 0 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 0 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 0 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 0 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 0 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 0 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 0 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 0 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 0 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 0 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 0 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 0 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 0 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 0 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 0 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 0 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 0 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 0 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 0 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 0 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 0 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 0 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 0 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 0 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 1 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 2 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 3 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 4 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 5 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 6 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 7 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 8 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 9 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 10 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 11 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 12 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 13 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 13 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 13 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 13 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 13 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 13 | 306

## FA_SQFRA
Failure Code | FA_SQFRA |  |  |  | Number of Locations in failure code when defaults assigned: | 244 |  | Final Criticality Code |  | A | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | EMERGENCY ALARM DEVICE
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | Count | 54 | 2
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | Selected ID | 50 | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10 |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System |  |  |  | 54 | 2
Safety | D | 10 | #N/A |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework
Environmental | H | 2 | 2 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C = |  | A | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table
Production | H | 2 | 2 |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing
Business | H | 2 | 2 |  |  | 2 |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity
[6 empty] | 2 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE
Loss of Function | D | 10 | #N/A | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps)
|  |  | #N/A |  |  |  | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel |  | A | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection | Mostly Manual alarm call points |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 0 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 0 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 0 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 0 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 0 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 0 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 0 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 0 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 0 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 0 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 0 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 0 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 0 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 0 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 0 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 0 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 0 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 0 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 0 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 0 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 0 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 0 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 0 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 0 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 0 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 0 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 0 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 0 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 0 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 0 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 0 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 0 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 0 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 0 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 0 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 0 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 0 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 0 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 0 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 0 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 0 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 0 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 0 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 0 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 0 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 0 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 0 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 0 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 0 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 0 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 0 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 0 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 0 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 0 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 0 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 0 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 0 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 0 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 0 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 0 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 0 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 0 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 0 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 0 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 0 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 0 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 0 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 0 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 0 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 0 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 0 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 0 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 0 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 0 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 0 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 0 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 0 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 0 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 0 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 0 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 0 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 0 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 0 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 0 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 0 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 0 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 0 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 0 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 0 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 0 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 0 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 0 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 0 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 0 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 0 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 0 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 0 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 0 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 0 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 0 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 0 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 0 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 0 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 0 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 0 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 0 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 0 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 0 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 0 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 0 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 0 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 0 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 0 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 0 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 0 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 0 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 0 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 0 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 0 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 0 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 0 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 0 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 0 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 0 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 0 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 0 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 0 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 0 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 0 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 0 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 0 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 0 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 0 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 0 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 0 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 0 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 0 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 0 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 0 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 0 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 0 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 0 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 0 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 0 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 0 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 0 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 0 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 0 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 0 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 0 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 0 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 0 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 0 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 0 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 0 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 0 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 0 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 0 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 0 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 0 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 0 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 0 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 0 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 0 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 0 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 0 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 0 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 0 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 0 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 0 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 0 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 0 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 0 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 0 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 0 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 0 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 0 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 0 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 0 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 0 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 0 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 0 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 0 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 0 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 0 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 0 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 1 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 2 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 2 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 2 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 2 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 2 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 2 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 2 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 2 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 2 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 2 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 2 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 2 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 2 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 2 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 2 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 2 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 2 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 2 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 2 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 2 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 2 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 2 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 2 | 306

## FA_SQFRE
Failure Code | FA_SQFRE |  |  |  | Number of Locations in failure code when defaults assigned: | 20 |  | Final Criticality Code |  | C | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | SAFETY SHOWER OR EYE BATH
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | Count | 54 | 13
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | Selected ID | 11 | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly | All pressure retaining Equipment and pipework for highly toxic substances | A
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8 |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System | All pressure retaining Equipment and pipework with corrosion resistant linings | A |  | 54 | 13
Safety | E | 8 | 11 |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework | All pressure retaining Equipment and pipework associated with fire water delivery systems | A
Environmental | H | 2 | 2 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C = |  | C | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table | Bilge and ballast pipework | A
Production | H | 2 | 2 |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing | All other pressure Equipment and pipework | C
Business | H | 2 | 2 |  |  | 2 |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity | Supports for criticality A pressure systems | A
[6 empty] | 2 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity | Insulation installed on criticality A pressure systems | A
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity | Painting on criticality A pressure systems | A
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE | Bolting on criticality A pressure systems | A
Loss of Function | E | 8 | 11 | 69 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | All other supports, paint and bolting | C
|  |  | #N/A |  |  |  | Process Containment Integrity | All other pressure Equipment and pipework |  | C | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection | Not MAH lifesaving equipment |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 1 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 2 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 3 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 4 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 5 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 6 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 7 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 8 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 9 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 10 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 11 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 12 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 13 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 13 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 13 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 13 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 13 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 13 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 13 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 13 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 13 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 13 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 13 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 13 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 13 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 13 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 13 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 13 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 13 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 13 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 13 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 13 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 13 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 13 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 13 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 13 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 13 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 13 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 13 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 13 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 13 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 13 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 13 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 13 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 13 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 13 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 13 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 13 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 13 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 13 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 13 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 13 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 13 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 13 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 13 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 13 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 13 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 13 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 13 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 13 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 13 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 13 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 13 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 13 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 13 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 13 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 13 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 13 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 13 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 13 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 13 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 13 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 13 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 13 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 13 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 13 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 13 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 13 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 13 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 13 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 13 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 13 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 13 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 13 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 13 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 13 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 13 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 13 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 13 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 13 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 13 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 13 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 13 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 13 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 13 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 13 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 13 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 13 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 13 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 13 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 13 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 13 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 13 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 13 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 13 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 13 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 13 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 13 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 13 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 13 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 13 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 13 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 13 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 13 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 13 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 13 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 13 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 13 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 13 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 13 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 13 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 13 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 13 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 13 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 13 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 13 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 13 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 13 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 13 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 13 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 13 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 13 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 13 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 13 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 13 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 13 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 13 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 13 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 13 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 13 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 13 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 13 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 13 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 13 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 13 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 13 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 13 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 13 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 13 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 13 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 13 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 13 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 13 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 13 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 13 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 13 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 13 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 13 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 13 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 13 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 13 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 13 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 13 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 13 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 13 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 13 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 13 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 13 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 13 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 13 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 13 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 13 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 13 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 13 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 13 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 13 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 13 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 13 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 13 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 13 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 13 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 13 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 13 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 13 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 13 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 13 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 13 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 13 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 13 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 13 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 13 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 13 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 13 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 13 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 13 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 13 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 13 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 13 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 13 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 13 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 13 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 13 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 13 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 13 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 13 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 13 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 13 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 13 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 13 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 13 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 13 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 13 | 306

## FA_SQMT
Failure Code | FA_SQMT |  |  |  | Number of Locations in failure code when defaults assigned: | 2 |  | Final Criticality Code |  | B | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | MAINTENANCE TOOL
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | Gas Generator | A | Count | 54 | 12
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity | Alternators | B | Selected ID | 12 | 3
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping | Power Turbine | B
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly | All Casing joints, fittings and seals | B
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 2 |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System | All Shaft Seals | A |  | 54 | 12
Safety | H | 2 | 2 |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework | All coupling members | B
Environmental | H | 2 | 2 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C = |  | B | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table | Pressurized Enclosures | A
Production | H | 2 | 2 |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing | Fire & Gas System | A
Business | H | 2 | 2 |  |  | 2 |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity | All Shaft Seals System Ancillaries | A
[6 empty] | 2 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps)
|  |  | #N/A |  |  |  | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) |  | B | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection | Barring devices for flash gas compressors |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 0 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 0 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 0 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 0 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 0 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 0 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 0 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 0 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 0 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 0 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 0 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 0 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 0 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 1 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 2 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 3 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 4 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 5 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 6 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 7 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 8 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 9 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 10 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 11 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 12 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 12 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 12 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 12 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 12 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 12 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 12 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 12 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 12 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 12 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 12 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 12 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 12 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 12 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 12 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 12 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 12 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 12 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 12 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 12 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 12 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 12 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 12 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 12 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 12 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 12 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 12 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 12 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 12 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 12 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 12 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 12 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 12 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 12 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 12 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 12 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 12 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 12 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 12 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 12 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 12 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 12 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 12 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 12 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 12 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 12 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 12 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 12 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 12 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 12 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 12 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 12 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 12 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 12 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 12 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 12 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 12 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 12 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 12 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 12 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 12 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 12 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 12 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 12 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 12 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 12 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 12 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 12 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 12 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 12 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 12 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 12 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 12 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 12 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 12 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 12 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 12 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 12 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 12 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 12 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 12 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 12 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 12 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 12 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 12 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 12 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 12 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 12 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 12 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 12 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 12 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 12 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 12 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 12 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 12 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 12 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 12 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 12 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 12 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 12 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 12 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 12 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 12 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 12 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 12 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 12 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 12 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 12 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 12 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 12 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 12 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 12 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 12 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 12 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 12 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 12 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 12 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 12 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 12 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 12 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 12 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 12 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 12 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 12 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 12 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 12 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 12 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 12 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 12 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 12 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 12 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 12 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 12 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 12 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 12 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 12 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 12 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 12 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 12 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 12 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 12 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 12 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 12 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 12 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 12 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 12 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 12 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 12 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 12 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 12 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 12 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 12 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 12 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 12 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 12 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 12 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 12 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 12 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 12 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 12 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 12 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 12 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 12 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 12 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 12 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 12 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 12 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 12 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 12 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 12 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 12 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 12 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 12 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 12 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 12 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 12 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 12 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 12 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 12 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 12 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 12 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 12 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 12 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 12 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 12 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 12 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 12 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 12 | 306

## FA_SQTA
Failure Code | FA_SQTA |  |  |  | Number of Locations in failure code when defaults assigned: | 78 |  | Final Criticality Code |  | A | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | PUBLIC ADDRESS AND ALARM SYSTEM
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | Count | 54 | 1
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity |  |  | Selected ID | 32 | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10 |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System |  |  |  | 54 | 1
Safety | D | 9 | #N/A |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework
Environmental | H | 1 | 1 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C = |  | A | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table
Production | H | 1 | 1 |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing
Business | G | 3 | 4 |  |  | 2 |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity
[6 empty] | 4 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE
Loss of Function | D | 9 | #N/A | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps)
|  |  | #N/A |  |  |  | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights |  | A | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection | Includes some un-validated MAC points. |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security
Loss of Function | H | 1 | 1 | 72 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | H | 1 | 1 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | G | 3 | 4 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 0 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 0 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 0 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 0 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 0 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 0 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 0 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 0 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 0 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 0 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 0 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 0 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 0 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 0 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 0 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 0 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 0 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 0 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 0 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 0 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 0 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 0 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 0 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 0 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 0 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 0 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 0 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 0 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 0 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 0 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 0 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 0 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 0 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 0 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 0 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 0 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 0 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 0 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 0 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 0 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 0 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 0 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 0 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 0 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 0 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 0 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 0 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 0 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 0 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 0 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 0 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 0 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 0 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 0 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 0 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 0 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 0 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 0 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 0 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 0 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 0 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 0 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 0 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 0 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 0 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 0 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 0 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 0 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 0 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 0 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 0 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 0 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 0 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 0 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 0 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 0 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 0 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 0 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 0 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 0 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 0 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 0 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 0 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 0 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 0 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 0 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 0 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 0 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 0 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 0 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 0 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 0 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 0 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 0 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 0 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 0 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 0 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 0 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 0 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 0 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 0 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 0 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 0 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 0 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 0 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 0 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 0 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 0 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 0 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 0 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 0 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 0 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 0 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 0 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 0 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 1 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 1 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 1 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 1 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 1 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 1 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 1 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 1 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 1 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 1 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 1 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 1 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 1 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 1 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 1 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 1 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 1 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 1 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 1 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 1 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 1 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 1 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 1 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 1 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 1 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 1 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 1 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 1 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 1 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 1 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 1 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 1 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 1 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 1 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 1 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 1 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 1 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 1 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 1 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 1 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 1 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 1 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 1 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 1 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 1 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 1 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 1 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 1 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 1 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 1 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 1 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 1 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 1 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 1 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 1 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 1 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 1 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 1 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 1 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 1 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 1 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 1 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 1 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 1 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 1 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 1 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 1 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 1 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 1 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 1 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 1 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 1 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 1 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 1 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 1 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 1 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 1 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 1 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 1 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 1 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 1 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 1 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 1 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 1 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 1 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 1 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 1 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 1 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 1 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 1 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 1 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 1 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 1 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 1 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 1 | 306

## FA_SQTB
Failure Code | FA_SQTB |  |  |  | Number of Locations in failure code when defaults assigned: | 169 |  | Final Criticality Code |  | A | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | NON DIRECTIONAL BEACON
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | Count | 54 | 1
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity |  |  | Selected ID | 32 | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10 |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System |  |  |  | 54 | 1
Safety | D | 9 | #N/A |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework
Environmental | H | 1 | 1 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C = |  | A | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table
Production | H | 1 | 1 |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing
Business | G | 3 | 4 |  |  | 2 |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity
[6 empty] | 4 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE
Loss of Function | D | 9 | #N/A | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps)
|  |  | #N/A |  |  |  | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights |  | A | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection | Alarm / status signals |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security
Loss of Function | H | 1 | 1 | 72 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | H | 1 | 1 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | G | 3 | 4 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 0 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 0 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 0 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 0 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 0 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 0 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 0 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 0 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 0 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 0 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 0 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 0 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 0 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 0 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 0 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 0 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 0 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 0 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 0 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 0 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 0 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 0 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 0 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 0 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 0 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 0 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 0 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 0 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 0 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 0 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 0 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 0 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 0 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 0 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 0 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 0 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 0 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 0 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 0 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 0 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 0 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 0 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 0 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 0 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 0 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 0 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 0 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 0 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 0 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 0 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 0 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 0 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 0 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 0 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 0 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 0 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 0 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 0 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 0 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 0 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 0 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 0 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 0 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 0 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 0 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 0 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 0 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 0 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 0 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 0 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 0 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 0 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 0 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 0 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 0 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 0 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 0 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 0 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 0 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 0 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 0 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 0 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 0 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 0 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 0 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 0 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 0 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 0 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 0 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 0 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 0 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 0 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 0 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 0 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 0 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 0 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 0 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 0 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 0 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 0 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 0 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 0 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 0 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 0 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 0 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 0 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 0 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 0 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 0 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 0 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 0 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 0 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 0 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 0 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 0 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 1 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 1 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 1 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 1 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 1 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 1 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 1 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 1 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 1 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 1 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 1 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 1 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 1 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 1 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 1 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 1 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 1 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 1 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 1 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 1 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 1 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 1 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 1 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 1 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 1 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 1 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 1 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 1 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 1 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 1 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 1 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 1 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 1 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 1 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 1 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 1 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 1 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 1 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 1 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 1 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 1 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 1 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 1 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 1 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 1 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 1 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 1 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 1 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 1 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 1 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 1 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 1 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 1 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 1 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 1 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 1 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 1 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 1 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 1 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 1 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 1 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 1 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 1 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 1 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 1 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 1 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 1 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 1 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 1 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 1 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 1 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 1 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 1 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 1 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 1 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 1 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 1 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 1 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 1 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 1 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 1 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 1 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 1 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 1 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 1 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 1 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 1 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 1 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 1 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 1 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 1 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 1 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 1 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 1 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 1 | 306

## FA_SQTE
Failure Code | FA_SQTE |  |  |  | Number of Locations in failure code when defaults assigned: | 33 |  | Final Criticality Code |  | A | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | TELECOMMUNICATION CABINET
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | Class A Telecommunication UPS & Shut down | A | Count | 54 | 1
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity |  |  | Selected ID | 34 | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8 |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System |  |  |  | 54 | 1
Safety | E | 7 | 10 |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework
Environmental | H | 1 | 1 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C = |  | A | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table
Production | G | 3 | 4 |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing
Business | G | 3 | 4 |  |  | 4 |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity
[6 empty] | 4 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE
Loss of Function | E | 7 | 10 | 69 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps)
|  |  | #N/A |  |  |  | Telecommunications | Class A Telecommunication UPS & Shut down |  | A | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection | Treating all cabinets as class A |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security
Loss of Function | H | 1 | 1 | 72 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | G | 3 | 4 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | G | 3 | 4 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 0 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 0 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 0 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 0 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 0 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 0 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 0 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 0 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 0 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 0 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 0 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 0 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 0 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 0 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 0 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 0 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 0 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 0 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 0 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 0 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 0 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 0 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 0 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 0 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 0 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 0 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 0 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 0 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 0 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 0 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 0 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 0 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 0 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 0 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 0 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 0 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 0 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 0 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 0 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 0 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 0 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 0 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 0 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 0 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 0 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 0 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 0 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 0 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 0 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 0 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 0 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 0 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 0 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 0 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 0 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 0 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 0 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 0 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 0 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 0 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 0 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 0 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 0 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 0 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 0 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 0 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 0 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 0 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 0 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 0 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 0 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 0 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 0 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 0 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 0 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 0 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 0 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 0 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 0 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 0 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 0 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 0 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 0 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 0 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 0 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 0 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 0 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 0 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 0 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 0 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 0 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 0 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 0 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 0 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 0 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 0 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 0 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 0 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 0 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 0 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 0 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 0 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 0 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 0 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 0 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 0 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 0 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 0 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 0 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 0 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 0 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 0 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 0 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 0 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 0 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 0 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 0 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 1 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 1 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 1 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 1 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 0 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 0 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 0 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 0 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 0 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 0 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 0 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 0 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 0 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 0 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 0 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 0 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 0 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 0 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 0 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 0 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 0 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 0 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 0 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 0 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 0 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 0 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 0 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 0 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 0 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 0 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 0 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 0 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 0 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 0 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 0 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 0 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 0 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 0 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 0 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 0 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 0 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 0 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 0 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 0 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 0 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 0 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 0 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 0 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 0 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 0 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 0 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 0 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 0 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 0 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 0 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 0 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 0 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 0 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 0 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 0 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 0 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 0 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 0 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 0 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 0 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 0 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 0 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 0 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 0 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 0 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 0 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 0 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 0 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 0 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 0 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 0 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 0 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 0 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 0 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 0 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 0 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 0 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 0 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 0 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 0 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 0 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 0 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 0 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 0 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 0 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 0 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 0 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 0 | 306

## FA_SQTH
Failure Code | FA_SQTH |  |  |  | Number of Locations in failure code when defaults assigned: | 95 |  | Final Criticality Code |  | A | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | PATCH PANEL
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | Fire walls | A | Count | 54 | 4
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity | Remote access servers | A | Selected ID | 18 | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping | Architecture | A
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly | Staging servers for Anti-virus and OS patches | A
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8 |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System |  |  |  | 54 | 4
Safety | E | 7 | 10 |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework
Environmental | H | 1 | 1 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C = |  | A | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table
Production | G | 3 | 4 |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing
Business | G | 3 | 4 |  |  | 4 |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity
[6 empty] | 4 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE
Loss of Function | E | 7 | 10 | 69 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps)
|  |  | #N/A |  |  |  | Digital security | Fire walls |  | A | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection | Unvalidated fibre optic panels. Picked digital security, but could be Telecoms. No difference in GES between High and Medium criticality |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security
Loss of Function | H | 1 | 1 | 72 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | G | 3 | 4 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | G | 3 | 4 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 0 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 0 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 0 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 0 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 0 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 0 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 0 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 0 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 0 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 0 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 0 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 0 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 0 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 0 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 0 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 0 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 0 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 0 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 0 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 0 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 0 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 0 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 0 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 0 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 0 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 0 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 0 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 0 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 0 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 0 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 0 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 0 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 0 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 0 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 0 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 0 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 0 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 0 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 0 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 0 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 0 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 0 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 0 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 0 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 0 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 0 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 0 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 0 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 0 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 0 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 0 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 0 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 0 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 0 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 0 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 0 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 0 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 0 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 0 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 0 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 0 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 0 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 0 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 0 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 0 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 0 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 0 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 0 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 0 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 0 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 0 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 0 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 0 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 0 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 0 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 0 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 0 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 0 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 0 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 0 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 0 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 0 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 0 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 0 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 1 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 2 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 3 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 4 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 4 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 4 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 4 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 4 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 4 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 4 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 4 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 4 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 4 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 4 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 4 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 4 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 4 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 4 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 4 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 4 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 4 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 4 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 4 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 4 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 4 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 4 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 4 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 4 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 4 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 4 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 4 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 4 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 4 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 4 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 4 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 4 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 4 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 4 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 4 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 4 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 4 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 4 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 4 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 4 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 4 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 4 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 4 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 4 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 4 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 4 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 4 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 4 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 4 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 4 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 4 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 4 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 4 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 4 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 4 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 4 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 4 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 4 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 4 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 4 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 4 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 4 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 4 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 4 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 4 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 4 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 4 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 4 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 4 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 4 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 4 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 4 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 4 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 4 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 4 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 4 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 4 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 4 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 4 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 4 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 4 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 4 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 4 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 4 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 4 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 4 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 4 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 4 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 4 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 4 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 4 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 4 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 4 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 4 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 4 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 4 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 4 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 4 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 4 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 4 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 4 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 4 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 4 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 4 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 4 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 4 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 4 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 4 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 4 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 4 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 4 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 4 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 4 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 4 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 4 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 4 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 4 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 4 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 4 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 4 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 4 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 4 | 306

## FA_SQTL
Failure Code | FA_SQTL |  |  |  | Number of Locations in failure code when defaults assigned: | 487 |  | Final Criticality Code |  | A | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | LOUDSPEAKER
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | Count | 54 | 1
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity |  |  | Selected ID | 32 | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10 |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System |  |  |  | 54 | 1
Safety | D | 9 | #N/A |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework
Environmental | H | 1 | 1 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C = |  | A | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table
Production | H | 1 | 1 |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing
Business | G | 3 | 4 |  |  | 2 |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity
[6 empty] | 4 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE
Loss of Function | D | 9 | #N/A | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps)
|  |  | #N/A |  |  |  | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights |  | A | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection | PAGA loudspeakers, outdoor and in |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security
Loss of Function | H | 1 | 1 | 72 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | H | 1 | 1 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | G | 3 | 4 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 0 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 0 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 0 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 0 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 0 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 0 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 0 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 0 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 0 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 0 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 0 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 0 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 0 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 0 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 0 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 0 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 0 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 0 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 0 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 0 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 0 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 0 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 0 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 0 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 0 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 0 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 0 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 0 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 0 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 0 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 0 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 0 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 0 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 0 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 0 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 0 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 0 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 0 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 0 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 0 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 0 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 0 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 0 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 0 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 0 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 0 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 0 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 0 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 0 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 0 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 0 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 0 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 0 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 0 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 0 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 0 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 0 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 0 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 0 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 0 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 0 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 0 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 0 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 0 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 0 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 0 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 0 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 0 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 0 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 0 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 0 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 0 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 0 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 0 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 0 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 0 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 0 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 0 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 0 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 0 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 0 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 0 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 0 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 0 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 0 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 0 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 0 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 0 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 0 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 0 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 0 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 0 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 0 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 0 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 0 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 0 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 0 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 0 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 0 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 0 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 0 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 0 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 0 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 0 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 0 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 0 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 0 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 0 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 0 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 0 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 0 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 0 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 0 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 0 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 0 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 1 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 1 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 1 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 1 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 1 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 1 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 1 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 1 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 1 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 1 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 1 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 1 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 1 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 1 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 1 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 1 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 1 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 1 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 1 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 1 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 1 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 1 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 1 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 1 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 1 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 1 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 1 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 1 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 1 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 1 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 1 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 1 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 1 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 1 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 1 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 1 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 1 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 1 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 1 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 1 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 1 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 1 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 1 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 1 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 1 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 1 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 1 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 1 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 1 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 1 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 1 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 1 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 1 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 1 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 1 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 1 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 1 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 1 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 1 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 1 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 1 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 1 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 1 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 1 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 1 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 1 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 1 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 1 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 1 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 1 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 1 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 1 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 1 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 1 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 1 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 1 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 1 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 1 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 1 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 1 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 1 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 1 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 1 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 1 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 1 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 1 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 1 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 1 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 1 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 1 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 1 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 1 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 1 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 1 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 1 | 306

## FA_SQTN
Failure Code | FA_SQTN |  |  |  | Number of Locations in failure code when defaults assigned: | 3 |  | Final Criticality Code |  | A | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | ANTENNA
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | Count | 54 | 1
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity |  |  | Selected ID | 37 | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10 |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System |  |  |  | 54 | 1
Safety | D | 9 | #N/A |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework
Environmental | H | 1 | 1 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C = |  | A | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table
Production | G | 3 | 4 |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing
Business | G | 3 | 4 |  |  | 4 |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity
[6 empty] | 4 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE
Loss of Function | D | 9 | #N/A | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps)
|  |  | #N/A |  |  |  | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers |  | A | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection |  |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security
Loss of Function | H | 1 | 1 | 72 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | G | 3 | 4 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | G | 3 | 4 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 0 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 0 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 0 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 0 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 0 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 0 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 0 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 0 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 0 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 0 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 0 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 0 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 0 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 0 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 0 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 0 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 0 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 0 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 0 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 0 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 0 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 0 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 0 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 0 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 0 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 0 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 0 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 0 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 0 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 0 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 0 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 0 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 0 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 0 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 0 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 0 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 0 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 0 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 0 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 0 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 0 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 0 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 0 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 0 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 0 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 0 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 0 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 0 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 0 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 0 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 0 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 0 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 0 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 0 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 0 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 0 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 0 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 0 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 0 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 0 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 0 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 0 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 0 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 0 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 0 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 0 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 0 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 0 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 0 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 0 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 0 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 0 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 0 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 0 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 0 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 0 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 0 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 0 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 0 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 0 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 0 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 0 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 0 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 0 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 0 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 0 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 0 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 0 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 0 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 0 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 0 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 0 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 0 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 0 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 0 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 0 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 0 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 0 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 0 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 0 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 0 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 0 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 0 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 0 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 0 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 0 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 0 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 0 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 0 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 0 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 0 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 0 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 0 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 0 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 0 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 0 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 0 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 0 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 0 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 0 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 1 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 0 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 0 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 0 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 0 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 0 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 0 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 0 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 0 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 0 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 0 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 0 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 0 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 0 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 0 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 0 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 0 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 0 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 0 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 0 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 0 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 0 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 0 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 0 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 0 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 0 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 0 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 0 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 0 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 0 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 0 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 0 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 0 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 0 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 0 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 0 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 0 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 0 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 0 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 0 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 0 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 0 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 0 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 0 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 0 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 0 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 0 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 0 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 0 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 0 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 0 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 0 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 0 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 0 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 0 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 0 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 0 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 0 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 0 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 0 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 0 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 0 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 0 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 0 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 0 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 0 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 0 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 0 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 0 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 0 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 0 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 0 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 0 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 0 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 0 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 0 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 0 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 0 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 0 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 0 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 0 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 0 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 0 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 0 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 0 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 0 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 0 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 0 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 0 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 0 | 306

## FA_SQTOF
Failure Code | FA_SQTOF |  |  |  | Number of Locations in failure code when defaults assigned: | 6 |  | Final Criticality Code |  | A | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | FIXED RADIO
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | Count | 54 | 1
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity |  |  | Selected ID | 37 | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10 |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System |  |  |  | 54 | 1
Safety | D | 9 | #N/A |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework
Environmental | H | 1 | 1 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C = |  | A | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table
Production | G | 3 | 4 |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing
Business | G | 3 | 4 |  |  | 4 |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity
[6 empty] | 4 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE
Loss of Function | D | 9 | #N/A | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps)
|  |  | #N/A |  |  |  | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers |  | A | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection |  |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security
Loss of Function | H | 1 | 1 | 72 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | G | 3 | 4 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | G | 3 | 4 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 0 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 0 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 0 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 0 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 0 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 0 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 0 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 0 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 0 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 0 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 0 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 0 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 0 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 0 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 0 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 0 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 0 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 0 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 0 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 0 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 0 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 0 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 0 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 0 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 0 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 0 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 0 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 0 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 0 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 0 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 0 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 0 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 0 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 0 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 0 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 0 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 0 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 0 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 0 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 0 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 0 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 0 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 0 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 0 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 0 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 0 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 0 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 0 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 0 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 0 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 0 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 0 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 0 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 0 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 0 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 0 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 0 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 0 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 0 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 0 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 0 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 0 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 0 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 0 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 0 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 0 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 0 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 0 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 0 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 0 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 0 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 0 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 0 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 0 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 0 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 0 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 0 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 0 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 0 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 0 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 0 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 0 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 0 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 0 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 0 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 0 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 0 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 0 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 0 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 0 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 0 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 0 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 0 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 0 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 0 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 0 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 0 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 0 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 0 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 0 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 0 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 0 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 0 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 0 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 0 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 0 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 0 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 0 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 0 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 0 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 0 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 0 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 0 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 0 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 0 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 0 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 0 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 0 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 0 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 0 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 1 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 0 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 0 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 0 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 0 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 0 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 0 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 0 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 0 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 0 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 0 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 0 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 0 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 0 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 0 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 0 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 0 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 0 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 0 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 0 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 0 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 0 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 0 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 0 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 0 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 0 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 0 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 0 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 0 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 0 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 0 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 0 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 0 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 0 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 0 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 0 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 0 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 0 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 0 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 0 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 0 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 0 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 0 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 0 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 0 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 0 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 0 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 0 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 0 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 0 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 0 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 0 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 0 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 0 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 0 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 0 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 0 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 0 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 0 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 0 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 0 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 0 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 0 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 0 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 0 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 0 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 0 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 0 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 0 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 0 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 0 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 0 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 0 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 0 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 0 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 0 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 0 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 0 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 0 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 0 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 0 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 0 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 0 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 0 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 0 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 0 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 0 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 0 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 0 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 0 | 306

## FA_SQTP
Failure Code | FA_SQTP |  |  |  | Number of Locations in failure code when defaults assigned: | 104 |  | Final Criticality Code |  | A | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | COMPUTER PERIPHERAL
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | #N/A | #N/A | Count | 54 | #N/A
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | #N/A | 2 | Stability loading control & watertight integrity | #N/A | #N/A | Selected ID | #N/A | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | #N/A | 3 | Station Keeping | #N/A | #N/A
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | #N/A | 4 | Swivel Stack Assembly | #N/A | #N/A
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 2 |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | #N/A | 5 | Swivel Fluid Barrier System | #N/A | #N/A |  | 54 | #N/A
Safety | H | 1 | 1 |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | #N/A | 6 | Swivel/Turret Pipework | #N/A | #N/A
Environmental | H | 1 | 1 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C = |  | A | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | #N/A | 7 | Turret Chain Table | #N/A | #N/A
Production | H | 1 | 1 |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | #N/A | 8 | Main Turret Bearing | #N/A | #N/A
Business | H | 1 | 1 |  |  | 2 |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | #N/A | 9 | Wellhead integrity | #N/A | #N/A
[6 empty] | 2 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | #N/A | 10 | Subsea Integrity | #N/A | #N/A
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | #N/A | 11 | Process Containment Integrity | #N/A | #N/A
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | #N/A | 12 | Gas Turbine Packages & Hydrocarbon RE | #N/A | #N/A
Loss of Function | H | 1 | 1 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | #N/A | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | #N/A | #N/A
|  |  | #N/A |  |  |  | #N/A | #N/A |  | #N/A | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | #N/A | 14 | Diesel Driven Packages | #N/A | #N/A
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | #N/A | 15 | Oil Storage & Offloading | #N/A | #N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | all NOTAGS, RJ45 network sockets - none allocated |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | #N/A | 16 | Overpressure Protection | #N/A | #N/A
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | #N/A | 17 | Blowdown vent and flare | #N/A | #N/A
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | #N/A | 18 | Digital security | #N/A | #N/A
Loss of Function | H | 1 | 1 | 72 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | #N/A | 19 | Control systems - LoPs | #N/A | #N/A
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | #N/A | 20 | Control systems - non LoPs, LOPA initiating causes | #N/A | #N/A
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | #N/A | 21 | Control systems - all others | #N/A | #N/A
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | #N/A | 22 | SIS - LoP Components | #N/A | #N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | #N/A | 23 | SIS - Non LoP Components | #N/A | #N/A
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | #N/A | 24 | Alarms & operator response | #N/A | #N/A
Loss of Function | H | 1 | 1 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | #N/A | 25 | Collision Prevention | #N/A | #N/A
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | #N/A | 26 | Export tanker birthing and position monitoring | #N/A | #N/A
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | #N/A | 27 | Bunding, Open and Closed Hazardous Drains | #N/A | #N/A
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | #N/A | 28 | Passive Fire Protection | #N/A | #N/A
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | #N/A | 29 | Blast Overpressure Protection | #N/A | #N/A
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | #N/A | 30 | Temporary refuge integrity | #N/A | #N/A
Loss of Function | H | 1 | 1 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | #N/A | 31 | Alarm Annunciation System: | #N/A | #N/A
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | #N/A | 32 | Personnel Address (PA) System | #N/A | #N/A
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | #N/A | 33 | Marine, Aircraft and Helicopter Radio System | #N/A | #N/A
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | #N/A | 34 | Telecommunications | #N/A | #N/A
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | #N/A | 35 | Electronic Muster System | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | #N/A | 36 | Facility Emergency Telephone & Hot line systems | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | #N/A | 37 | Facility radio system | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | #N/A | 38 | Emergency Power | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | #N/A | 39 | Emergency Lighting | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | #N/A | 40 | Ignition Prevention | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | #N/A | 41 | Inert Gas Blanketing | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | #N/A | 42 | Lifesaving Equipment | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | #N/A | 43 | Muster areas, escape and evacuation routes | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | #N/A | 44 | Lifeboats | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | #N/A | 45 | Means of escape to sea | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | #N/A | 46 | Helideck | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | #N/A | 47 | Rescue & Recovery Systems | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | #N/A | 48 | Cranes | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | #N/A | 49 | Lifting system | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | #N/A | 50 | Fire & Gas systems | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | #N/A | 51 | Emergency Shutdown Systems | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | #N/A | 52 | Riser ESDVs & EIVs | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | #N/A | 53 | Fire protection | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | #N/A | 54 | Miscellaneous fire protection systems | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | #N/A | 55 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | #N/A | 56 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | #N/A | 57 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | #N/A | 58 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | #N/A | 59 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | #N/A | 60 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | #N/A | 61 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | #N/A | 62 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | #N/A | 63 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | #N/A | 64 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | #N/A | 65 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | #N/A | 66 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | #N/A | 67 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | #N/A | 68 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | #N/A | 69 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | #N/A | 70 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | #N/A | 71 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | #N/A | 72 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | #N/A | 73 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | #N/A | 74 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | #N/A | 75 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | #N/A | 76 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | #N/A | 77 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | #N/A | 78 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | #N/A | 79 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | #N/A | 80 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | #N/A | 81 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | #N/A | 82 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | #N/A | 83 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | #N/A | 84 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | #N/A | 85 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | #N/A | 86 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | #N/A | 87 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | #N/A | 88 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | #N/A | 89 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | #N/A | 90 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | #N/A | 91 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | #N/A | 92 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | #N/A | 93 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | #N/A | 94 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | #N/A | 95 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | #N/A | 96 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | #N/A | 97 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | #N/A | 98 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | #N/A | 99 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | #N/A | 100 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | #N/A | 101 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | #N/A | 102 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | #N/A | 103 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | #N/A | 104 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | #N/A | 105 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | #N/A | 106 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | #N/A | 107 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | #N/A | 108 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | #N/A | 109 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | #N/A | 110 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | #N/A | 111 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | #N/A | 112 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | #N/A | 113 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | #N/A | 114 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | #N/A | 115 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | #N/A | 116 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | #N/A | 117 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | #N/A | 118 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | #N/A | 119 |  | #N/A | #N/A
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | #N/A | 120 |  | #N/A | #N/A
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | #N/A | 121 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | #N/A | 122 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | #N/A | 123 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | #N/A | 124 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | #N/A | 125 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | #N/A | 126 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | #N/A | 127 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | #N/A | 128 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | #N/A | 129 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | #N/A | 130 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | #N/A | 131 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | #N/A | 132 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | #N/A | 133 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | #N/A | 134 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | #N/A | 135 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | #N/A | 136 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | #N/A | 137 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | #N/A | 138 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | #N/A | 139 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | #N/A | 140 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | #N/A | 141 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | #N/A | 142 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | #N/A | 143 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | #N/A | 144 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | #N/A | 145 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | #N/A | 146 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | #N/A | 147 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | #N/A | 148 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | #N/A | 149 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | #N/A | 150 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | #N/A | 151 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | #N/A | 152 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | #N/A | 153 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | #N/A | 154 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | #N/A | 155 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | #N/A | 156 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | #N/A | 157 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | #N/A | 158 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | #N/A | 159 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | #N/A | 160 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | #N/A | 161 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | #N/A | 162 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | #N/A | 163 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | #N/A | 164 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | #N/A | 165 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | #N/A | 166 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | #N/A | 167 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | #N/A | 168 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | #N/A | 169 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | #N/A | 170 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | #N/A | 171 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | #N/A | 172 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | #N/A | 173 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | #N/A | 174 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | #N/A | 175 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | #N/A | 176 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | #N/A | 177 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | #N/A | 178 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | #N/A | 179 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | #N/A | 180 |  | #N/A | #N/A
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | #N/A | 181 |  | #N/A | #N/A
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | #N/A | 182 |  | #N/A | #N/A
[11 empty] | P6-A | Digital security | Architecture | A | 18 | #N/A | 183 |  | #N/A | #N/A
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | #N/A | 184 |  | #N/A | #N/A
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | #N/A | 185 |  | #N/A | #N/A
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | #N/A | 186 |  | #N/A | #N/A
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | #N/A | 187 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | #N/A | 188 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | #N/A | 189 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | #N/A | 190 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | #N/A | 191 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | #N/A | 192 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | #N/A | 193 |  | #N/A | #N/A
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | #N/A | 194 |  | #N/A | #N/A
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | #N/A | 195 |  | #N/A | #N/A
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | #N/A | 196 |  | #N/A | #N/A
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | #N/A | 197 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | #N/A | 198 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | #N/A | 199 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | #N/A | 200 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | #N/A | 201 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | #N/A | 202 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | #N/A | 203 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | #N/A | 204 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | #N/A | 205 |  | #N/A | #N/A
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | #N/A | 206 |  | #N/A | #N/A
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | #N/A | 207 |  | #N/A | #N/A
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | #N/A | 208 |  | #N/A | #N/A
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | #N/A | 209 |  | #N/A | #N/A
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | #N/A | 210 |  | #N/A | #N/A
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | #N/A | 211 |  | #N/A | #N/A
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | #N/A | 212 |  | #N/A | #N/A
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | #N/A | 213 |  | #N/A | #N/A
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | #N/A | 214 |  | #N/A | #N/A
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | #N/A | 215 |  | #N/A | #N/A
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | #N/A | 216 |  | #N/A | #N/A
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | #N/A | 217 |  | #N/A | #N/A
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | #N/A | 218 |  | #N/A | #N/A
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | #N/A | 219 |  | #N/A | #N/A
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | #N/A | 220 |  | #N/A | #N/A
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | #N/A | 221 |  | #N/A | #N/A
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | #N/A | 222 |  | #N/A | #N/A
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | #N/A | 223 |  | #N/A | #N/A
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | #N/A | 224 |  | #N/A | #N/A
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | #N/A | 225 |  | #N/A | #N/A
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | #N/A | 226 |  | #N/A | #N/A
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | #N/A | 227 |  | #N/A | #N/A
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | #N/A | 228 |  | #N/A | #N/A
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | #N/A | 229 |  | #N/A | #N/A
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | #N/A | 230 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | #N/A | 231 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | #N/A | 232 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | #N/A | 233 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | #N/A | 234 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | #N/A | 235 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | #N/A | 236 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | #N/A | 237 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | #N/A | 238 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | #N/A | 239 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | #N/A | 240 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | #N/A | 241 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | #N/A | 242 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | #N/A | 243 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | #N/A | 244 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | #N/A | 245 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | #N/A | 246 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | #N/A | 247 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | #N/A | 248 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | #N/A | 249 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | #N/A | 250 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | #N/A | 251 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | #N/A | 252 |  | #N/A | #N/A
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | #N/A | 253 |  | #N/A | #N/A
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | #N/A | 254 |  | #N/A | #N/A
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | #N/A | 255 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | #N/A | 256 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | #N/A | 257 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | #N/A | 258 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | #N/A | 259 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | #N/A | 260 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | #N/A | 261 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | #N/A | 262 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | #N/A | 263 |  | #N/A | #N/A
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | #N/A | 264 |  | #N/A | #N/A
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | #N/A | 265 |  | #N/A | #N/A
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | #N/A | 266 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | #N/A | 267 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Boom system | A | 48 | #N/A | 268 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | #N/A | 269 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Structure | A | 48 | #N/A | 270 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | #N/A | 271 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | #N/A | 272 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | #N/A | 273 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | #N/A | 274 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | #N/A | 275 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | #N/A | 276 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | #N/A | 277 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | #N/A | 278 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | #N/A | 279 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | #N/A | 280 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | #N/A | 281 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | #N/A | 282 |  | #N/A | #N/A
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | #N/A | 283 |  | #N/A | #N/A
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | #N/A | 284 |  | #N/A | #N/A
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | #N/A | 285 |  | #N/A | #N/A
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | #N/A | 286 |  | #N/A | #N/A
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | #N/A | 287 |  | #N/A | #N/A
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | #N/A | 288 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | #N/A | 289 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | #N/A | 290 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | #N/A | 291 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | #N/A | 292 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | #N/A | 293 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | #N/A | 294 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | #N/A | 295 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | #N/A | 296 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | #N/A | 297 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | #N/A | 298 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | #N/A | 299 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | #N/A | 300 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | #N/A | 301 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | #N/A | 302 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | #N/A | 303 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | #N/A | 304 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | #N/A | 305 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | #N/A | 306 |  | #N/A | #N/A

## FA_SQTS
Failure Code | FA_SQTS |  |  |  | Number of Locations in failure code when defaults assigned: | 101 |  | Final Criticality Code |  | A | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | TELEPHONE OR MULTIMEDIA EQUIPMENT
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity |  |  | Count | 54 | 0
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity |  |  | Selected ID | 36 | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10 |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System |  |  |  | 54 | #REF!
Safety | D | 9 | #N/A |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework
Environmental | H | 1 | 1 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C = |  | A | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table
Production | G | 3 | 4 |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing
Business | G | 3 | 4 |  |  | 4 |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity
[6 empty] | 4 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE
Loss of Function | D | 9 | #N/A | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps)
|  |  | #N/A |  |  |  | Facility Emergency Telephone & Hot line systems | Call control - PABX/IPT Ex telephones Designated emergency phones (Control rooms muster points etc.) Interconnecting cable plant and networks |  | #N/A | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection | Includes outdoor EX call points as well as control room IP phone, so will want to downrate non-EX phones |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security
Loss of Function | H | 1 | 1 | 72 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | G | 3 | 4 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | G | 3 | 4 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 0 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 0 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 0 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 0 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 0 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 0 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 0 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 0 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 0 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 0 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 0 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 0 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 0 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 0 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 0 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 0 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 0 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 0 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 0 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 0 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 0 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 0 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 0 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 0 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 0 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 0 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 0 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 0 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 0 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 0 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 0 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 0 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 0 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 0 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 0 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 0 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 0 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 0 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 0 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 0 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 0 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 0 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 0 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 0 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 0 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 0 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 0 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 0 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 0 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 0 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 0 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 0 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 0 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 0 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 0 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 0 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 0 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 0 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 0 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 0 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 0 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 0 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 0 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 0 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 0 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 0 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 0 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 0 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 0 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 0 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 0 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 0 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 0 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 0 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 0 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 0 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 0 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 0 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 0 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 0 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 0 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 0 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 0 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 0 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 0 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 0 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 0 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 0 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 0 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 0 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 0 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 0 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 0 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 0 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 0 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 0 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 0 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 0 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 0 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 0 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 0 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 0 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 0 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 0 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 0 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 0 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 0 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 0 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 0 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 0 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 0 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 0 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 0 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 0 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 0 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 0 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 0 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 0 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 0 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 0 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 0 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 0 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 0 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 0 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 0 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 0 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 0 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 0 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 0 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 0 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 0 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 0 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 0 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 0 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 0 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 0 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 0 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 0 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 0 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 0 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 0 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 0 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 0 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 0 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 0 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 0 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 0 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 0 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 0 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 0 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 0 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 0 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 0 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 0 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 0 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 0 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 0 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 0 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 0 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 0 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 0 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 0 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 0 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 0 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 0 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 0 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 0 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 0 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 0 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 0 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 0 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 0 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 0 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 0 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 0 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 0 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 0 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 0 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 0 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 0 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 0 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 0 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 0 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 0 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 0 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 0 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 0 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 0 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 0 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 0 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 0 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 0 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 0 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 0 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 0 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 0 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 0 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 0 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 0 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 0 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 0 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 0 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 0 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 0 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 0 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 0 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 0 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 0 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 0 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 0 | 306

## FA_SQTV
Failure Code | FA_SQTV |  |  |  | Number of Locations in failure code when defaults assigned: | 167 |  | Final Criticality Code |  | A | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | CCTV CAMERA UNIT
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | #N/A | #N/A | Count | 54 | #N/A
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | #N/A | 2 | Stability loading control & watertight integrity | #N/A | #N/A | Selected ID | #N/A | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | YES |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | #N/A | 3 | Station Keeping | #N/A | #N/A
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | #N/A | 4 | Swivel Stack Assembly | #N/A | #N/A
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 10 |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | #N/A | 5 | Swivel Fluid Barrier System | #N/A | #N/A |  | 54 | #N/A
Safety | D | 9 | #N/A |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | #N/A | 6 | Swivel/Turret Pipework | #N/A | #N/A
Environmental | G | 3 | 4 |  | Elements contributing to CMMS Location Criticality rating | 10 |  | Derived SAP A/B/C = |  | A | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | #N/A | 7 | Turret Chain Table | #N/A | #N/A
Production | G | 3 | 4 |  |  | 4 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | #N/A | 8 | Main Turret Bearing | #N/A | #N/A
Business | G | 3 | 4 |  |  | 4 |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | #N/A | 9 | Wellhead integrity | #N/A | #N/A
[6 empty] | 4 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | #N/A | 10 | Subsea Integrity | #N/A | #N/A
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | #N/A | 11 | Process Containment Integrity | #N/A | #N/A
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | #N/A | 12 | Gas Turbine Packages & Hydrocarbon RE | #N/A | #N/A
Loss of Function | D | 9 | #N/A | 68 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | #N/A | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | #N/A | #N/A
|  |  | #N/A |  |  |  | #N/A | #N/A |  | #N/A | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | #N/A | 14 | Diesel Driven Packages | #N/A | #N/A
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | #N/A | 15 | Oil Storage & Offloading | #N/A | #N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | None allocated - not explicitly listed in MAH table |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | #N/A | 16 | Overpressure Protection | #N/A | #N/A
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | #N/A | 17 | Blowdown vent and flare | #N/A | #N/A
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | #N/A | 18 | Digital security | #N/A | #N/A
Loss of Function | G | 3 | 4 | 71 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | #N/A | 19 | Control systems - LoPs | #N/A | #N/A
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | #N/A | 20 | Control systems - non LoPs, LOPA initiating causes | #N/A | #N/A
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | #N/A | 21 | Control systems - all others | #N/A | #N/A
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | #N/A | 22 | SIS - LoP Components | #N/A | #N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | #N/A | 23 | SIS - Non LoP Components | #N/A | #N/A
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | #N/A | 24 | Alarms & operator response | #N/A | #N/A
Loss of Function | G | 3 | 4 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | #N/A | 25 | Collision Prevention | #N/A | #N/A
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | #N/A | 26 | Export tanker birthing and position monitoring | #N/A | #N/A
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | #N/A | 27 | Bunding, Open and Closed Hazardous Drains | #N/A | #N/A
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | #N/A | 28 | Passive Fire Protection | #N/A | #N/A
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | #N/A | 29 | Blast Overpressure Protection | #N/A | #N/A
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | #N/A | 30 | Temporary refuge integrity | #N/A | #N/A
Loss of Function | G | 3 | 4 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | #N/A | 31 | Alarm Annunciation System: | #N/A | #N/A
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | #N/A | 32 | Personnel Address (PA) System | #N/A | #N/A
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | #N/A | 33 | Marine, Aircraft and Helicopter Radio System | #N/A | #N/A
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | #N/A | 34 | Telecommunications | #N/A | #N/A
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | #N/A | 35 | Electronic Muster System | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | #N/A | 36 | Facility Emergency Telephone & Hot line systems | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | #N/A | 37 | Facility radio system | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | #N/A | 38 | Emergency Power | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | #N/A | 39 | Emergency Lighting | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | #N/A | 40 | Ignition Prevention | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | #N/A | 41 | Inert Gas Blanketing | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | #N/A | 42 | Lifesaving Equipment | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | #N/A | 43 | Muster areas, escape and evacuation routes | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | #N/A | 44 | Lifeboats | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | #N/A | 45 | Means of escape to sea | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | #N/A | 46 | Helideck | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | #N/A | 47 | Rescue & Recovery Systems | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | #N/A | 48 | Cranes | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | #N/A | 49 | Lifting system | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | #N/A | 50 | Fire & Gas systems | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | #N/A | 51 | Emergency Shutdown Systems | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | #N/A | 52 | Riser ESDVs & EIVs | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | #N/A | 53 | Fire protection | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | #N/A | 54 | Miscellaneous fire protection systems | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | #N/A | 55 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | #N/A | 56 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | #N/A | 57 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | #N/A | 58 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | #N/A | 59 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | #N/A | 60 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | #N/A | 61 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | #N/A | 62 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | #N/A | 63 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | #N/A | 64 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | #N/A | 65 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | #N/A | 66 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | #N/A | 67 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | #N/A | 68 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | #N/A | 69 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | #N/A | 70 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | #N/A | 71 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | #N/A | 72 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | #N/A | 73 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | #N/A | 74 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | #N/A | 75 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | #N/A | 76 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | #N/A | 77 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | #N/A | 78 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | #N/A | 79 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | #N/A | 80 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | #N/A | 81 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | #N/A | 82 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | #N/A | 83 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | #N/A | 84 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | #N/A | 85 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | #N/A | 86 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | #N/A | 87 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | #N/A | 88 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | #N/A | 89 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | #N/A | 90 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | #N/A | 91 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | #N/A | 92 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | #N/A | 93 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | #N/A | 94 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | #N/A | 95 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | #N/A | 96 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | #N/A | 97 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | #N/A | 98 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | #N/A | 99 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | #N/A | 100 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | #N/A | 101 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | #N/A | 102 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | #N/A | 103 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | #N/A | 104 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | #N/A | 105 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | #N/A | 106 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | #N/A | 107 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | #N/A | 108 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | #N/A | 109 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | #N/A | 110 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | #N/A | 111 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | #N/A | 112 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | #N/A | 113 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | #N/A | 114 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | #N/A | 115 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | #N/A | 116 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | #N/A | 117 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | #N/A | 118 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | #N/A | 119 |  | #N/A | #N/A
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | #N/A | 120 |  | #N/A | #N/A
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | #N/A | 121 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | #N/A | 122 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | #N/A | 123 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | #N/A | 124 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | #N/A | 125 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | #N/A | 126 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | #N/A | 127 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | #N/A | 128 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | #N/A | 129 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | #N/A | 130 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | #N/A | 131 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | #N/A | 132 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | #N/A | 133 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | #N/A | 134 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | #N/A | 135 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | #N/A | 136 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | #N/A | 137 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | #N/A | 138 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | #N/A | 139 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | #N/A | 140 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | #N/A | 141 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | #N/A | 142 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | #N/A | 143 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | #N/A | 144 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | #N/A | 145 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | #N/A | 146 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | #N/A | 147 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | #N/A | 148 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | #N/A | 149 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | #N/A | 150 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | #N/A | 151 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | #N/A | 152 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | #N/A | 153 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | #N/A | 154 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | #N/A | 155 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | #N/A | 156 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | #N/A | 157 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | #N/A | 158 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | #N/A | 159 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | #N/A | 160 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | #N/A | 161 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | #N/A | 162 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | #N/A | 163 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | #N/A | 164 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | #N/A | 165 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | #N/A | 166 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | #N/A | 167 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | #N/A | 168 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | #N/A | 169 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | #N/A | 170 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | #N/A | 171 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | #N/A | 172 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | #N/A | 173 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | #N/A | 174 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | #N/A | 175 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | #N/A | 176 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | #N/A | 177 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | #N/A | 178 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | #N/A | 179 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | #N/A | 180 |  | #N/A | #N/A
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | #N/A | 181 |  | #N/A | #N/A
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | #N/A | 182 |  | #N/A | #N/A
[11 empty] | P6-A | Digital security | Architecture | A | 18 | #N/A | 183 |  | #N/A | #N/A
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | #N/A | 184 |  | #N/A | #N/A
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | #N/A | 185 |  | #N/A | #N/A
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | #N/A | 186 |  | #N/A | #N/A
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | #N/A | 187 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | #N/A | 188 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | #N/A | 189 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | #N/A | 190 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | #N/A | 191 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | #N/A | 192 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | #N/A | 193 |  | #N/A | #N/A
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | #N/A | 194 |  | #N/A | #N/A
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | #N/A | 195 |  | #N/A | #N/A
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | #N/A | 196 |  | #N/A | #N/A
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | #N/A | 197 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | #N/A | 198 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | #N/A | 199 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | #N/A | 200 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | #N/A | 201 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | #N/A | 202 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | #N/A | 203 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | #N/A | 204 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | #N/A | 205 |  | #N/A | #N/A
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | #N/A | 206 |  | #N/A | #N/A
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | #N/A | 207 |  | #N/A | #N/A
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | #N/A | 208 |  | #N/A | #N/A
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | #N/A | 209 |  | #N/A | #N/A
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | #N/A | 210 |  | #N/A | #N/A
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | #N/A | 211 |  | #N/A | #N/A
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | #N/A | 212 |  | #N/A | #N/A
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | #N/A | 213 |  | #N/A | #N/A
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | #N/A | 214 |  | #N/A | #N/A
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | #N/A | 215 |  | #N/A | #N/A
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | #N/A | 216 |  | #N/A | #N/A
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | #N/A | 217 |  | #N/A | #N/A
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | #N/A | 218 |  | #N/A | #N/A
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | #N/A | 219 |  | #N/A | #N/A
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | #N/A | 220 |  | #N/A | #N/A
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | #N/A | 221 |  | #N/A | #N/A
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | #N/A | 222 |  | #N/A | #N/A
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | #N/A | 223 |  | #N/A | #N/A
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | #N/A | 224 |  | #N/A | #N/A
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | #N/A | 225 |  | #N/A | #N/A
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | #N/A | 226 |  | #N/A | #N/A
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | #N/A | 227 |  | #N/A | #N/A
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | #N/A | 228 |  | #N/A | #N/A
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | #N/A | 229 |  | #N/A | #N/A
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | #N/A | 230 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | #N/A | 231 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | #N/A | 232 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | #N/A | 233 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | #N/A | 234 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | #N/A | 235 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | #N/A | 236 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | #N/A | 237 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | #N/A | 238 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | #N/A | 239 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | #N/A | 240 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | #N/A | 241 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | #N/A | 242 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | #N/A | 243 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | #N/A | 244 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | #N/A | 245 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | #N/A | 246 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | #N/A | 247 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | #N/A | 248 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | #N/A | 249 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | #N/A | 250 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | #N/A | 251 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | #N/A | 252 |  | #N/A | #N/A
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | #N/A | 253 |  | #N/A | #N/A
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | #N/A | 254 |  | #N/A | #N/A
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | #N/A | 255 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | #N/A | 256 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | #N/A | 257 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | #N/A | 258 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | #N/A | 259 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | #N/A | 260 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | #N/A | 261 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | #N/A | 262 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | #N/A | 263 |  | #N/A | #N/A
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | #N/A | 264 |  | #N/A | #N/A
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | #N/A | 265 |  | #N/A | #N/A
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | #N/A | 266 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | #N/A | 267 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Boom system | A | 48 | #N/A | 268 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | #N/A | 269 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Structure | A | 48 | #N/A | 270 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | #N/A | 271 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | #N/A | 272 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | #N/A | 273 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | #N/A | 274 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | #N/A | 275 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | #N/A | 276 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | #N/A | 277 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | #N/A | 278 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | #N/A | 279 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | #N/A | 280 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | #N/A | 281 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | #N/A | 282 |  | #N/A | #N/A
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | #N/A | 283 |  | #N/A | #N/A
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | #N/A | 284 |  | #N/A | #N/A
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | #N/A | 285 |  | #N/A | #N/A
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | #N/A | 286 |  | #N/A | #N/A
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | #N/A | 287 |  | #N/A | #N/A
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | #N/A | 288 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | #N/A | 289 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | #N/A | 290 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | #N/A | 291 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | #N/A | 292 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | #N/A | 293 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | #N/A | 294 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | #N/A | 295 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | #N/A | 296 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | #N/A | 297 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | #N/A | 298 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | #N/A | 299 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | #N/A | 300 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | #N/A | 301 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | #N/A | 302 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | #N/A | 303 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | #N/A | 304 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | #N/A | 305 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | #N/A | 306 |  | #N/A | #N/A

## FA_SQTW
Failure Code | FA_SQTW |  |  |  | Number of Locations in failure code when defaults assigned: | 17 |  | Final Criticality Code |  | A | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | WIRELESS COMMUNICATION OR CONTROL EQUIPMENT
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | #N/A | #N/A | Count | 54 | #N/A
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | #N/A | 2 | Stability loading control & watertight integrity | #N/A | #N/A | Selected ID | #N/A | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | #N/A | 3 | Station Keeping | #N/A | #N/A
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | #N/A | 4 | Swivel Stack Assembly | #N/A | #N/A
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8 |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | #N/A | 5 | Swivel Fluid Barrier System | #N/A | #N/A |  | 54 | #N/A
Safety | E | 7 | 10 |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | #N/A | 6 | Swivel/Turret Pipework | #N/A | #N/A
Environmental | H | 7 | 7 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C = |  | A | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | #N/A | 7 | Turret Chain Table | #N/A | #N/A
Production | G | 7 | 8 |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | #N/A | 8 | Main Turret Bearing | #N/A | #N/A
Business | H | 7 | 7 |  |  | 4 |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | #N/A | 9 | Wellhead integrity | #N/A | #N/A
[6 empty] | 2 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | #N/A | 10 | Subsea Integrity | #N/A | #N/A
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | #N/A | 11 | Process Containment Integrity | #N/A | #N/A
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | #N/A | 12 | Gas Turbine Packages & Hydrocarbon RE | #N/A | #N/A
Loss of Function | E | 7 | 10 | 69 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | #N/A | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | #N/A | #N/A
|  |  | #N/A |  |  |  | #N/A | #N/A |  | #N/A | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | #N/A | 14 | Diesel Driven Packages | #N/A | #N/A
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | #N/A | 15 | Oil Storage & Offloading | #N/A | #N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | NOTAGged personnel badge readers, described as access control, not electronic muster system so None allocated |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | #N/A | 16 | Overpressure Protection | #N/A | #N/A
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | #N/A | 17 | Blowdown vent and flare | #N/A | #N/A
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | #N/A | 18 | Digital security | #N/A | #N/A
Loss of Function | H | 7 | 7 | 72 | Initial Estimate based quick judegment (not in AGT) | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | #N/A | 19 | Control systems - LoPs | #N/A | #N/A
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | #N/A | 20 | Control systems - non LoPs, LOPA initiating causes | #N/A | #N/A
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | #N/A | 21 | Control systems - all others | #N/A | #N/A
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | #N/A | 22 | SIS - LoP Components | #N/A | #N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | #N/A | 23 | SIS - Non LoP Components | #N/A | #N/A
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | #N/A | 24 | Alarms & operator response | #N/A | #N/A
Loss of Function | G | 7 | 8 | 71 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | #N/A | 25 | Collision Prevention | #N/A | #N/A
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | #N/A | 26 | Export tanker birthing and position monitoring | #N/A | #N/A
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | #N/A | 27 | Bunding, Open and Closed Hazardous Drains | #N/A | #N/A
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | #N/A | 28 | Passive Fire Protection | #N/A | #N/A
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | #N/A | 29 | Blast Overpressure Protection | #N/A | #N/A
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | #N/A | 30 | Temporary refuge integrity | #N/A | #N/A
Loss of Function | H | 7 | 7 | 72 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | #N/A | 31 | Alarm Annunciation System: | #N/A | #N/A
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | #N/A | 32 | Personnel Address (PA) System | #N/A | #N/A
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | #N/A | 33 | Marine, Aircraft and Helicopter Radio System | #N/A | #N/A
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | #N/A | 34 | Telecommunications | #N/A | #N/A
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | #N/A | 35 | Electronic Muster System | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | #N/A | 36 | Facility Emergency Telephone & Hot line systems | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | #N/A | 37 | Facility radio system | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | #N/A | 38 | Emergency Power | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | #N/A | 39 | Emergency Lighting | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | #N/A | 40 | Ignition Prevention | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | #N/A | 41 | Inert Gas Blanketing | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | #N/A | 42 | Lifesaving Equipment | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | #N/A | 43 | Muster areas, escape and evacuation routes | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | #N/A | 44 | Lifeboats | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | #N/A | 45 | Means of escape to sea | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | #N/A | 46 | Helideck | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | #N/A | 47 | Rescue & Recovery Systems | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | #N/A | 48 | Cranes | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | #N/A | 49 | Lifting system | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | #N/A | 50 | Fire & Gas systems | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | #N/A | 51 | Emergency Shutdown Systems | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | #N/A | 52 | Riser ESDVs & EIVs | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | #N/A | 53 | Fire protection | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | #N/A | 54 | Miscellaneous fire protection systems | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | #N/A | 55 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | #N/A | 56 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | #N/A | 57 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | #N/A | 58 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | #N/A | 59 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | #N/A | 60 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | #N/A | 61 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | #N/A | 62 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | #N/A | 63 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | #N/A | 64 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | #N/A | 65 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | #N/A | 66 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | #N/A | 67 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | #N/A | 68 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | #N/A | 69 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | #N/A | 70 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | #N/A | 71 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | #N/A | 72 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | #N/A | 73 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | #N/A | 74 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | #N/A | 75 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | #N/A | 76 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | #N/A | 77 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | #N/A | 78 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | #N/A | 79 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | #N/A | 80 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | #N/A | 81 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | #N/A | 82 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | #N/A | 83 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | #N/A | 84 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | #N/A | 85 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | #N/A | 86 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | #N/A | 87 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | #N/A | 88 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | #N/A | 89 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | #N/A | 90 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | #N/A | 91 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | #N/A | 92 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | #N/A | 93 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | #N/A | 94 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | #N/A | 95 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | #N/A | 96 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | #N/A | 97 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | #N/A | 98 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | #N/A | 99 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | #N/A | 100 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | #N/A | 101 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | #N/A | 102 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | #N/A | 103 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | #N/A | 104 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | #N/A | 105 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | #N/A | 106 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | #N/A | 107 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | #N/A | 108 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | #N/A | 109 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | #N/A | 110 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | #N/A | 111 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | #N/A | 112 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | #N/A | 113 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | #N/A | 114 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | #N/A | 115 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | #N/A | 116 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | #N/A | 117 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | #N/A | 118 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | #N/A | 119 |  | #N/A | #N/A
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | #N/A | 120 |  | #N/A | #N/A
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | #N/A | 121 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | #N/A | 122 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | #N/A | 123 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | #N/A | 124 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | #N/A | 125 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | #N/A | 126 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | #N/A | 127 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | #N/A | 128 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | #N/A | 129 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | #N/A | 130 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | #N/A | 131 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | #N/A | 132 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | #N/A | 133 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | #N/A | 134 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | #N/A | 135 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | #N/A | 136 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | #N/A | 137 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | #N/A | 138 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | #N/A | 139 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | #N/A | 140 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | #N/A | 141 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | #N/A | 142 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | #N/A | 143 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | #N/A | 144 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | #N/A | 145 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | #N/A | 146 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | #N/A | 147 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | #N/A | 148 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | #N/A | 149 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | #N/A | 150 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | #N/A | 151 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | #N/A | 152 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | #N/A | 153 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | #N/A | 154 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | #N/A | 155 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | #N/A | 156 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | #N/A | 157 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | #N/A | 158 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | #N/A | 159 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | #N/A | 160 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | #N/A | 161 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | #N/A | 162 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | #N/A | 163 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | #N/A | 164 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | #N/A | 165 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | #N/A | 166 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | #N/A | 167 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | #N/A | 168 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | #N/A | 169 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | #N/A | 170 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | #N/A | 171 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | #N/A | 172 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | #N/A | 173 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | #N/A | 174 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | #N/A | 175 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | #N/A | 176 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | #N/A | 177 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | #N/A | 178 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | #N/A | 179 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | #N/A | 180 |  | #N/A | #N/A
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | #N/A | 181 |  | #N/A | #N/A
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | #N/A | 182 |  | #N/A | #N/A
[11 empty] | P6-A | Digital security | Architecture | A | 18 | #N/A | 183 |  | #N/A | #N/A
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | #N/A | 184 |  | #N/A | #N/A
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | #N/A | 185 |  | #N/A | #N/A
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | #N/A | 186 |  | #N/A | #N/A
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | #N/A | 187 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | #N/A | 188 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | #N/A | 189 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | #N/A | 190 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | #N/A | 191 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | #N/A | 192 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | #N/A | 193 |  | #N/A | #N/A
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | #N/A | 194 |  | #N/A | #N/A
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | #N/A | 195 |  | #N/A | #N/A
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | #N/A | 196 |  | #N/A | #N/A
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | #N/A | 197 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | #N/A | 198 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | #N/A | 199 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | #N/A | 200 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | #N/A | 201 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | #N/A | 202 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | #N/A | 203 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | #N/A | 204 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | #N/A | 205 |  | #N/A | #N/A
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | #N/A | 206 |  | #N/A | #N/A
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | #N/A | 207 |  | #N/A | #N/A
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | #N/A | 208 |  | #N/A | #N/A
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | #N/A | 209 |  | #N/A | #N/A
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | #N/A | 210 |  | #N/A | #N/A
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | #N/A | 211 |  | #N/A | #N/A
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | #N/A | 212 |  | #N/A | #N/A
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | #N/A | 213 |  | #N/A | #N/A
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | #N/A | 214 |  | #N/A | #N/A
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | #N/A | 215 |  | #N/A | #N/A
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | #N/A | 216 |  | #N/A | #N/A
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | #N/A | 217 |  | #N/A | #N/A
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | #N/A | 218 |  | #N/A | #N/A
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | #N/A | 219 |  | #N/A | #N/A
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | #N/A | 220 |  | #N/A | #N/A
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | #N/A | 221 |  | #N/A | #N/A
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | #N/A | 222 |  | #N/A | #N/A
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | #N/A | 223 |  | #N/A | #N/A
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | #N/A | 224 |  | #N/A | #N/A
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | #N/A | 225 |  | #N/A | #N/A
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | #N/A | 226 |  | #N/A | #N/A
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | #N/A | 227 |  | #N/A | #N/A
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | #N/A | 228 |  | #N/A | #N/A
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | #N/A | 229 |  | #N/A | #N/A
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | #N/A | 230 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | #N/A | 231 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | #N/A | 232 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | #N/A | 233 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | #N/A | 234 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | #N/A | 235 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | #N/A | 236 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | #N/A | 237 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | #N/A | 238 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | #N/A | 239 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | #N/A | 240 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | #N/A | 241 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | #N/A | 242 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | #N/A | 243 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | #N/A | 244 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | #N/A | 245 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | #N/A | 246 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | #N/A | 247 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | #N/A | 248 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | #N/A | 249 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | #N/A | 250 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | #N/A | 251 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | #N/A | 252 |  | #N/A | #N/A
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | #N/A | 253 |  | #N/A | #N/A
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | #N/A | 254 |  | #N/A | #N/A
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | #N/A | 255 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | #N/A | 256 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | #N/A | 257 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | #N/A | 258 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | #N/A | 259 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | #N/A | 260 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | #N/A | 261 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | #N/A | 262 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | #N/A | 263 |  | #N/A | #N/A
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | #N/A | 264 |  | #N/A | #N/A
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | #N/A | 265 |  | #N/A | #N/A
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | #N/A | 266 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | #N/A | 267 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Boom system | A | 48 | #N/A | 268 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | #N/A | 269 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Structure | A | 48 | #N/A | 270 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | #N/A | 271 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | #N/A | 272 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | #N/A | 273 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | #N/A | 274 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | #N/A | 275 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | #N/A | 276 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | #N/A | 277 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | #N/A | 278 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | #N/A | 279 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | #N/A | 280 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | #N/A | 281 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | #N/A | 282 |  | #N/A | #N/A
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | #N/A | 283 |  | #N/A | #N/A
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | #N/A | 284 |  | #N/A | #N/A
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | #N/A | 285 |  | #N/A | #N/A
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | #N/A | 286 |  | #N/A | #N/A
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | #N/A | 287 |  | #N/A | #N/A
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | #N/A | 288 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | #N/A | 289 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | #N/A | 290 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | #N/A | 291 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | #N/A | 292 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | #N/A | 293 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | #N/A | 294 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | #N/A | 295 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | #N/A | 296 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | #N/A | 297 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | #N/A | 298 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | #N/A | 299 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | #N/A | 300 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | #N/A | 301 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | #N/A | 302 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | #N/A | 303 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | #N/A | 304 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | #N/A | 305 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | #N/A | 306 |  | #N/A | #N/A

## FA_SQTY
Failure Code | FA_SQTY |  |  |  | Number of Locations in failure code when defaults assigned: | 4 |  | Final Criticality Code |  | A | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | RECEIVER / TRANSMITTER
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | Count | 54 | 2
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | Selected ID | 50 | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8 |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System |  |  |  | 54 | 2
Safety | E | 7 | 10 |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework
Environmental | H | 1 | 1 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C = |  | A | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table
Production | G | 3 | 4 |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing
Business | G | 3 | 4 |  |  | 4 |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity
[6 empty] | 4 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE
Loss of Function | E | 7 | 10 | 69 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps)
|  |  | #N/A |  |  |  | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel |  | A | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection | NOTTAGged gas detectors |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security
Loss of Function | H | 1 | 1 | 72 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | G | 3 | 4 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | G | 3 | 4 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 0 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 0 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 0 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 0 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 0 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 0 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 0 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 0 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 0 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 0 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 0 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 0 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 0 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 0 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 0 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 0 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 0 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 0 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 0 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 0 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 0 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 0 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 0 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 0 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 0 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 0 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 0 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 0 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 0 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 0 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 0 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 0 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 0 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 0 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 0 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 0 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 0 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 0 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 0 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 0 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 0 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 0 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 0 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 0 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 0 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 0 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 0 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 0 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 0 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 0 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 0 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 0 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 0 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 0 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 0 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 0 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 0 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 0 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 0 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 0 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 0 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 0 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 0 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 0 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 0 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 0 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 0 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 0 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 0 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 0 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 0 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 0 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 0 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 0 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 0 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 0 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 0 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 0 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 0 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 0 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 0 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 0 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 0 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 0 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 0 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 0 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 0 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 0 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 0 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 0 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 0 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 0 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 0 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 0 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 0 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 0 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 0 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 0 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 0 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 0 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 0 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 0 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 0 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 0 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 0 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 0 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 0 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 0 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 0 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 0 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 0 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 0 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 0 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 0 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 0 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 0 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 0 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 0 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 0 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 0 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 0 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 0 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 0 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 0 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 0 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 0 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 0 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 0 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 0 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 0 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 0 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 0 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 0 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 0 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 0 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 0 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 0 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 0 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 0 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 0 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 0 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 0 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 0 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 0 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 0 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 0 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 0 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 0 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 0 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 0 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 0 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 0 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 0 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 0 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 0 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 0 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 0 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 0 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 0 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 0 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 0 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 0 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 0 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 0 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 0 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 0 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 0 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 0 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 0 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 0 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 0 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 0 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 0 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 0 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 0 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 0 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 0 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 0 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 0 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 0 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 0 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 0 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 0 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 0 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 0 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 0 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 0 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 1 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 2 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 2 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 2 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 2 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 2 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 2 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 2 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 2 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 2 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 2 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 2 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 2 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 2 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 2 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 2 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 2 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 2 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 2 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 2 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 2 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 2 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 2 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 2 | 306

## FA_SYLH
Failure Code | FA_SYLH |  |  |  | Number of Locations in failure code when defaults assigned: | 316 |  | Final Criticality Code |  | A | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | SYSTEM LEVEL HIERARCHY
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | #N/A | #N/A | Count | 54 | #N/A
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | #N/A | 2 | Stability loading control & watertight integrity | #N/A | #N/A | Selected ID | #N/A | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | #N/A | 3 | Station Keeping | #N/A | #N/A
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | #N/A | 4 | Swivel Stack Assembly | #N/A | #N/A
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 8 |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | #N/A | 5 | Swivel Fluid Barrier System | #N/A | #N/A |  | 54 | #N/A
Safety | E | 7 | 10 |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | #N/A | 6 | Swivel/Turret Pipework | #N/A | #N/A
Environmental | E | 7 | 10 |  | Elements contributing to CMMS Location Criticality rating | 8 |  | Derived SAP A/B/C = |  | A | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | #N/A | 7 | Turret Chain Table | #N/A | #N/A
Production | E | 7 | 10 |  |  | 8 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | #N/A | 8 | Main Turret Bearing | #N/A | #N/A
Business | E | 7 | 10 |  |  | 8 |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | #N/A | 9 | Wellhead integrity | #N/A | #N/A
[6 empty] | 8 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | #N/A | 10 | Subsea Integrity | #N/A | #N/A
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | #N/A | 11 | Process Containment Integrity | #N/A | #N/A
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | #N/A | 12 | Gas Turbine Packages & Hydrocarbon RE | #N/A | #N/A
Loss of Function | E | 7 | 10 | 69 | Initial Estimate based quick judegment (not in AGT) |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | #N/A | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | #N/A | #N/A
|  |  | #N/A |  |  |  | #N/A | #N/A |  | #N/A | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | #N/A | 14 | Diesel Driven Packages | #N/A | #N/A
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | #N/A | 15 | Oil Storage & Offloading | #N/A | #N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | None allocated - Assumed non-physically meaningful or pending proper classification |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | #N/A | 16 | Overpressure Protection | #N/A | #N/A
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | #N/A | 17 | Blowdown vent and flare | #N/A | #N/A
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | #N/A | 18 | Digital security | #N/A | #N/A
Loss of Function | E | 7 | 10 | 69 | Initial Estimate based quick judegment (not in AGT) | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | #N/A | 19 | Control systems - LoPs | #N/A | #N/A
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | #N/A | 20 | Control systems - non LoPs, LOPA initiating causes | #N/A | #N/A
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | #N/A | 21 | Control systems - all others | #N/A | #N/A
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | #N/A | 22 | SIS - LoP Components | #N/A | #N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | #N/A | 23 | SIS - Non LoP Components | #N/A | #N/A
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | #N/A | 24 | Alarms & operator response | #N/A | #N/A
Loss of Function | E | 7 | 10 | 69 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | #N/A | 25 | Collision Prevention | #N/A | #N/A
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | No | A | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | #N/A | 26 | Export tanker birthing and position monitoring | #N/A | #N/A
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | No | B | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | #N/A | 27 | Bunding, Open and Closed Hazardous Drains | #N/A | #N/A
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | No |  | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | #N/A | 28 | Passive Fire Protection | #N/A | #N/A
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | #N/A | 29 | Blast Overpressure Protection | #N/A | #N/A
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | #N/A | 30 | Temporary refuge integrity | #N/A | #N/A
Loss of Function | E | 7 | 10 | 69 | Initial Estimate based quick judegment (not in AGT) |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | #N/A | 31 | Alarm Annunciation System: | #N/A | #N/A
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | #N/A | 32 | Personnel Address (PA) System | #N/A | #N/A
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | #N/A | 33 | Marine, Aircraft and Helicopter Radio System | #N/A | #N/A
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | #N/A | 34 | Telecommunications | #N/A | #N/A
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | #N/A | 35 | Electronic Muster System | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | #N/A | 36 | Facility Emergency Telephone & Hot line systems | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | #N/A | 37 | Facility radio system | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | #N/A | 38 | Emergency Power | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | #N/A | 39 | Emergency Lighting | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | #N/A | 40 | Ignition Prevention | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | #N/A | 41 | Inert Gas Blanketing | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | #N/A | 42 | Lifesaving Equipment | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | #N/A | 43 | Muster areas, escape and evacuation routes | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | #N/A | 44 | Lifeboats | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | #N/A | 45 | Means of escape to sea | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | #N/A | 46 | Helideck | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | #N/A | 47 | Rescue & Recovery Systems | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | #N/A | 48 | Cranes | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | #N/A | 49 | Lifting system | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | #N/A | 50 | Fire & Gas systems | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | #N/A | 51 | Emergency Shutdown Systems | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | #N/A | 52 | Riser ESDVs & EIVs | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | #N/A | 53 | Fire protection | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | #N/A | 54 | Miscellaneous fire protection systems | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | #N/A | 55 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | #N/A | 56 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | #N/A | 57 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | #N/A | 58 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | #N/A | 59 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | #N/A | 60 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | #N/A | 61 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | #N/A | 62 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | #N/A | 63 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | #N/A | 64 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | #N/A | 65 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | #N/A | 66 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | #N/A | 67 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | #N/A | 68 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | #N/A | 69 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | #N/A | 70 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | #N/A | 71 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | #N/A | 72 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | #N/A | 73 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | #N/A | 74 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | #N/A | 75 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | #N/A | 76 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | #N/A | 77 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | #N/A | 78 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | #N/A | 79 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | #N/A | 80 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | #N/A | 81 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | #N/A | 82 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | #N/A | 83 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | #N/A | 84 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | #N/A | 85 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | #N/A | 86 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | #N/A | 87 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | #N/A | 88 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | #N/A | 89 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | #N/A | 90 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | #N/A | 91 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | #N/A | 92 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | #N/A | 93 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | #N/A | 94 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | #N/A | 95 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | #N/A | 96 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | #N/A | 97 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | #N/A | 98 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | #N/A | 99 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | #N/A | 100 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | #N/A | 101 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | #N/A | 102 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | #N/A | 103 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | #N/A | 104 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | #N/A | 105 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | #N/A | 106 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | #N/A | 107 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | #N/A | 108 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | #N/A | 109 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | #N/A | 110 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | #N/A | 111 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | #N/A | 112 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | #N/A | 113 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | #N/A | 114 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | #N/A | 115 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | #N/A | 116 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | #N/A | 117 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | #N/A | 118 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | #N/A | 119 |  | #N/A | #N/A
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | #N/A | 120 |  | #N/A | #N/A
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | #N/A | 121 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | #N/A | 122 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | #N/A | 123 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | #N/A | 124 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | #N/A | 125 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | #N/A | 126 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | #N/A | 127 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | #N/A | 128 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | #N/A | 129 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | #N/A | 130 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | #N/A | 131 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | #N/A | 132 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | #N/A | 133 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | #N/A | 134 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | #N/A | 135 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | #N/A | 136 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | #N/A | 137 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | #N/A | 138 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | #N/A | 139 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | #N/A | 140 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | #N/A | 141 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | #N/A | 142 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | #N/A | 143 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | #N/A | 144 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | #N/A | 145 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | #N/A | 146 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | #N/A | 147 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | #N/A | 148 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | #N/A | 149 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | #N/A | 150 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | #N/A | 151 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | #N/A | 152 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | #N/A | 153 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | #N/A | 154 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | #N/A | 155 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | #N/A | 156 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | #N/A | 157 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | #N/A | 158 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | #N/A | 159 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | #N/A | 160 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | #N/A | 161 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | #N/A | 162 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | #N/A | 163 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | #N/A | 164 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | #N/A | 165 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | #N/A | 166 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | #N/A | 167 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | #N/A | 168 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | #N/A | 169 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | #N/A | 170 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | #N/A | 171 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | #N/A | 172 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | #N/A | 173 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | #N/A | 174 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | #N/A | 175 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | #N/A | 176 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | #N/A | 177 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | #N/A | 178 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | #N/A | 179 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | #N/A | 180 |  | #N/A | #N/A
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | #N/A | 181 |  | #N/A | #N/A
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | #N/A | 182 |  | #N/A | #N/A
[11 empty] | P6-A | Digital security | Architecture | A | 18 | #N/A | 183 |  | #N/A | #N/A
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | #N/A | 184 |  | #N/A | #N/A
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | #N/A | 185 |  | #N/A | #N/A
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | #N/A | 186 |  | #N/A | #N/A
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | #N/A | 187 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | #N/A | 188 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | #N/A | 189 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | #N/A | 190 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | #N/A | 191 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | #N/A | 192 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | #N/A | 193 |  | #N/A | #N/A
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | #N/A | 194 |  | #N/A | #N/A
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | #N/A | 195 |  | #N/A | #N/A
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | #N/A | 196 |  | #N/A | #N/A
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | #N/A | 197 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | #N/A | 198 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | #N/A | 199 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | #N/A | 200 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | #N/A | 201 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | #N/A | 202 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | #N/A | 203 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | #N/A | 204 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | #N/A | 205 |  | #N/A | #N/A
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | #N/A | 206 |  | #N/A | #N/A
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | #N/A | 207 |  | #N/A | #N/A
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | #N/A | 208 |  | #N/A | #N/A
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | #N/A | 209 |  | #N/A | #N/A
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | #N/A | 210 |  | #N/A | #N/A
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | #N/A | 211 |  | #N/A | #N/A
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | #N/A | 212 |  | #N/A | #N/A
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | #N/A | 213 |  | #N/A | #N/A
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | #N/A | 214 |  | #N/A | #N/A
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | #N/A | 215 |  | #N/A | #N/A
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | #N/A | 216 |  | #N/A | #N/A
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | #N/A | 217 |  | #N/A | #N/A
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | #N/A | 218 |  | #N/A | #N/A
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | #N/A | 219 |  | #N/A | #N/A
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | #N/A | 220 |  | #N/A | #N/A
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | #N/A | 221 |  | #N/A | #N/A
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | #N/A | 222 |  | #N/A | #N/A
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | #N/A | 223 |  | #N/A | #N/A
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | #N/A | 224 |  | #N/A | #N/A
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | #N/A | 225 |  | #N/A | #N/A
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | #N/A | 226 |  | #N/A | #N/A
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | #N/A | 227 |  | #N/A | #N/A
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | #N/A | 228 |  | #N/A | #N/A
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | #N/A | 229 |  | #N/A | #N/A
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | #N/A | 230 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | #N/A | 231 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | #N/A | 232 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | #N/A | 233 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | #N/A | 234 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | #N/A | 235 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | #N/A | 236 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | #N/A | 237 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | #N/A | 238 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | #N/A | 239 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | #N/A | 240 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | #N/A | 241 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | #N/A | 242 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | #N/A | 243 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | #N/A | 244 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | #N/A | 245 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | #N/A | 246 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | #N/A | 247 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | #N/A | 248 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | #N/A | 249 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | #N/A | 250 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | #N/A | 251 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | #N/A | 252 |  | #N/A | #N/A
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | #N/A | 253 |  | #N/A | #N/A
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | #N/A | 254 |  | #N/A | #N/A
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | #N/A | 255 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | #N/A | 256 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | #N/A | 257 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | #N/A | 258 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | #N/A | 259 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | #N/A | 260 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | #N/A | 261 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | #N/A | 262 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | #N/A | 263 |  | #N/A | #N/A
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | #N/A | 264 |  | #N/A | #N/A
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | #N/A | 265 |  | #N/A | #N/A
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | #N/A | 266 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | #N/A | 267 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Boom system | A | 48 | #N/A | 268 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | #N/A | 269 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Structure | A | 48 | #N/A | 270 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | #N/A | 271 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | #N/A | 272 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | #N/A | 273 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | #N/A | 274 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | #N/A | 275 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | #N/A | 276 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | #N/A | 277 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | #N/A | 278 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | #N/A | 279 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | #N/A | 280 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | #N/A | 281 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | #N/A | 282 |  | #N/A | #N/A
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | #N/A | 283 |  | #N/A | #N/A
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | #N/A | 284 |  | #N/A | #N/A
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | #N/A | 285 |  | #N/A | #N/A
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | #N/A | 286 |  | #N/A | #N/A
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | #N/A | 287 |  | #N/A | #N/A
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | #N/A | 288 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | #N/A | 289 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | #N/A | 290 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | #N/A | 291 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | #N/A | 292 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | #N/A | 293 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | #N/A | 294 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | #N/A | 295 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | #N/A | 296 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | #N/A | 297 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | #N/A | 298 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | #N/A | 299 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | #N/A | 300 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | #N/A | 301 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | #N/A | 302 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | #N/A | 303 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | #N/A | 304 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | #N/A | 305 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | #N/A | 306 |  | #N/A | #N/A

## FA_WECO
Failure Code | FA_WECO |  |  |  | Number of Locations in failure code when defaults assigned: | 11 |  | Final Criticality Code |  | B | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | OVERHEAD CRANE
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | Gas Generator | A | Count | 54 | 12
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | 0 | 2 | Stability loading control & watertight integrity | Alternators | B | Selected ID | 12 | 3
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | 0 | 3 | Station Keeping | Power Turbine | B
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | 0 | 4 | Swivel Stack Assembly | All Casing joints, fittings and seals | B
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 6 |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | 0 | 5 | Swivel Fluid Barrier System | All Shaft Seals | A |  | 54 | 12
Safety | H | 2 | 2 |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | 0 | 6 | Swivel/Turret Pipework | All coupling members | B
Environmental | H | 2 | 2 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C = |  | B | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | 0 | 7 | Turret Chain Table | Pressurized Enclosures | A
Production | G | 4 | 5 |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | 0 | 8 | Main Turret Bearing | Fire & Gas System | A
Business | F | 6 | 8 |  |  | 4 |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | 0 | 9 | Wellhead integrity | All Shaft Seals System Ancillaries | A
[6 empty] | 6 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | 0 | 10 | Subsea Integrity | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | 0 | 11 | Process Containment Integrity | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | 0 | 12 | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | 0 | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps)
|  |  | #N/A |  |  |  | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) |  | B | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | 0 | 14 | Diesel Driven Packages
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | 0 | 15 | Oil Storage & Offloading
|  |  | #N/A |  |  |  | Comment on barrier selection | Maintenance equipment on RE packages |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | 0 | 16 | Overpressure Protection
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | 0 | 17 | Blowdown vent and flare
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | 0 | 18 | Digital security
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | 0 | 19 | Control systems - LoPs
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | 0 | 20 | Control systems - non LoPs, LOPA initiating causes
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | 0 | 21 | Control systems - all others
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | 0 | 22 | SIS - LoP Components
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | 0 | 23 | SIS - Non LoP Components
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | 0 | 24 | Alarms & operator response
Loss of Function | G | 4 | 5 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | 0 | 25 | Collision Prevention
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | 0 | 26 | Export tanker birthing and position monitoring
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | 0 | 27 | Bunding, Open and Closed Hazardous Drains
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | 0 | 28 | Passive Fire Protection
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | 0 | 29 | Blast Overpressure Protection
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | 0 | 30 | Temporary refuge integrity
Loss of Function | F | 6 | 8 | 70 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | 0 | 31 | Alarm Annunciation System:
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | 0 | 32 | Personnel Address (PA) System
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | 0 | 33 | Marine, Aircraft and Helicopter Radio System
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | 0 | 34 | Telecommunications
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | 0 | 35 | Electronic Muster System
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | 0 | 36 | Facility Emergency Telephone & Hot line systems
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | 0 | 37 | Facility radio system
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | 0 | 38 | Emergency Power
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | 0 | 39 | Emergency Lighting
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | 0 | 40 | Ignition Prevention
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | 0 | 41 | Inert Gas Blanketing
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | 0 | 42 | Lifesaving Equipment
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | 0 | 43 | Muster areas, escape and evacuation routes
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | 0 | 44 | Lifeboats
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | 0 | 45 | Means of escape to sea
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | 0 | 46 | Helideck
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | 0 | 47 | Rescue & Recovery Systems
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | 0 | 48 | Cranes
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | 0 | 49 | Lifting system
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | 0 | 50 | Fire & Gas systems
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | 0 | 51 | Emergency Shutdown Systems
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | 0 | 52 | Riser ESDVs & EIVs
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | 0 | 53 | Fire protection
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | 0 | 54 | Miscellaneous fire protection systems
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | 0 | 55
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | 0 | 56
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | 0 | 57
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | 0 | 58
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | 0 | 59
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | 0 | 60
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | 0 | 61
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | 0 | 62
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | 0 | 63
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | 0 | 64
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | 0 | 65
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | 0 | 66
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | 0 | 67
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | 0 | 68
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | 0 | 69
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | 0 | 70
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | 0 | 71
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | 0 | 72
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | 0 | 73
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | 0 | 74
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | 0 | 75
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | 0 | 76
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | 0 | 77
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | 0 | 78
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | 0 | 79
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | 0 | 80
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | 0 | 81
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | 0 | 82
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | 0 | 83
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | 0 | 84
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | 0 | 85
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | 0 | 86
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | 0 | 87
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | 0 | 88
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | 0 | 89
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | 0 | 90
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | 0 | 91
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | 0 | 92
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | 0 | 93
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | 0 | 94
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | 0 | 95
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | 0 | 96
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | 0 | 97
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | 0 | 98
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | 0 | 99
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | 0 | 100
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | 0 | 101
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | 0 | 102
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | 0 | 103
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | 0 | 104
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | 0 | 105
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | 0 | 106
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | 0 | 107
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | 1 | 108
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | 2 | 109
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | 3 | 110
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | 4 | 111
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | 5 | 112
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | 6 | 113
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | 7 | 114
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | 8 | 115
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | 9 | 116
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | 10 | 117
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | 11 | 118
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | 12 | 119
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | 12 | 120
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | 12 | 121
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | 12 | 122
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | 12 | 123
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | 12 | 124
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | 12 | 125
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | 12 | 126
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | 12 | 127
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | 12 | 128
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | 12 | 129
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | 12 | 130
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | 12 | 131
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | 12 | 132
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | 12 | 133
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | 12 | 134
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | 12 | 135
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | 12 | 136
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | 12 | 137
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | 12 | 138
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | 12 | 139
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | 12 | 140
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | 12 | 141
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | 12 | 142
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | 12 | 143
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | 12 | 144
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | 12 | 145
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | 12 | 146
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | 12 | 147
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | 12 | 148
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | 12 | 149
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | 12 | 150
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | 12 | 151
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | 12 | 152
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | 12 | 153
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | 12 | 154
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | 12 | 155
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | 12 | 156
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | 12 | 157
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | 12 | 158
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | 12 | 159
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | 12 | 160
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | 12 | 161
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | 12 | 162
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | 12 | 163
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | 12 | 164
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | 12 | 165
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | 12 | 166
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 12 | 167
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | 12 | 168
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | 12 | 169
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | 12 | 170
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | 12 | 171
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | 12 | 172
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | 12 | 173
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | 12 | 174
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | 12 | 175
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | 12 | 176
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | 12 | 177
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | 12 | 178
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | 12 | 179
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | 12 | 180
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | 12 | 181
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | 12 | 182
[11 empty] | P6-A | Digital security | Architecture | A | 18 | 12 | 183
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | 12 | 184
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | 12 | 185
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | 12 | 186
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | 12 | 187
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | 12 | 188
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | 12 | 189
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | 12 | 190
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | 12 | 191
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | 12 | 192
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | 12 | 193
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | 12 | 194
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | 12 | 195
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | 12 | 196
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | 12 | 197
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | 12 | 198
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | 12 | 199
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | 12 | 200
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | 12 | 201
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | 12 | 202
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | 12 | 203
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | 12 | 204
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | 12 | 205
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | 12 | 206
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | 12 | 207
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | 12 | 208
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | 12 | 209
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | 12 | 210
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | 12 | 211
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | 12 | 212
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | 12 | 213
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | 12 | 214
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | 12 | 215
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | 12 | 216
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | 12 | 217
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | 12 | 218
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | 12 | 219
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | 12 | 220
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | 12 | 221
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | 12 | 222
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | 12 | 223
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | 12 | 224
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | 12 | 225
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | 12 | 226
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | 12 | 227
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | 12 | 228
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | 12 | 229
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | 12 | 230
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | 12 | 231
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | 12 | 232
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | 12 | 233
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | 12 | 234
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | 12 | 235
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | 12 | 236
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | 12 | 237
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | 12 | 238
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | 12 | 239
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | 12 | 240
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | 12 | 241
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | 12 | 242
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | 12 | 243
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | 12 | 244
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | 12 | 245
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | 12 | 246
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | 12 | 247
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | 12 | 248
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | 12 | 249
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | 12 | 250
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | 12 | 251
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | 12 | 252
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | 12 | 253
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | 12 | 254
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | 12 | 255
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | 12 | 256
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | 12 | 257
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | 12 | 258
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | 12 | 259
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | 12 | 260
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | 12 | 261
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | 12 | 262
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | 12 | 263
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | 12 | 264
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | 12 | 265
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | 12 | 266
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | 12 | 267
[11 empty] | M5-G | Cranes | Boom system | A | 48 | 12 | 268
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | 12 | 269
[11 empty] | M5-G | Cranes | Structure | A | 48 | 12 | 270
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | 12 | 271
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | 12 | 272
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | 12 | 273
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | 12 | 274
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | 12 | 275
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | 12 | 276
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | 12 | 277
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | 12 | 278
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | 12 | 279
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | 12 | 280
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | 12 | 281
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | 12 | 282
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | 12 | 283
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | 12 | 284
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | 12 | 285
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | 12 | 286
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | 12 | 287
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | 12 | 288
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | 12 | 289
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | 12 | 290
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | 12 | 291
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | 12 | 292
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | 12 | 293
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | 12 | 294
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | 12 | 295
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | 12 | 296
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | 12 | 297
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | 12 | 298
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | 12 | 299
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | 12 | 300
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | 12 | 301
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | 12 | 302
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | 12 | 303
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | 12 | 304
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | 12 | 305
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | 12 | 306

## FA_WEHY
Failure Code | FA_WEHY |  |  |  | Number of Locations in failure code when defaults assigned: | 2 |  | Final Criticality Code |  | A | This table and supporting cells are used to populate dynamic dropdowns for typical component criticalities, copy and paste from here if selectors for safety impact overrides are not working
Description | CONVEYOR
Reviewed | [10 empty] | Barrier Family | Barrier Family Description | Typical Components | Typical Criticality | Barrier Family ID | Column2 | Item No | FamilyList | ComponentList | Code |  | Barrier Family | Components
Agreed | [10 empty] | P2-A/B | Structural Integrity | Primary Structures - All Components | A | 1 | 0 | 1 | Structural Integrity | #N/A | #N/A | Count | 54 | #N/A
Risk Matrix Assessment |  |  |  |  | Criticality for CMMS Rules |  | ABC Allocation Rules |  |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in hydrocarbon LOPC | A | 1 | #N/A | 2 | Stability loading control & watertight integrity | #N/A | #N/A | Selected ID | #N/A | #N/A
Highest Impact Event with its likelihood is shown in each category (may not be highest risk score) |  |  |  |  | Is the item SCE? (Safety impact D or greater) | NO |  |  | Calculation has been overriden? | FALSE | P2-A/B | Structural Integrity | Secondary Structures - Single component failure results in object dropping >3m | A | 1 | #N/A | 3 | Station Keeping | #N/A | #N/A
This is used to feed the failure code criticalities | [7 empty] | Replace this text with some comments if overriding the calculated code. This cell is locked until the code is changed fromm the derived value below |  |  | P2-A/B | Structural Integrity | Secondary Structures - Single component failure has no immediate consequence | C | 1 | #N/A | 4 | Swivel Stack Assembly | #N/A | #N/A
Category | Impact | Likelihood | Rating |  | Derived CMMS Location Priority | 4 |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall >3m | A | 1 | #N/A | 5 | Swivel Fluid Barrier System | #N/A | #N/A |  | 54 | #N/A
Safety | H | 2 | 2 |  | Redundancy applies? | No |  |  |  |  | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall 1 - 3m | B | 1 | #N/A | 6 | Swivel/Turret Pipework | #N/A | #N/A
Environmental | H | 2 | 2 |  | Elements contributing to CMMS Location Criticality rating | 2 |  | Derived SAP A/B/C = |  | A | P2-A/B | Structural Integrity | Tertiary Structures - Failure may result in fall <1m | C | 1 | #N/A | 7 | Turret Chain Table | #N/A | #N/A
Production | H | 2 | 2 |  |  | 2 |  | This can be manually overidden, by overwriting |  |  | P3-A | Stability loading control & watertight integrity | Ballast Pumps | A | 2 | #N/A | 8 | Main Turret Bearing | #N/A | #N/A
Business | G | 4 | 5 |  |  | 2 |  | formula in K1, but comments to be supplied as justification |  |  | P3-A | Stability loading control & watertight integrity | Sea Chest Valves | A | 2 | #N/A | 9 | Wellhead integrity | #N/A | #N/A
[6 empty] | 4 |  |  |  |  | P3-A | Stability loading control & watertight integrity | Loading Computer | A | 2 | #N/A | 10 | Subsea Integrity | #N/A | #N/A
Risk Matrix Population Inputs | [10 empty] | P3-A | Stability loading control & watertight integrity | Tank/Draft Monitoring systems | B | 2 | #N/A | 11 | Process Containment Integrity | #N/A | #N/A
Safety Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Safety Impact Overrides based on typical criticalities BP Guide 100041 |  |  |  | P3-A | Stability loading control & watertight integrity | Ballast/Cargo/Slop tank Valve control monitoring system | A | 2 | #N/A | 12 | Gas Turbine Packages & Hydrocarbon RE | #N/A | #N/A
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | MAH Barrier family | MAH barrier |  | ABC | P3-A | Stability loading control & watertight integrity | Bilge System Alarms CCR | A | 2 | #N/A | 13 | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | #N/A | #N/A
|  |  | #N/A |  |  |  | #N/A | #N/A |  | #N/A | P3-A | Stability loading control & watertight integrity | Ballast Pump Hydraulic Power | A | 2 | #N/A | 14 | Diesel Driven Packages | #N/A | #N/A
|  |  | #N/A | [7 empty] | P3-A | Stability loading control & watertight integrity | Down-flooding Points | A | 2 | #N/A | 15 | Oil Storage & Offloading | #N/A | #N/A
|  |  | #N/A |  |  |  | Comment on barrier selection | None allocatedSalt discharge screw conveyors, no MAH role identified |  |  | P3-A | Stability loading control & watertight integrity | Tank Hatches | B | 2 | #N/A | 16 | Overpressure Protection | #N/A | #N/A
[11 empty] | P3-A | Stability loading control & watertight integrity | Cargo transfer/loading system | A | 2 | #N/A | 17 | Blowdown vent and flare | #N/A | #N/A
Environmental Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 | [5 empty] | P3-B | Station Keeping | Chain Stoppers | A | 3 | #N/A | 18 | Digital security | #N/A | #N/A
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide | [5 empty] | P3-B | Station Keeping | Mooring Chains (top chain, bottom chain, wire/polyester rope rope) | A | 3 | #N/A | 19 | Control systems - LoPs | #N/A | #N/A
|  |  | #N/A | [7 empty] | P3-B | Station Keeping | Suction Piles | A | 3 | #N/A | 20 | Control systems - non LoPs, LOPA initiating causes | #N/A | #N/A
|  |  | #N/A | [7 empty] | P3-C | Swivel Stack Assembly | Utility, Production, LVSR (Low Voltage Slip Ring) Swivel Rings | A | 4 | #N/A | 21 | Control systems - all others | #N/A | #N/A
[11 empty] | P3-C | Swivel Stack Assembly | Swivel Seals (Primary and Secondary Seals) | A | 4 | #N/A | 22 | SIS - LoP Components | #N/A | #N/A
[7 empty] | High likelihood threshold for business impacts: likelihood > |  | 5 |  | P3-C | Swivel Stack Assembly | Fibre Optic Ring Joint | A | 4 | #N/A | 23 | SIS - Non LoP Components | #N/A | #N/A
Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Financial Impact Flowchart |  |  |  | P3-C | Swivel Fluid Barrier System | HPU Reservoir | A | 5 | #N/A | 24 | Alarms & operator response | #N/A | #N/A
Loss of Function | H | 2 | 2 | 72 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Swivel Fluid Barrier System | HPU Pumps, filters and automatic controls | A | 5 | #N/A | 25 | Collision Prevention | #N/A | #N/A
|  |  | #N/A |  |  |  | Failure of location < E business impact? |  | Yes | C | P3-C | Swivel Fluid Barrier System | N2 hydraulic Accumulators | A | 5 | #N/A | 26 | Export tanker birthing and position monitoring | #N/A | #N/A
|  |  | #N/A |  |  |  | Failure of location < F business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Hard piping, PSVs, Valves, etc. | A | 6 | #N/A | 27 | Bunding, Open and Closed Hazardous Drains | #N/A | #N/A
|  |  | #N/A |  |  |  | Failure of location <= G business impact? |  | Yes | C | P3-C | Swivel/Turret Pipework | Flexible Hoses Required | A | 6 | #N/A | 28 | Passive Fire Protection | #N/A | #N/A
[11 empty] | P3-C | Turret Chain Table | Anchor Mooring Leg | A | 7 | #N/A | 29 | Blast Overpressure Protection | #N/A | #N/A
Non-Financial Scenarios | Impact | Likelihood | Risk Score | Code for Letter | Justification / Comment2 |  | Non-financial flowchart |  |  |  | P3-C | Turret Chain Table | Riser/Umbilical Installation and Maintenance System | A | 7 | #N/A | 30 | Temporary refuge integrity | #N/A | #N/A
Loss of Function | G | 4 | 5 | 71 | Copied From AGT UMCL Criticality Guide |  | Condition |  | Output | ABC | P3-C | Turret Chain Table | (hydraulic winch, wire rope, and HPU) | A | 7 | #N/A | 31 | Alarm Annunciation System: | #N/A | #N/A
|  |  | #N/A |  |  |  | Is this equipment an IPL in a LOPA? |  | No | C | P3-C | Turret Chain Table | Adjusting Mooring Chain Tension | A | 7 | #N/A | 32 | Personnel Address (PA) System | #N/A | #N/A
|  |  | #N/A |  |  |  | Non-financial impact > E or regulatory req't && Likelihood high |  | No | C | P3-C | Main Turret Bearing | Grease Lubrication System (grease pump, | A | 8 | #N/A | 33 | Marine, Aircraft and Helicopter Radio System | #N/A | #N/A
[7 empty] | Regulatory Requirement overrides? | No | No | C | P3-C | Main Turret Bearing | metering valves, injector divider valves, etc.) | A | 8 | #N/A | 34 | Telecommunications | #N/A | #N/A
[11 empty] | P3-C | Main Turret Bearing | Main Bearing, Cover, Bearing Studs etc. | A | 8 | #N/A | 35 | Electronic Muster System | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Annulus Swab | B | 9 | #N/A | 36 | Facility Emergency Telephone & Hot line systems | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Annulus Master | B | 9 | #N/A | 37 | Facility radio system | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Crossover | B | 9 | #N/A | 38 | Emergency Power | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Production Swab | B | 9 | #N/A | 39 | Emergency Lighting | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Production Master | B | 9 | #N/A | 40 | Ignition Prevention | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | Production Wing | B | 9 | #N/A | 41 | Inert Gas Blanketing | #N/A | #N/A
[11 empty] | P4-A | Wellhead integrity | SCSSV | A | 9 | #N/A | 42 | Lifesaving Equipment | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Production Tree | A | 10 | #N/A | 43 | Muster areas, escape and evacuation routes | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Gas Injection Tree | A | 10 | #N/A | 44 | Lifeboats | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Water Injection Tree | A | 10 | #N/A | 45 | Means of escape to sea | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Process Gas Pipeline | A | 10 | #N/A | 46 | Helideck | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Oil Production Pipeline | A | 10 | #N/A | 47 | Rescue & Recovery Systems | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Water Injection Pipeline | B | 10 | #N/A | 48 | Cranes | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Pig Launcher / Receiver | A | 10 | #N/A | 49 | Lifting system | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile | A | 10 | #N/A | 50 | Fire & Gas systems | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Buoyancy Tank | A | 10 | #N/A | 51 | Emergency Shutdown Systems | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Pipeline Crossing Support | B | 10 | #N/A | 52 | Riser ESDVs & EIVs | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Flying Lead | B | 10 | #N/A | 53 | Fire protection | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Electrical Junction Box | B | 10 | #N/A | 54 | Miscellaneous fire protection systems | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Extension Umbilical | B | 10 | #N/A | 55 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Buckle Initiator | B | 10 | #N/A | 56 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Flowline Holdback Pile | A | 10 | #N/A | 57 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flexible Riser | A | 10 | #N/A | 58 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Riser | A | 10 | #N/A | 59 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Riser | A | 10 | #N/A | 60 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flexible Riser | A | 10 | #N/A | 61 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flexible Spur | A | 10 | #N/A | 62 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flexible Spur | B | 10 | #N/A | 63 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Production Flowline Termination Assembly | A | 10 | #N/A | 64 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Flowline Termination Assembly | A | 10 | #N/A | 65 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Flowline Termination Assembly | B | 10 | #N/A | 66 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Service Flowline Termination Assembly | B | 10 | #N/A | 67 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Gas Lift Module | A | 10 | #N/A | 68 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Distribution (Hydraulic Control) Unit | B | 10 | #N/A | 69 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic/Chemical Flying Lead | B | 10 | #N/A | 70 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Main Umbilical | B | 10 | #N/A | 71 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Hydraulic Power Unit | A | 10 | #N/A | 72 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Control Panel | B | 10 | #N/A | 73 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Production Inline Tee Assembly | A | 10 | #N/A | 74 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Inline Tee Assembly | A | 10 | #N/A | 75 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Inline Tee Assembly | B | 10 | #N/A | 76 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Service Inline Tee Assembly | B | 10 | #N/A | 77 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Infield Umbilical | B | 10 | #N/A | 78 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Master Control System | A | 10 | #N/A | 79 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Multiphase Flowmeter | B | 10 | #N/A | 80 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold | A | 10 | #N/A | 81 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Anchor Pile (Manifold Support Structure) | B | 10 | #N/A | 82 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Manifold Support Structure | B | 10 | #N/A | 83 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower Monitoring System | B | 10 | #N/A | 84 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Tower | A | 10 | #N/A | 85 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Rigid Riser | A | 10 | #N/A | 86 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Riser Base | A | 10 | #N/A | 87 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Control Module | B | 10 | #N/A | 88 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Production Spool Piece | A | 10 | #N/A | 89 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Gas Injection Spool Piece | A | 10 | #N/A | 90 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Water Injection Spool Piece | B | 10 | #N/A | 91 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Service Spool Piece | A | 10 | #N/A | 92 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Umbilical | B | 10 | #N/A | 93 |  | #N/A | #N/A
[11 empty] | P4-B | Subsea Integrity | Subsea Production Tree Jumper | B | 10 | #N/A | 94 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for hydrocarbons with flash point less than 52o C | A | 11 | #N/A | 95 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for service conditions greater than B16.5, Class 300 | A | 11 | #N/A | 96 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework operating at temperature greater than 120o C | A | 11 | #N/A | 97 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework for highly toxic substances | A | 11 | #N/A | 98 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework with corrosion resistant linings | A | 11 | #N/A | 99 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All pressure retaining Equipment and pipework associated with fire water delivery systems | A | 11 | #N/A | 100 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | Bilge and ballast pipework | A | 11 | #N/A | 101 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All other pressure Equipment and pipework | C | 11 | #N/A | 102 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | Supports for criticality A pressure systems | A | 11 | #N/A | 103 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | Insulation installed on criticality A pressure systems | A | 11 | #N/A | 104 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | Painting on criticality A pressure systems | A | 11 | #N/A | 105 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | Bolting on criticality A pressure systems | A | 11 | #N/A | 106 |  | #N/A | #N/A
[11 empty] | P4-C | Process Containment Integrity | All other supports, paint and bolting | C | 11 | #N/A | 107 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Gas Generator | A | 12 | #N/A | 108 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Alternators | B | 12 | #N/A | 109 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Power Turbine | B | 12 | #N/A | 110 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Casing joints, fittings and seals | B | 12 | #N/A | 111 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals | A | 12 | #N/A | 112 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All coupling members | B | 12 | #N/A | 113 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Pressurized Enclosures | A | 12 | #N/A | 114 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Fire & Gas System | A | 12 | #N/A | 115 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Shaft Seals System Ancillaries | A | 12 | #N/A | 116 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Special Protection Systems (Surge Protection, Over Speed, Electrical Power Protection) | A | 12 | #N/A | 117 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | All Protective Systems (Pressure, temperature, Vibration, NRV, PSVs) | A | 12 | #N/A | 118 |  | #N/A | #N/A
[11 empty] | P4-D | Gas Turbine Packages & Hydrocarbon RE | Auxiliaries like (cleaning system, control system, utilities) | B | 12 | #N/A | 119 |  | #N/A | #N/A
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk turquoise and below) | B | 13 | #N/A | 120 |  | #N/A | #N/A
[11 empty] | P4-D | Non Hydrocarbon RE (air compressors, water and hydraulic pumps) | Equipment and protective systems including all LOPC for fluid and power (mechanical destruction) (LOPC risk above turquoise) | A | 13 | #N/A | 121 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | Diesel Engine | B | 14 | #N/A | 122 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | Alternators | B | 14 | #N/A | 123 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | All Fuel system Joints, Fittings and Seals | B | 14 | #N/A | 124 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | All coupling members | B | 14 | #N/A | 125 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | All Safety Protective Systems (over speed, Mist Detection, Cooling Medium Temperature, etc.) | A | 14 | #N/A | 126 |  | #N/A | #N/A
[11 empty] | P4-D | Diesel Driven Packages | All other Systems (governor, control, utilities, etc.) | B | 14 | #N/A | 127 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Export Booster Pumps | A | 15 | #N/A | 128 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Export Hose | A | 15 | #N/A | 129 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Marine Growth Prevention Equipment | B | 15 | #N/A | 130 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Cargo Tank Cleaning Systems | B | 15 | #N/A | 131 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Cargo & Ballast Hydraulic Valve Control | A | 15 | #N/A | 132 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Marine Hydraulic systems (pumps, power units and storage tanks) | B | 15 | #N/A | 133 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Gas Detection | A | 15 | #N/A | 134 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Void Tank Dehumidification systems | B | 15 | #N/A | 135 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Hydrocarbon Tanks | A | 15 | #N/A | 136 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Ballast Tanks | A | 15 | #N/A | 137 |  | #N/A | #N/A
[11 empty] | P4-E | Oil Storage & Offloading | Void Tanks | B | 15 | #N/A | 138 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | PSV in hazardous or toxic duty | A | 16 | #N/A | 139 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, non-toxic service where pressure is above 50 barg | A | 16 | #N/A | 140 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where fluid temperature is above 120 degrees Celsius | A | 16 | #N/A | 141 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | PSV in non-hazardous, nontoxic service where inlet size 8” or above | A | 16 | #N/A | 142 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | All other PSVs | B | 16 | #N/A | 143 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | NRV credited in the sizing case for a PSV | A | 16 | #N/A | 144 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | NRV that protects against any E+ severity event. For example, damage to Equipment | A | 16 | #N/A | 145 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | NRVs where consequence/likelihood of failure combination leads to a turquoise risk | B | 16 | #N/A | 146 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | All other NRVs | C | 16 | #N/A | 147 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict gas flow to flare | A | 16 | #N/A | 148 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | ROs (or FOs) that restrict flow to a PSV | A | 16 | #N/A | 149 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | ROs in pump recirculation lines | B | 16 | #N/A | 150 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Control valves credited in LOPA | A | 16 | #N/A | 151 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Bursting disks in hazardous or toxic duty | A | 16 | #N/A | 152 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Bursting disks protecting an HP/LP interface. For example, cases where a bursting disk is protecting the shell side of a heat exchanger in the event of tube rupture | A | 16 | #N/A | 153 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Bursting disk relieving directly to flare (i.e. no PSV downstream) | A | 16 | #N/A | 154 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Bursting disks located upstream of a PSV with the intent of protecting that PSV from fouling | Same criticality as the PSV | 16 | #N/A | 155 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Other bursting disks | B | 16 | #N/A | 156 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers that are part of barrier P4-E (Oil Storage and Offloading) | A | 16 | #N/A | 157 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Vacuum breakers in hazardous or toxic duty | A | 16 | #N/A | 158 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Other Vacuum breakers not covered by the descriptions above. | C | 16 | #N/A | 159 |  | #N/A | #N/A
[11 empty] | P5-A | Overpressure Protection | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 16 | #N/A | 160 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in hazardous or toxic duty | A | 17 | #N/A | 161 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Blowdown valves in non-hazardous, nontoxic duty | B | 17 | #N/A | 162 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Bursting disks provided as an alternative means to relieve back pressure in the event of FOV failure. For example, bursting disks in flare XXV bypass lines | A | 17 | #N/A | 163 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | FOVs in hazardous and non-toxic duty required to react within 2 seconds to prevent an overpressure ratio of >=1.3 | A | 17 | #N/A | 164 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | All other FOVs | B | 17 | #N/A | 165 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum | A | 17 | #N/A | 166 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | #N/A | 167 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | HP Flare KO Drum Heaters | A | 17 | #N/A | 168 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum | A | 17 | #N/A | 169 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | LP Flare KO Drum Pumps (at a component level, align with P4-D) | A | 17 | #N/A | 170 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | KO Drum systems that ensure that liquid droplets larger than 300 microns cannot carry to flare | B | 17 | #N/A | 171 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Flare tip ignition systems | A | 17 | #N/A | 172 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Flare system XXVs that are not covered under FOVs | A | 17 | #N/A | 173 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Flare tips | A | 17 | #N/A | 174 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Any Equipment that maintains the barrier between wet and dry fluids | A | 17 | #N/A | 175 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Vents in hazardous or toxic duty that are required to prevent overpressure ratio >=1.3 | A | 17 | #N/A | 176 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Other vents | C | 17 | #N/A | 177 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Equipment providing early indication of blockages within flare header | A | 17 | #N/A | 178 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Isolation valves where sealing integrity is essential to ensure planned maintenance of Equipment can be performed. | Same criticality as Equipment being isolated. | 17 | #N/A | 179 |  | #N/A | #N/A
[11 empty] | P5-B | Blowdown vent and flare | Flare pipework and headers (align with barrier P4-C) | A | 17 | #N/A | 180 |  | #N/A | #N/A
[11 empty] | P6-A | Digital security | Fire walls | A | 18 | #N/A | 181 |  | #N/A | #N/A
[11 empty] | P6-A | Digital security | Remote access servers | A | 18 | #N/A | 182 |  | #N/A | #N/A
[11 empty] | P6-A | Digital security | Architecture | A | 18 | #N/A | 183 |  | #N/A | #N/A
[11 empty] | P6-A | Digital security | Staging servers for Anti-virus and OS patches | A | 18 | #N/A | 184 |  | #N/A | #N/A
[11 empty] | P6-A | Control systems - LoPs | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, motor/compressor/heater contactors and relays, control valves, Anti-surge valve, positioners, solenoids on control valves, ccc controller cards, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | A | 19 | #N/A | 185 |  | #N/A | #N/A
[11 empty] | P6-A | Control systems - non LoPs, LOPA initiating causes | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | B | 20 | #N/A | 186 |  | #N/A | #N/A
[11 empty] | P6-A | Control systems - all others | Transmitter, pressure and level switches, barrier, junction box, I/O card, controller card, communications card, Wiring Panels, system cable, control valves, positioners, network switches, HMI screens, UPS, Power cables, power supplies and power distribution. | C | 21 | #N/A | 187 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - LoP Components | LoP Components: | A | 22 | #N/A | 188 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, actuators, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 22 | #N/A | 189 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - LoP Components | Testing Equipment | A | 22 | #N/A | 190 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - LoP Components | Shutdown Components: XXV valves, blow down valves, switches/push buttons | A | 22 | #N/A | 191 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - Non LoP Components | LoP Components: | B | 23 | #N/A | 192 |  | #N/A | #N/A
[11 empty] | P7-A | SIS - Non LoP Components | Transmitter, barrier, junction box, I/O card, communications card, logic solvers, system cable, motor/compressor contactors/heater and relays, shutdown valves, solenoids, XV valve HPU units, partial stroke testing Equipment, HMI screens, Wiring Panels, Shutdown switches, network switches, UPS, Power cables, power supplies and power distribution. | B | 23 | #N/A | 193 |  | #N/A | #N/A
[11 empty] | P8 | Alarms & operator response | Transmitter, barrier, junction box, I/O card, controller card, system cable, network switches, VDU screens, Wiring Panels, UPS, power supplies and power distribution. | A | 24 | #N/A | 194 |  | #N/A | #N/A
[11 empty] | P9-A | Collision Prevention | Nav Aids lights, sounders & UPS systems | A | 25 | #N/A | 195 |  | #N/A | #N/A
[11 empty] | P9-B | Export tanker birthing and position monitoring | Mooring Hawser and Load Monitoring | B | 26 | #N/A | 196 |  | #N/A | #N/A
[11 empty] | P9-B | Export tanker birthing and position monitoring | Berthing System (TAOMS) | B | 26 | #N/A | 197 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Tunn dishes / Drain Pans/Drip trays / Isolation valves / Bunds | B | 27 | #N/A | 198 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Main Deck Coaming | B | 27 | #N/A | 199 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Open Hazardous Drains Water seals | A | 27 | #N/A | 200 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum Alarms | A | 27 | #N/A | 201 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Close drain Drum heating system (heating Coil, instrumentation, insulation) | A | 27 | #N/A | 202 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Secondary containments | B | 27 | #N/A | 203 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Helideck Drainage | B | 27 | #N/A | 204 |  | #N/A | #N/A
[11 empty] | M1-A | Bunding, Open and Closed Hazardous Drains | Rodding | A | 27 | #N/A | 205 |  | #N/A | #N/A
[11 empty] | M2-A | Passive Fire Protection | PFP where applied | A | 28 | #N/A | 206 |  | #N/A | #N/A
[11 empty] | M2-B | Blast Overpressure Protection | Blast Walls | A | 29 | #N/A | 207 |  | #N/A | #N/A
[11 empty] | M2-B | Blast Overpressure Protection | Blast Doors | A | 29 | #N/A | 208 |  | #N/A | #N/A
[11 empty] | M2-C | Temporary refuge integrity | External Temporary Refuge doors | A | 30 | #N/A | 209 |  | #N/A | #N/A
[11 empty] | M2-C | Temporary refuge integrity | Internal Temporary Fire Refuge doors | B | 30 | #N/A | 210 |  | #N/A | #N/A
[11 empty] | M3-A | Alarm Annunciation System: | External Speakers Internal Speakers, Strobe Lights Indicator Lights Alarm interface with Fire & Gas Controllers | A | 31 | #N/A | 211 |  | #N/A | #N/A
[11 empty] | M3-A | Personnel Address (PA) System | Amplifiers Controllers External Speakers Internal Speakers Beacons / Strobe Lights Indicator Lights | A | 32 | #N/A | 212 |  | #N/A | #N/A
[11 empty] | M3-B | Marine, Aircraft and Helicopter Radio System | Antenna Receiver/transmitter Batteries Sat comms | A | 33 | #N/A | 213 |  | #N/A | #N/A
[11 empty] | M3-B | Telecommunications | Class A Telecommunication UPS & Shut down | A | 34 | #N/A | 214 |  | #N/A | #N/A
[11 empty] | M3-B | Electronic Muster System | Locations sensors / badge readers Controllers & Software Interconnecting cable plant and network Display screen and printers Personnel RFID badge devices | A | 35 | #N/A | 215 |  | #N/A | #N/A
[11 empty] | M3-B | Facility Emergency Telephone & Hot line systems |  | A | 36 | #N/A | 216 |  | #N/A | #N/A
[11 empty] | M3-B | Facility radio system | Telecommunication towers Hand held radios Base Stations Antennas Radio Repeaters System Controllers | A | 37 | #N/A | 217 |  | #N/A | #N/A
[11 empty] | M3-C | Emergency Power | Emergency Generator | A | 38 | #N/A | 218 |  | #N/A | #N/A
[11 empty] | M3-C | Emergency Power | Hull Generators | A | 38 | #N/A | 219 |  | #N/A | #N/A
[11 empty] | M3-C | Emergency Power | Hull Generators (2 out of 3) | B | 38 | #N/A | 220 |  | #N/A | #N/A
[11 empty] | M3-C | Emergency Power | UPS Systems | A | 38 | #N/A | 221 |  | #N/A | #N/A
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - battery backed | A | 39 | #N/A | 222 |  | #N/A | #N/A
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - supplied from Emergency Generator Switchboard | B | 39 | #N/A | 223 |  | #N/A | #N/A
[11 empty] | M3-D | Emergency Lighting | Emergency Lighting - Emergency Hand Torches in switchgear rooms | B | 39 | #N/A | 224 |  | #N/A | #N/A
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 0 and Zone 1 | A | 40 | #N/A | 225 |  | #N/A | #N/A
[11 empty] | M4-A | Ignition Prevention | For Equipment in Zone 2 | B | 40 | #N/A | 226 |  | #N/A | #N/A
[11 empty] | M4-A | Ignition Prevention | Equipment that is required to remain energized in the event of an incident (e.g. Tannoy and beacon systems, emergency lighting, emergency generation etc). | A | 40 | #N/A | 227 |  | #N/A | #N/A
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator | A | 41 | #N/A | 228 |  | #N/A | #N/A
[11 empty] | M4-B | Inert Gas Blanketing | IGG Generator Diesel Oil Supply Pumps | B | 41 | #N/A | 229 |  | #N/A | #N/A
[11 empty] | M4-B | Inert Gas Blanketing | Isolation valves on locked valve register | A | 41 | #N/A | 230 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Emergency escape breathing devices | A | 42 | #N/A | 231 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Grab bags and smoke hoods | B | 42 | #N/A | 232 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Lifejackets | A | 42 | #N/A | 233 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Lifebuoys | B | 42 | #N/A | 234 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Line-throwing Device | B | 42 | #N/A | 235 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Helicopter Crash Equipment | B | 42 | #N/A | 236 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Fireman Outfits | A | 42 | #N/A | 237 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Emergency Breathing Air Compressor | B | 42 | #N/A | 238 |  | #N/A | #N/A
[11 empty] | M5-A | Lifesaving Equipment | Storage Containers | C | 42 | #N/A | 239 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Station Bill | B | 43 | #N/A | 240 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Routes | A | 43 | #N/A | 241 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Escape Route Doors | A | 43 | #N/A | 242 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Primary Muster Area | A | 43 | #N/A | 243 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Egress Routes | A | 43 | #N/A | 244 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Temporary Refuge Facilities - HVAC Equipment and Fire / Blast Dampers | A | 43 | #N/A | 245 |  | #N/A | #N/A
[11 empty] | M5-B | Muster areas, escape and evacuation routes | Alternative Muster Areas | B | 43 | #N/A | 246 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Hull, hatch seals, penetrations, shaft, shaft seals, cable glance or window seals, Structural and watertight integrity | A | 44 | #N/A | 247 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Clutch, steering, internal lighting, fuel tank, air bottles, emergency provisions and survival Equipment | A | 44 | #N/A | 248 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Release Mechanism | A | 44 | #N/A | 249 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Deluge, Engine | A | 44 | #N/A | 250 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | VHF Radio | A | 44 | #N/A | 251 |  | #N/A | #N/A
[11 empty] | M5-C | Lifeboats | Emergency Beacons | A | 44 | #N/A | 252 |  | #N/A | #N/A
[11 empty] | M5-D | Means of escape to sea | Life-rafts | A | 45 | #N/A | 253 |  | #N/A | #N/A
[11 empty] | M5-D | Means of escape to sea | Personal Davit Descent devices | A | 45 | #N/A | 254 |  | #N/A | #N/A
[11 empty] | M5-D | Means of escape to sea | Embarkation Rope Ladders to Sea | A | 45 | #N/A | 255 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Helideck Landing Area Net (as required) | C | 46 | #N/A | 256 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Perimeter Net - (Integrity inspections) | B | 46 | #N/A | 257 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Helideck Lights - Heliport Identification Lights (H) / Floodlights / Obstruction Lighting | A | 46 | #N/A | 258 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Refueling Equipment - Aviation Fuel System & Equipment (Heli-fuel transfer pumps /nozzles) / Fuel testing / inspections | A | 46 | #N/A | 259 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Firefighting Equipment (System) - including Foam (as required) | A | 46 | #N/A | 260 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Helideck Equipment - Deck crew duties and helicopter Ops support | C | 46 | #N/A | 261 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | Emergency Equipment - Helideck emergency response Equipment | B | 46 | #N/A | 262 |  | #N/A | #N/A
[11 empty] | M5-E | Helideck | MET System (Meteorological Equipment) - On-board IMMS System | C | 46 | #N/A | 263 |  | #N/A | #N/A
[11 empty] | M5-F | Rescue & Recovery Systems | Place of Safety | B | 47 | #N/A | 264 |  | #N/A | #N/A
[11 empty] | M5-F | Rescue & Recovery Systems | Man Overboard Alarm | B | 47 | #N/A | 265 |  | #N/A | #N/A
[11 empty] | M5-F | Rescue & Recovery Systems | Fast Rescue craft | B | 47 | #N/A | 266 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Hoisting system | A | 48 | #N/A | 267 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Boom system | A | 48 | #N/A | 268 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Warning, recording & measuring systems | A | 48 | #N/A | 269 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Structure | A | 48 | #N/A | 270 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Slewing system | B | 48 | #N/A | 271 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Hydraulic system | B | 48 | #N/A | 272 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Prime mover system | B | 48 | #N/A | 273 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Access & walkways | A | 48 | #N/A | 274 |  | #N/A | #N/A
[11 empty] | M5-G | Cranes | Maintenance Equipment | C | 48 | #N/A | 275 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Runway beams | A | 49 | #N/A | 276 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Gantry crane | A | 49 | #N/A | 277 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Lifeboat davit | A | 49 | #N/A | 278 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Life-raft davit | A | 49 | #N/A | 279 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | General purpose/maintenance davit | B | 49 | #N/A | 280 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Winch (for lifting personnel) | A | 49 | #N/A | 281 |  | #N/A | #N/A
[11 empty] | M5-G | Lifting system | Winch (general purpose - not for lifting personnel) | B | 49 | #N/A | 282 |  | #N/A | #N/A
[11 empty] | M6-A | Fire & Gas systems | Barrier, junction box, I/O card, communications card, logic solvers, system cable, shutdown valves, solenoids, HMI screens, Wiring Panels, network switches, UPS, Power cables, power supplies and power distribution. | A | 50 | #N/A | 283 |  | #N/A | #N/A
[11 empty] | M6-A | Fire & Gas systems | Detectors: Flame, Flammable Gas, Heat, Oil Mist, Smoke, Personal Gas Detector Manual call point Testing Equipment F&G mimic panel | A | 50 | #N/A | 284 |  | #N/A | #N/A
[11 empty] | M6-C | Emergency Shutdown Systems | XV/XXVs on emergency shutdown duty | A | 51 | #N/A | 285 |  | #N/A | #N/A
[11 empty] | M6-D | Riser ESDVs & EIVs | Export/Import/Injection Riser ESDVs (XXVs) & actuators | A | 52 | #N/A | 286 |  | #N/A | #N/A
[11 empty] | M6-D | Riser ESDVs & EIVs | Umbilical emergency ESDVs (XXVs) & actuators | A | 52 | #N/A | 287 |  | #N/A | #N/A
[11 empty] | M6-D | Riser ESDVs & EIVs | Injection Flowline EIVs (XV) & actuators | A | 52 | #N/A | 288 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Firewater pumps (main and jockey), drivers, their controls and control panels | A | 53 | #N/A | 289 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (supplementary fire-fighting system) | B | 53 | #N/A | 290 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Fixed firewater /foam monitors/hydrants/hose stations (primary fire-fighting system) | A | 53 | #N/A | 291 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Zone isolation valves | A | 53 | #N/A | 292 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (≥10 per zone) | B | 53 | #N/A | 293 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Sprinkler / Deluge Nozzle (<10 per zone) | A | 53 | #N/A | 294 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Pressure / level / flow instruments | A | 53 | #N/A | 295 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Control Valves | A | 53 | #N/A | 296 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Logic solvers | A | 53 | #N/A | 297 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Accommodation hydrants (main fire-fighting mechanism) | A | 53 | #N/A | 298 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Accommodation hydrants (if sprinkler system present) | B | 53 | #N/A | 299 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (≥3 per fire zone) | B | 53 | #N/A | 300 |  | #N/A | #N/A
[11 empty] | M7 | Fire protection | Fusible plug / fusible loop (<3 per zone) | A | 53 | #N/A | 301 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Hose reels, nozzles and portable fire monitors | B | 54 | #N/A | 302 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Mobile (wheeled) fire extinguishers | B | 54 | #N/A | 303 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Fixed CO2 Fire Extinguishing Systems | B | 54 | #N/A | 304 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Galley Fire Suppression System | A | 54 | #N/A | 305 |  | #N/A | #N/A
[11 empty] | M7-B | Miscellaneous fire protection systems | Water Mist Systems | B | 54 | #N/A | 306 |  | #N/A | #N/A